## Sheet1
Test and Inspection Plan
Section | Rev | Title | CM-CE Submittal Review Req'd | Type of Submittal Review | CM-CE Inspection Req'd | Inspection Type | (For LANL) Checklist used? | Subcontractor Inspection Responsibilities | Comments
PREPARERS NOTES (delete when issuing)
Template based on LANL Master Specs as of issue date. Tailor this template to Project by deleting N/A rows and adding rows for Project-initiated spec sections.
Rev number reflects LANL Master version used to develop template. If later edition is used, update inspections as required. When issuing TIP, delete column or reset numbers to match Project spec section revisions (all 0 initially).
SELF PERFORM WORK (delete when non-LANL constructor)
For self perform work (CM-CS), where references are made to contract requirements, CM groups will perform "Subcontractor Inspection Responsiblities" as noted.
01 1116 | 1 | Work by Owner | 1 Yes |  | 1 Yes | Ensure GFE is accepted prior to turnover to subcontractor |  | N/A | (1 only for GFE) Ensure GFE is accepted for turnover to subcontractor
01 2500 | 1 | Substitution Procedures | N/A |  | N/A |  |  | Review and clearly identify to LANL
01 3300 | 3 | Submittal Procedures | N/A |  | N/A |  |  | Review and clearly identify to LANL | If used, ensure codes match Exh I
01 3545 | 6 | Water Discharge Requirements | N/A |  | N/A |  |  | Review and document to LANL
01 4000 | 4 | Quality Requirements | Yes | Quality programs, quality procedures, test and inspection plan, qualification of testing agencies, coordination schedules, licenses and certificates, statement of responsibility | N/A |  |  | Review and document to LANL, ensure full compliance with contract
01 4200 | 3 | References | N/A |  | N/A |  |  | N/A
01 4444 | 0 | Offsite Welding & Joining Requirements | Yes | WPS, PQR, WQT, shop drawings, weld inspection procedures and weld inspection reports | Yes | Shop welding oversight |  | Review submittals, ensure compliance, ensure all code examinations are performed and documents using approved personnel | HOLD POINT for subcontracted work, must be submitted and approved prior to start of work.
01 4455 | 0 | Onsite Welding & Joining Requirements | Yes | shop drawing, weld inspection procedures and weld inspection reports | Yes | Field welding | Yes | Review submittals, ensure compliance, ensure all code examinations are performed and documents using approved personnel | HOLD POINT for subcontracted work, must be submitted and approved prior to start of work.
01 5705 | 4 | Temporary Controls and Compliance Requirements | No |  | No-STR |  |  | Review submittals, ensure compliance and document per contract
01 6000 | 1 | Product Requirements | No |  | No-STR |  |  | Ensure compliance and document inspections as required
01 7700 | 1 | Closeout Procedures | No2 |  | No2 - STR |  |  | Ensure compliance and document inspections as required | 2 Ensure final training complete prior to final signoff
01 7839 | 2 | Project Record Documents | No3 |  | No3 - STR |  |  | Review and document to LANL, ensure full compliance with contract | 3 Ensure project record documents/ as-built information/O&M manuals received prior to final signoff
02 4115 | 2 | Electrical Demolition | No4 |  | No4 - STR |  |  | Ensure compliance and document inspections as required | 4 Records of capped utilities (as-builts)
02 4119 | 1 | Selective Structure Demolition | No |  | No-STR |  |  | Ensure compliance and document as required
03 1534 | 3 | Post-Installed Concrete Anchor Purchase – High Confidence | Yes | All plans, QA program, MTRs, and technical documents | Yes | Field installation | Yes | Review submittals, ensure full compliance with contract, test plans, test reports | HOLD POINT - Special Inspection Required
03 1534 | 5 | Post-Installed Concrete Anchor Purchase – Normal Confidence | No | All plans, QA program, MTRs, and technical documents | Yes | Field installation | Yes | Review submittals, ensure full compliance with contract, Document shelf life | HOLD POINT - Special Inspection required, 1704.4, Periodic only unless otherwise noted
03 3001 | 6 | Reinforced Concrete | Yes | CMTRs, shop drawings, cold, hot weather plans | Yes | Field installation, field tolerances | Yes | Review submittals, ensure full compliance with contract, Pre-placement, placement, and post-placement inspections and documentation. | HOLD POINT- Special Inspection Required, 1704.4, see full submittal table in specification; includes concrete slab inspection per IBC 110.3.2 as applicable. Note: LANL will document pour locations for each tested group of batches (e.g., 50 yds)
03 3053 | 6 | Miscellaneous Cast-in-place Concrete | Yes | CMTRs, shop drawings | Yes | Field installation, field tolerances | Yes | Review submittals, ensure full compliance with contract, Pre-placement, placement, and post-placement inspections and documentation. | HOLD POINT- if Special Inspection is required
03 4100 | 0 | Precast Structural Concrete | Yes | Design mixtures, shop drawings, approved Special Inspection agency, WPS, PQR, WQT as applicable | Yes | Shop inspection oversight, Receipt inspection. Installation including welding inspection as required. | Yes | Review submittals, ensure full compliance with contract, receipt inspection. | HOLD POINT - Special Inspection required, 1704.4, Periodic only unless otherwise noted
03 6000 | 0 | Grout | Yes | Mfr C of C | Yes | Field installation |  | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection required, 1704.5, Periodic only unless otherwise noted
04 2220 | 0 | Reinforced Unit Masonry | Yes | Shop Drawings, Mfr C of C | Yes | Field installation |  | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection required, 1704.5, Periodic only unless otherwise noted
05 1000 | 6 | Structural Metal Framing | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation, welding, bolting | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection Required, 1704.3
05 1305 | 1 | Stainless Steel | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation, welding, bolting | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection Required, 1704.3; The specification does not address welding requirements
05 2100 | 3 | Steel Joist Framing | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation, welding, bolting | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection Required, 1704.3
05 3000 | 2 | Metal Decking | Yes | shop drawings, installation plan, WPS, PQR, WQT, attachment method | Yes | Field installation, welding or attachment method | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection Required, 1704.3
05 4000 | 2 | Cold Formed Metal Framing | Yes | shop drawings, installation plan, WPS, PQR, WQT, Fabrication qualifications, MTRs | Yes | Field installation, welding, bolting | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | HOLD POINT - Special Inspection Required, 1704.3
05 5000 | 3 | Metal Fabrications | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation, erection tolerances, welding, grouting | Yes | Review submittals, ensure full compliance with contract, receipt inspection, testing requirements. | Random inspection only
05 5100 | 0 | Metal Stairs | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation |  | Review submittals, ensure full compliance with contract, receipt inspection | Random inspection only
05 5213 | 1 | Pipe and Tubing Railing | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation |  | Review submittals, ensure full compliance with contract, receipt inspection | Random inspection only
05 5350 | 3 | Gratings and Floor Plates | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Field installation |  | Review submittals, ensure full compliance with contract, receipt inspection | Random inspection only
06 1000 | 2 | Rough Carpentry | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, ensure full compliance with contract, receipt inspection, Check tolerances | HOLD POINT - Rough Framing Inspection per IBC 110.3.4
06 2000 | 1 | Finish Carpentry | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify ready for installation
06 4100 | 1 | Architectural Wood Casework | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify ready for installation and location of items
07 0150.19 | 2 | Preparation for Re-Roofing | No |  | No-STR | Verify correct material, installation per instructions against approved submittals, qualification statements, landfill records |  | Review Submittal, verify installation and disposal records
07 0155 | 2 | Roof Patching | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review Submittal, verify installation and disposal records
07 1113 | 2 | Bituminous Dampproofing | No |  | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application | Random inspection only
07 1326 | 0 | Self-Adhering Sheet Waterproofing | Yes | Shop drawings, product test reports, Mfr certificates | Yes | Verify correct material, installation per instructions against approved submittals, witness flood test | Yes | Review submittal, examine substrate, inspect application , flood test | random inspection only except HOLD POINT - witness flood test
07 2100 | 2 | Thermal Insulation | No |  | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application | HOLD POINT - Energy efficiency inspection per IBC 110.374
07 2400 | 2 | Exterior Insulation and Finish Systems | Yes | Installation instructions, shop drawings, Mfr certificates, ICC-ES reports | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application | HOLD POINT - Energy efficiency inspection per IBC 110.374
07 4113 | 3 | Metal Roof Panels | Yes | Pre-installation conference, shop drawings | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation | HOLD POINT - Special Inspection Required, 1704.3
07 5050 | 1 | Membrane Roofing General Provisions | Yes | Shop drawings, water intrusion plan, installation instructions | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | HOLD POINT - Special Inspection Required, 1704.14; Witness drain testing
07 5213.13 | 0 | Atatic-Polypropylene Modified-Bitumen Roofing, Cold-Applied | Yes | Shop drawings, Mfr certificates, product test reports, research evaluation reports, Mfr instructions, Installer Qualification data | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | Testing agency: Owner will engage a qualified testing agency to perform tests and inspections and to prepare test reports? HOLD POINT - Special Inspection Required, 1704.14 and IBC 110.3.7
07 5216 | 2 | Styrene-Butadiene-Styrene Modified Bituminous Membrane Roofing | Yes | Shop drawings, Mfr certificates, product test reports, research evaluation reports, Mfr instructions, Installer Qualification data | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | Testing agency: Owner will engage a qualified testing agency to perform tests and inspections and to prepare test reports? HOLD POINT - Special Inspection Required, 1704.14 and IBC 110.3.7
07 5217 | 0 | Styrene-Butadiene-Styrene Modified-Bituminous Membrane Roofing, Cold-Applied | Yes | Shop drawings, Mfr certificates, product test reports, research evaluation reports, Mfr instructions, Installer Qualification data | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | Testing agency: Owner will engage a qualified testing agency to perform tests and inspections and to prepare test reports? HOLD POINT - Special Inspection Required, 1704.14 and IBC 110.3.7
07 5316 | 2 | Chlorosulfonate-Polyethylene Roofing | Yes | Shop drawings, Mfr certificates, product test reports, research evaluation reports, Mfr instructions, Installer Qualification data | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | Testing agency: Owner will engage a qualified testing agency to perform tests and inspections and to prepare test reports? HOLD POINT - Special Inspection Required, 1704.14 and IBC 110.3.7
07 6200 | 3 | Sheet Metal Flashing and Trim | Yes | Shop drawings, Mfr certificates, | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation | Random inspection only
07 7100 | 2 | Roof Specialties | Yes | Shop drawings, Mfr certificates, Mfr instructions | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation | Random inspection only
07 7233 | 2 | Roof Hatches | N/A | N/A | N/A | N/A |  |  | Obsolete, covered in Specification Section 07 7100, Roof Specialties
07 7600 | 2 | Roof Pavers | N/A | N/A | N/A | N/A |  |  | Obsolete, covered in Specification Section 07 7100, Roof Specialties
07 8400 | 3 | Firestopping | Yes | product data, product schedule, Mfr certificate, engineering judgements, Mfr installation instructions,installer certificates, laboratory test reports | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal, examine substrate, inspect application, document installation | HOLD POINT - Fire and Smoke-resistant penetrations Inspection per IBC 110.3.6; There are some Spec. issues, labeling, etc.
07 9200 | 3 | Joint Sealants | No | product data, product schedule, Mfr certificate, Mfr installation instructions,installer certificates, | Yes | Verify approval, license, storage, correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation | Random inspection only
08 1100 | 2 | Metal Doors and Frames | Yes5 | catalog data, shop drawings, 5fire rated certifications if applicable | Yes | Verify correct material, installation per instructions against approved submittals | Yes5 | Review submittals, Inspect Installation | Random inspection only, 5HOLD POINT-Fire rated doors require 100% inspection per IBC 110.3.6
08 1213 | 2 | Hollow Metal Frames | Yes5 | 5fire rated certifications if applicable | Yes | Verify correct material, installation per instructions against approved submittals | Yes5 | Review submittals, Inspect Installation | Do not use this specification if 08 1100, Metal Doors and Frames is being used in specification package, Random inspection only, 5HOLD POINT-Fire rated doors require 100% inspection per IBC 110.3.6
08 1400 | 2 | Wood Doors | Yes5 | 5fire rated certifications if applicable | Yes | Verify correct material, installation per instructions against approved submittals | Yes5 | Review submittals, Inspect Installation | Random inspection only, 5HOLD POINT-Fire rated doors require 100% inspection per IBC 110.3.6
08 3100 | 2 | Access Doors and Panels | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
08 3323 | 2 | Overhead Coiling Doors | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
08 4113 | 2 | Aluminum-Framed Entrances | No | Shop drawings | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Energy Inspection per IBC 110.3.7, Random inspection unless otherwise stated
08 5113 | 2 | Aluminum Windows | No | Shop Drawings | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Energy Inspection per IBC 110.3.7, Random inspection unless otherwise stated
08 7100 | 2 | Door Hardware | Yes5 | 5fire rated certifications if applicable | Yes | Verify correct material, installation per instructions against approved submittals | Yes5 | Review submittals, Inspect Installation | Random inspection only, 5HOLD POINT-Fire rated doors require 100% inspection per IBC 110.3.6
08 8000 | 2 | Glazing | Yes6 | 6bullet resistant glass if applicable | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Random inspection only
08 9100 | 2 | Louvers | Yes | Shop drawings, Mfr instructions | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Random inspection only
09 2000 | 0 | Three-Coat Stucco System | No |  | Yes | Verify correct material, installation per instructions against approved submittals, cure times |  | Review submittal, examine substrate, inspect application, document installation | Cure times are specific
09 2116 | 2.1 | Gypsum Board Systems | No |  | Yes | Verify correct material, installation per instructions against approved submittals | Yes7 | Review submittal, examine substrate, inspect application, document installation | Random inspection only, 7HOLD POINT-Fire rated doors require 100% inspection per IBC 110.3.5
09 2913 | 1 | Gypsum Roof Board | Yes | shop drawings, certification | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation, Special storage and installation requirements | Energy Inspection per IBC 110.3.7, Random inspection unless otherwise stated
09 3013 | 1 | Ceramic Tiling | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittal, examine substrate, inspect application, document installation | Do not permit traffic over finished floor for 4 days after installation
09 5100 | 2 | Acoustical Ceiling | Yes | Shop drawings, Mfr instructions | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation | [LANL will engage] [Engage] a qualified special inspector to perform the following special inspections, Seismic installation Inspection per IBC 110.3.8; [LANL will engage] [Engage] a qualified testing agency to perform power-actuated fasteners and post-installed anchors tests and prepare test reports
09 6500 | 3 | Resilient Flooring | No |  | No-STR | Verify correct material, installation per instructions against approved submittals, installation temperature |  | Review submittals, Inspect Installation, special storage | Check special storage requirements
09 6813 | 1 | Tile Carpeting | No | Mfr test reports | No-STR | Verify correct material, installation per instructions against approved submittals, installation temperature |  | Review submittals, Inspect Installation, special storage
09 6816 | 1 | Sheet Carpeting | No | Mfr test reports | No-STR | Verify correct material, installation per instructions against approved submittals, installation temperature |  | Review submittals, Inspect Installation, special storage
09 6900 | 1 | Access Flooring | Yes | Shop drawings, Mfr certificate, installation instructions, delegated design, O&M manual, Project records | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation | Delegated design shall require LBO Stamp, special inspector to perform seismic installation Inspection per IBC 110.3.8
09 9100 | 3 | Painting | No |  | No-STR | Verify correct material, installation per instructions against approved submittals, total film thickness |  | Review submittal, examine substrate, inspect application, document installation | Receive paint film thickness reports from subcontractor.
10 1100 | 1 | Visual Display Surfaces | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 1405 | 2 | Signage, Exterior | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 1410 | 2 | Signage, Interior | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 2113.13 | 1 | Metal Toilet Compartments | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 2800 | 2 | Toilet and Bath Accessories | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 4400 | 1 | Fire Protection Specialties | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
10 5113 | 1 | Metal Lockers | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
11 1313 | 1 | Loading Dock Bumpers | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Verify Anchor bolt location
11 5311.08 | 1 | Glovebox Design | Yes | See attachment 4 to specification | N/A | Design only |  | N/A | HOLD POINT - Attend Kick-off meeting, participate in design review
11 5311.10 | 2 | Glovebox Fabrication | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but willparticipate in receipt inspection on-site | Yes8 | Receive and Inspect GFE | HOLD POINT - participate in receipt inspection on-site.
11 5311.12 | 2 | Glovebox Installation | Yes | REVIEW ALL SUBMITTALS, QA PLANS, PROCEDURES, INSTRUCTIONS, ETC. | Yes | Verify correct material, installation per instructions against approved submittals, Follow project-specific plan | Yes | MUST FOLLOW AND DOCUMENT ALL REQUIREMENTS IN SPECIFICATION | HOLD POINT - Oversight or participate in all inspections and tests, write project-specific plan.
11 5311.14 | 1 | Glovebox Gloves | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but will participate in receipt inspection on-site | Yes8 | Receive and Inspect GFE | HOLD POINT - participate in receipt inspection on-site and if applicable, on-site installation .
11 5311.16 | 1 | Glovebox Feedthroughs, Hermetically Sealed | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but will participate in receipt inspection on-site and on-site installation | Yes8 | Receive and Inspect GFE | HOLD POINT - participate in receipt inspection on-site and on-site installation.
11 5311.17 | 1 | Glovebox Instrumentation | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but will participate in receipt inspection on-site and on-site installation and testing | Yes8 | Receive and Inspect GFE | HOLD POINT - participate in receipt inspection on-site and on-site installation and testing.
11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but will participate in receipt inspection on-site | Yes8 | Receive and Inspect GFE | HOLD POINT - participate in receipt inspection on-site.
11 6100 | 0 | High Performance Laboratory Fume Hoods | Yes | ASHRAE 110 Test Reports | Yes | Verify correct material, installation per instructions against approved submittals. Witness velocity and air flow tests |  | Review submittals, Inspect Installation | HOLD POINT-Witness velocity and air flow tests
12 2113 | 1 | Horizontal Louver Blinds | No | Installation instructions | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
12 3100 | 3 | Manufactured Metal Casework | No |  | no-STR, Yes9 | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | 9CM-CE to inspect anchoring per Specification 03 1550 requirements
13 3419 | 2b | Metal Building Systems | Yes | Data sheets, Shop or erection dwgs, delegated design submittals, test and evaluation reports, product test reports, field inspection reports, Mfr and erecter certifications, testing agency | Yes | Verify correct material, installation per instructions against approved submittals, oversee testing agency |  | Review submittals, Inspect Installation | Delegated design shall require LBO Stamp, HOLD POINT-attend pre-installation meeting, HOLD POINT-Regular and Special inspection required -may include multiple portions of IBC Section 110 and Chapter 17. LIST PROJECT SPECIFIC INSPECTIONS REQUIRED.
13 4800 | 2 | Sound Vibration and Seismic Controls | Yes | Shop drawings, component certifications, as-built records | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Delegated design shall require LBO Stamp, special inspector to perform seismic installation Inspection per IBC 110.3.8
14 2413 | 1 | Hydraulic Freight Elevators | Yes | Shop dwgs, O&M manuals, Inspection Reports, Test Reports |  | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation, ASME-qualified inspector provided by the Subcontractor, conduct complete acceptance tests for approval | ASME-qualified inspector provided by the Subcontractor WITNESS POINT-elevator testing and operations
14 2423 | 1 | Hydraulic Passenger Elevators | Yes | Shop dwgs, O&M manuals, Inspection Reports, Test Reports |  | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation, ASME-qualified inspector provided by the Subcontractor, conduct complete acceptance tests for approval | ASME-qualified inspector provided by the Subcontractor WITNESS POINT-elevator testing and operations
14 4216 | 0 | Vertical Platform Lift | No |  | Yes | Verify correct material, installation per instructions against approved submittals, Witness ASME A17.1, A17.2, A18.1 and CSA B355 testing |  | Review submittals, Inspect Installation, ASME-qualified inspector provided by the Subcontractor, conduct complete acceptance tests for approval | ASME-qualified inspector provided by the Subcontractor WITNESS POINT-elevator testing and operations
21 1313 | 5 | Wet-Pipe Sprinkler Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
21 1316 | 4 | Dry-Pipe Sprinkler Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
21 1319 | 4 | Preaction Sprinkler Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
21 1326 | 4 | Deluge Fire-Suppression Sprinkler Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
21 1339 | 4 | Foam-Water Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
21 2200 | 4 | Clean Agent Fire-Extinguishing Systems | Yes | Seismic design, Shop drawings, test and inspection plan, test reports, project record documents/ as-built, O&M manual | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect Installation, inspect per NFPA requirements, test system | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
22 0529 | 3 | Hangers and Supports for Plumbing Piping and Equipment | Yes | shop drawings, WPS, PQR, WQT, Fabrication qualifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Random Inspection Only
22 0535 | 0 | Electric Heat Tracing Systems | Yes | Shop drawings, installation instructions, O&M manual, Inspection and test records | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation, perform and record tests | WITNESS POINT- Witness testing, electrical inspection per IBC 110.3.8
22 0548 | 2 | Vibration and Seismic Controls for Plumbing Piping and Equipment | Yes | Shop drawings | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Perform seismic installation Inspection per IBC 110.3.8
22 0554 | 2 | Identification for Plumbing, HVAC, and Fire Piping and Equipment | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Random Inspection only
22 0713 | 4 | Plumbing and HVAC Insulation | No | Installation Instructions | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Not to be installed until TAB is complete, Energy Inspection per IBC 110.3.7, Random inspection unless otherwise stated
22 0813 | 6 | Testing Piping Systems | Yes | Test plan, test reports | Yes | pressure testing, leak testing, Holiday testing |  | Review submittals, Perform tests per plan using acceptable equipment | WITNESS POINT -hydrostatic, pneumatic, and holiday tests
22 0816 | 4 | Disinfection of Potable Water Piping | No |  | No-STR | water quality testing, disinfection report |  | Review submittals, Perform tests per plan using acceptable equipment | Include Utilities and Infrastructure personnel. Also, same as specification 33 1300
22 1100 | 3 | Facility Water Distribution | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect and document installation per UPC and AWWA requirements | Random Inspection only
22 1316 | 3 | Sanitary Waste and Vent Piping | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect and document installation per UPC requirements | Random Inspection only
22 1343.16 | 2 | Facility Wet-Well Packaged Sewage Pumping Stations (Interior) | No | Service Engineer certification report, | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect installation, provide factory coverage as required | Factory WITNESS POINT-check installation and operation, provide a minimum of 4 hours per pump station of training to operating personnel on O&M, C. Provide a report by the service engineer certifying that equipment has been installed and is operating correctly
22 1413 | 2 | Facility Storm Drainage Piping | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect and document installation per UPC requirements | Random Inspection only
22 1500 | 3 | Compressed-Air Systems | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect and document installation per UPC requirements, ensure compliance with examination requirements of ASME B31.9 | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated
22 3700 | 0 | Domestic Water Heaters | Yes | Delegated seismic design, Factory test reports, Site test reports | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect and document installation per UPC requirements, ensure compliance with examination requirements of ASME. | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests, HOLD POINT-Factory test and inspect ASME water heaters to ASME Boiler and Pressure Vessel Code, Hydrostatically test water heaters to minimum of one and one-half times pressure rating before shipment
22 4200 | 5 | Plumbing Fixtures | No | Mfr's installation Instructions, Mfr's Certificate | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation
22 6313 | 0 | Gas Piping for Laboratory Facilities | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect and document installation, ensure compliance with examination requirements of ASME. | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated
22 6600 | 0 | Chemical-Waste Systems for Laboratory | Yes | WPS, PQR, WQT, shop drawings, weld inspection procedures and weld inspection reports | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect and document installation, ensure compliance with examination requirements of ASME. | MANY ITEMS TO INSPECT IN THIS SECTION
23 0593 | 3 | Testing, Adjusting, and Balancing for HVAC | Yes | TAB certifications, procedures, field reports, draft and final test reports | Yes | Witness testing by either CM-CE or start-up personnel. |  | TAB Subcontractor | This is required to be a LANL subcontract. WITNESS POINT-testing
23 1123 | 3 | Facility Natural-Gas Piping | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals and ensure compliance with Uniform Plumbing Code, Uniform Mechanical Code, and NFPA 54 requirements. | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated
23 2113 | 4 | Hydronic Piping | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect and document installation, ensure compliance with examination requirements of ASME B31.9. | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated, Paragraph 3.4 I should reference firestopping specification, Paragraph 3.5 B should reference pipe testing for holiday testing.
23 2123 | 0 | Hydronic Pumps | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, Inspect Installation | Random Inspection Only
23 2215 | 0 | Steam and Condensate Heating Piping and Specialties | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect and document installation, ensure compliance with examination requirements of ASME B31.9 and AWS D1.1. | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated
23 2300 | 2 | Refrigerant Piping | Yes10 | 10bonding, fusion, brazing or welding procedures and qualifications | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, Inspect and document installation, ensure compliance with examination requirements of ASME ASME B31.5, ASHRAE 15, and ASHRAE 34. | Piping Inspection per IBC 110.3.8, Random inspection unless otherwise stated
23 2500 | 2 | HVAC Water Treatment | No |  | No-STR | Witness cleaning and chemical balance by either STR or start-up personnel. |  | Review submittals, clean and test system, provide training and consulting service. | Do not fill or flush piping systems until source of water supply is approved by LANL STR, A. Provide consulting services from chemical supplier for a period of 1 year, furnish xx hour training course
23 3101 | 0 | HVAC Ducts | Yes | WPS, PQR, WQT, shop drawings, pressure test reports, Certificate of Conformance (COC) | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittal and ensure compliance with SMACNA - HVAC Duct Construction Standards - Metal and Flexible, and NFPA 90A | Random inspection only unless otherwise specified, WITNESS POINT- testing on 25 % of representative duct systems
23 3225 | 2 | Bag-in Bag-out Housings | Yes8 | 8If requested to participate | Yes8 | 8If requested to participate, but will participate in receipt inspection on-site | Yes8 | Review submittals, Install in accordance with ASME AG-1, ASME NQA-1 requirements as applicable. | HOLD POINT - participate in receipt inspection on-site, LANL is responsible for having installed HEPA filers and chemical adsorbers in-place tested
23 3300 | 0 | Air Duct Accessories | Yes | product data, shop drawings, install instructions, WPS, PQR, WQT | Yes | Verify correct material, installation per instructions against approved submittals | Yes | SMACNA - HVAC Duct Construction Standards - Metal and Flexible, UL 555, UL 555S, NFPA 90A, NFPA 90B, and NFPA 92A | Fire and smoke installation inspection per IBC 110.3.6, Random inspection unless otherwise stated, WITNESS POINT-operation test of dampers, access doors,and turning vanes.
23 3400 | 0 | HVAC Fans | Yes | Delegated fan design, shop drawings, installation instructions, Mfr certificate, factory test reports, site test reports | Yes | Verify correct material, installation per instructions against approved submittals, witness testing by either CM-CE or start-up personnel. |  | Review submittals, install per specification, engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections, Perform site tests and inspections per 3.3 B, | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 3416 | 0 | Centrifugal HVAC Fans | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  |  | Note: Section 3.3.A to be part of commissioning operational checks.
23 3713 | 0 | Diffusers, Registers & Grills | No |  | No-STR
23 3816 | 0 | Fume Hoods | No | product data, shop drawings, install instructions, factory and site test reports and certificates | Yes | Factory inspections and tests if requested, receipt inspection, and site inspections and tests |  | Review submittals, install per specification | witness factory inspections and tests if requested, perform joint receipt inspection, and WITNESS POINT-site inspections and tests
23 4133 | 2 | High Efficiency Particulate Filtration | Yes | Certification documentation, C of C, QA Plan or verify Mfr on LANL IESL, Factory test results | Yes | Factory inspections and tests if requested, receipt inspection, and site inspections and tests, Verify correct material, installation per instructions against approved submittals, witness testing by either CM-CE or start-up personnel. |  | Review submittals, receipt inspection, install per specification, Comply with AG-1 | witness factory inspections and tests if requested, perform joint receipt inspection, and WITNESS POINT-site inspections and tests
23 6200 | 0 | Packaged Compressor and Condenser Units | Yes | Product data, delegated design, shop drawings, installation instructions, O&M Manual, factory test documentation | Yes | Factory test and inspection documentation, field inspections and tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 6509 | 1 | Induced-Draft Cooling Towers--Steel | Yes | Product data, shop drawings, installation instructions, O&M Manual | Yes | Verify correct material, installation per instructions against approved submittals witness tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Supplier to provide aminimum of 4 hours O&M training. HOLD POINT - Special Inspection Required, 1704.3, perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 6511 | 1 | Induced-Draft Cooling Towers--Fiberglass | Yes | Product data, shop drawings, installation instructions, O&M Manual | Yes | Verify correct material, installation per instructions against approved submittals witness tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Supplier to provide aminimum of 4 hours O&M training. HOLD POINT - Special Inspection Required, 1704.3, perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 7300 | 0 | Indoor Central-Station Air Handling Units | Yes | Product data, delegated design, shop drawings, installation instructions, O&M Manual, factory test documentation | Yes | Factory test and inspection documentation, field inspections and tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 7413 | 2 | Packaged, Outdoor, Central-Station Air-Handling Units | Yes | Product data, shop drawings, installation instructions, O&M Manual | Yes | Verify correct material, installation per instructions against approved submittals witness tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Supplier to provide a minimum of X hours O&M training. HOLD POINT-perform piping and seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 8119 | 0 | Self-Contained Air-Conditioners | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  |  | Factory representative to inspects, test, adjust (no time frame given)
23 8123 | 0 | Computer-Room Air-Conditioners | Yes | Product data, delegated design, shop drawings, installation instructions, O&M Manual | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification, provide Mfr representative for testing | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
23 8239 | 0 | Unit Heaters | Yes | Product data, delegated design, shop drawings, installation instructions, O&M Manual, factory test documentation | Yes | Factory test and inspection documentation, field inspections and tests |  | Review submittals, ensure factory tests perfomed and documented, install, inspect and test per specification | Delegated design shall require LBO Stamp, HOLD POINT-perform seismic installation Inspection per IBC 110.3.8 before testing, WITNESS POINT-all tests
25 5000 | 1 | Integrated Automated Facility Controls | No | Shop drawings, Point verification and sensor calibration forms | No-STR | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification, provide Mfr representative for testing | Installer shall be factory certified, records drawings, Preooperational acceptance test, functional performance test, eighty hours (80) factory representative for training , Work to be monitored by commissioning
26 0519 | 4 | Low-Voltage Electrical Power Conductors and Cables | Yes | Cable pulling records and inspection and test reports | Yes | Verify correct material, installation per instructions against approved submittals. Witness megohm tests, continuity, 10% of all torque connections | Yes | Review submittals, install, inspect and test per specification | Subcontractor quality control to document inspections and tests; electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated; WITNESS POINT-all tests
26 0526 | 1 | Grounding and Bonding for Electrical Systems | Yes | shop drawings, Inspection and test reports | Yes | Verify correct material, installation per instructions against approved submittals. Witness resistance tests. | Yes | Review submittals, install, inspect and test per specification | Subcontractor quality control to document inspections and tests; electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated; WITNESS POINT-all tests
26 0529 | 4 | Hangers and Supports for Electrical Systems | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification | Random inspection unless otherwise stated
26 0533 | 4 | Raceways and Boxes for Electrical Systems | No |  | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated; HOLD POINT-Inspection prior to covering up electrical system, i.e. underground, in walls, etc.
26 0536 | 2 | Cable Trays for Electrical Systems | Yes | shop drawings, istallation instructions, certification statement | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, install, inspect and test per specification, provide notification | electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated; HOLD POINT-Inspection prior to covering up electrical system, i.e. underground, in walls, etc.
26 0548 | 2 | Vibration and Seismic Controls for Electrical Systems | No | Catalog data, material list, test reports, shop drawings, component certifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification, provide notification | Seismic and electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated; HOLD POINT-Inspection prior to covering up electrical system, i.e. underground, in walls, etc.
26 0553 | 2 | Identification for Electrical Systems | No | installation instructions | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install, inspect and test per specification, provide notification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated
26 0700 | 2 | Induction Motors – 500 HP and Smaller | Yes | Certification report, factory test reports, field inspection reports, Mfr field certification report, when applicable | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, install, inspect and test per specification, provide notification and documentation of inspections, provide Mfr field inspections as applicable | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Note: Section 3.5 to be part of commissioning operational checks.
26 0813 | 1 | Electrical Acceptance Testing | Yes11 | Certifications, test plans, test reports, | Yes11 | Yes11 Tests witnessed by Start-up/Commisioning and/or CM-CE as agreed upon on the specific project |  | Review submittals, install, inspect and test per specification, provide notification | Yes11 Covered by Start-up/Commisioning and/or CM-CE as agreed upon on the specific project, WITNESS POINT-all tests, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated
26 2213 | 2 | Low Voltage Distribution Transformers | Yes11 | Certification reports, O&M manual | Yes11 | Yes11 Tests witnessed by Start-up/Commisioning and/or CM-CE as agreed upon on the specific project | Yes | Review submittals, install, inspect and test per specification, provide notification | Yes11 Covered by Start-up/Commisioning and/or CM-CE as agreed upon on the specific project, WITNESS POINT-all tests, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated
26 2300 | 2 | Low-Voltage Switchgear | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Perform dimensional field measurements and notify STR, provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training for up to three owner’s representatives at the project site
26 2413 | 3 | Switchboards | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Random witness of receipt inspection, Verify correct material, installation per instructions against approved submittals | Yes | Perform dimensional field measurements and notify STR, provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training for up to three owner’s representatives at the project site
26 2416 | 2 | Panelboards | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing, load balance reports | Yes | Perform dimensional field measurements and notify STR, provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training for up to three owner’s representatives at the project site, WITNESS POINT-load balancing
26 2419 | 3 | Motor Control Centers | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing, | Yes | Perform dimensional field measurements and notify STR, provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training for up to three owner’s representatives at the project site, WITNESS POINT-all tests
26 2500 | 2 | Enclosed Bus Assemblies | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing, load balance reports | Yes | Perform dimensional field measurements and notify STR, provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training for up to three owner’s representatives at the project site, WITNESS POINT-all tests
26 2713 | 3 | Electricity Metering | No |  | No-LANL U&I, ES-DE |  |  | Review submittals, install per specification | LANL Utilities will inspect, test, program, and adjust the meter, meter wiring, Ethernet communication wiring, and Ethernet communications interface, LANL ES-DE Process and Automation Team will inspect and test the RS-485 communication wiring and communications interface
26 2726 | 4 | Wiring Devices | No |  | Yes | Verify correct material, installation per instructions against approved submittals, electrical polarity and grounding testing, GFCI testing |  | Review submittals, install per specification, test per Sections 3.8. and 3.9 | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, WITNESS POINT-all tests
26 2816 | 3 | Enclosed Switches and Circuit Breakers | Yes | Certifications | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, receipt inspection, install per specification, test per Sections 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, WITNESS POINT-all tests
26 2913 | 2 | Enclosed Controllers | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, test per NECA 230, torque connections |  | Review submittals, receipt inspection, install per specification, test per Sections 3.5 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, WITNESS POINT-all tests
26 2923 | 2 | Variable Frequency Motor Controllers | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing | Yes | Provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.4 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide one full work day of training , WITNESS POINT-all tests
26 3334 | 0 | Stored Emergency Power Supply System | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing | Yes | Provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 and 3.6 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, WITNESS POINT-all tests
26 3353 | 1 | Static Uninterruptible Power Supply | Yes | Certification reports, O&M manual, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals, electrical testing | Yes | Provide factory tests, provide Mfr representative for inspection and testing, inspect installation and document Section 3.5 and 3.6 | Receipt inspection, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Subcontractor to provide 12 hours of training (2 days) , WITNESS POINT-all tests
26 4100 | 1 | Facility Lightning Protection | Yes | Certifications, shop drawings, test reports, project record documents (as-builts) | Yes | Verify correct material, installation per instructions against approved submittals, fall of potential ground test | Yes | Review submittals, receipt inspection, install per specification, test per Sections 3.7 | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, HOLD POINT- Final installation inspection and tests
26 4115 | 1 | Lightning Protection for Explosive Facilities | Yes | Certifications, shop drawings, test reports, project record documents (as-builts) | Yes | Verify correct material, installation per instructions against approved submittals, fall of potential ground test | Yes | Review submittals, receipt inspection, install per specification, test per Sections 3.11 | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, HOLD POINT- Final installation inspection and tests
26 4300 | 0 | Surge Protective Devices | Yes | Certification reports, Installation instructions, shop drawings, test reports, wiring diagrams | Yes | Verify correct material, installation per instructions against approved submittals | Yes | Review submittals, install per specification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,
26 5100 | 4 | Interior Lighting | Yes | Certification Report | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, install per specification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, SPARE PARTS LISTED
26 5200 | 5 | Emergency Lighting | Yes | Certification Report | Yes | Verify correct material, installation per instructions against approved submittals, footcandle test |  | Review submittals, install per specification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, SPARE PARTS LISTED
26 5600 | 4 | Exterior Lighting | Yes |  | Yes | Verify correct material, installation per instructions against approved submittals, footcandle test |  | Review submittals, install per specification | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, SPARE PARTS LISTED
27 1000 | 3 | Structured Cabling | Yes | Installer certifications, cable routing records, test records | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, LANL Telecommunications group may spot check
27 1500.18 | 1 | Protected Transmission System Rough-In | Yes | Certifications, as-built dwgs | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Certification as BICSI Installer Level II, Review submittals, install per specification, perform tests and provide test reports | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated, Continuity acceptance test, PTS fiber termination and testing will be performed by LANL “Q”-CLEARED personnel only
27 3000 | 3 | Voice Communications | Yes | As-built dwgs, test and inspection records | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.11
28 0528 | 3 | Pathways for Electronic Security | Yes | As-built dwgs, test and inspection records | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.13
28 1321 | 3 | Administrative Access Control System Rough-In | Yes | As-built dwgs, test and inspection records | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.7
28 3100 | 6 | Fire Detection and Alarm | Yes | Certifications, shop drawings, test plan test reports, O&M manual, project record documents (as-builts) | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Delegated design shall require LBO Stamp, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.7, WITNESS POINT-Fire Protection Division, and Facility Operations Director
28 3110 | 2 | Fire Detection and Alarm – Addition to Existing | Yes | Certifications, shop drawings, test plan test reports, O&M manual, project record documents (as-builts) | Yes | Verify correct material, installation per instructions against approved submittals, Acceptance testing |  | Review submittals, install per specification, perform tests and provide test reports | Delegated design shall require LBO Stamp, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.7, WITNESS POINT-Fire Protection Division, and Facility Operations Director
31 2000 | 5 | Earth Moving | Yes | Certifications for bedding, base course, stone, compaction tests reports, tracing wire tests | Yes | Verify correct material, installation per instructions against approved submittals, witness compaction tests and tracer wire. |  | Review submittals, install per specification, Provide approved third party testing organization,to perform tests and provide test reports | Tracer wire testing, Random inspection only, see frequency schedule HOLD POINT- Special Inspection required per 1704.7
31 2323.33 | 5 | Flowable Fill | Yes | Material certifications, batch tickets, field test reports | Yes | Verify material matches specification requirements |  | Verify material matches specification requirements, provide batch tickets and testing agency if required | testing not required unless specifically required, rasndom inspection only
32 1216 | 3 | Asphalt Paving | Yes | Material certifications, Mix design, laboratory test reports, certifications, batch tickets, field test reports | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Verify subsurface is ready, verify material matches specification requirements, provide batch tickets and testing agency, test per Section 3.8 | Submit the approved material certifications and mix designs data to the LANL Utilities and Institutional (U&I) roads system engineer, WITNESS POINT-asphalt testing random inspection only.
32 3100 | 2 | Fences and Gates | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals | Note: CM-CE to inspect welding on security fencing, other inspection by CM-CE as agreed upon by project, grounding inspection per NEC
32 3113 | 3 | Chain Link Fences and Gates | No |  | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals | Note: CM-CE to inspect welding on security fencing, other inspection by CM-CE as agreed upon by project, grounding inspection per NEC
32 8400 | 3 | Planting Irrigation | No | Installation instructions, O&M manual, record drawing | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals
32 9219 | 3 | Seeding | No | Certifications, installation instructions | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals | Seeded areas will be reviewed for acceptance by LANL when final stabilization has been achieved such that: "All soil disturbing activities at the site have been completed and a uniform (e.g., evenly distributed, without large bare areas) perennial vegetative cover with a density of 70 percent of the native background vegetative cover for the area has been established on all unpaved areas and areas not covered by permanent structures, or equivalent permanent stabilization measures (such as the use of riprap, gabions, or geotextiles) have been employed."
32 9223 | 3 | Sodding | No | Certification, schedule | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals | Sodded lawns to be maintained not less than 30 days after final acceptance, or through the September 15 growing season, whichever is longer
32 9300 | 4 | Plants | No | Schedule, material list | No-STR | Verify correct material, installation per instructions against approved submittals |  | Verify correct material, installation per instructions against approved submittals
33 0513 | 6 | Manholes and Structures | No | Certifications, NMED, Alarm system data, Exfiltration test | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, NMED, Alarm system data, Exfiltration test, inspect per requirements, test | Note: Precast may require Special Inspection per IBC Section 1704.4, WITNESS POINT-Exfiltration test
33 1000 | 5 | Water Utilities | Yes | WPS, PQR, WQT, installation instructions | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test | Note: Tie-in to existing piping systems will be performed by LANL U&I group, Mechanical inspection per IBC 110.3.8, Random inspection unless otherwise stated
33 1300 | 4 | Disinfecting of Water Utility Distribution [22 0816] | No |  | No-STR | water quality testing, disinfection report |  | Review submittals, Perform tests per plan using acceptable equipment | Include Utilities and Infrastructure personnel. Also, same as specification 22 0816
33 3000 | 6 | Sanitary Sewerage Utilities | Yes | WPS, PQR, WQT, installation instructions | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test | Note: Tie-in to existing piping systems will be performed by LANL U&I group, Mechanical inspection per IBC 110.3.8, Random inspection unless otherwise stated
33 3200 | 6 | Wastewater Utility Pumping Stations | Yes | Acceptance report | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Review submittals, inspect installation, and perform tests | U&I Group will perform acceptance inspection, testing, adjusting and tie-in of lift station, factory trained service engineer to be present to check installation and operation and to provide a minimum of 4 hours per pump station of training
33 4000 | 3 | Storm Drainage Utilities | Yes | WPS, PQR, WQT, installation instructions, U&I inspection report | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test | Note: Tie-in to existing piping systems will be performed by LANL U&I group, U&I will inspect interior of storm drainage lines beyond the building wall with video camera for piping integrity and proper construction, mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated
33 5100 | 9 | Natural-Gas Distribution | Yes | WPS, PQR, WQT, installation instructions, U&I inspection report | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test | Note: Tie-in to existing piping systems will be performed by LANL U&I group, mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated
33 6300 | 4 | Steam Energy Distribution | Yes | WPS, PQR, WQT, installation instructions, U&I inspection report | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test, corrosion control installation and testing | Note: Tie-in to existing piping systems will be performed by LANL U&I group, mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated
33 7119 | 3 | Electrical Underground Ducts and Manholes | Yes | Test reports from Subcontractor | Yes | Verify correct material, installation per instructions against approved submittals, witness tests. |  | Submit Certifications, inspect per requirements, test, corrosion control installation and testing | LANL U&I will furnish, install, and test medium-voltage power cables, and at electrical manholes containing energized cables, will make penetrations into manholes and will install the last 5 ft of duct into the manhole using materials furnished by Subcontractor, Electrical inspection per IBC 110.3.8, Random inspection unless otherwise stated,tests per Section 3.7, WITNESS POINT-all tests
33 7311 | 3 | Pad-Mounted Transformer Rough-In | No |  | Yes | Concrete inspection per 03 3001 |  | Same as responsibilities for 03 3001 | A. LANL Utilities & Institutional (U&I) will furnish, install, and test the pad-mounted transformer and associated medium-voltage cables
33 7711 | 3 | Pad-Mounted Switch Rough-In | No |  | Yes | Concrete inspection per 03 3001 |  | Same as responsibilities for 03 3001 | A. LANL Utilities & Institutional (U&I) will furnish, install, and test the pad-mounted switch and associated medium-voltage cables
40 0511 | 1 | Compression Fittings on Copper and Stainless Steel Tubing | No |  | Yes | Verify correct material, installation per instructions against approved submittals, leak tests. |  | Submit Certifications, inspect per requirements, test | Installers of compression fittings shall be one-time trained on their assembly by the manufacturer or an authorized distributor, or through a formal LANL course, mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated
40 0513 | 0 | Process Piping | Yes | Unlisted component analysis, NDE procedures, WPS, WPR WQT,Examiner qualification, Inspection and Test reports | Yes | Verify correct material, installation per instructions against approved submittals, monitor examiner, |  | Review submittals, receipt inspection, install per specification, submit examiner, final cleaning, perform inspections and tests | Mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated. WITNESS POINT-monitor examinations
40 0527 | 2 | Piping and Tubing Inspection Checklist | No |  | Yes | Monitor Subcontractor |  | Utilize checklist to perform installation and inspection | Mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated. WITNESS POINT-monitor examinations
41 2213.13 | 2 | Bridge Cranes | Yes | Material certifications, NDE procedures, WPS, WPR WQT, shop drawings, QA Plan, design data, O&M manual, examiner qualification, inspection and test reports | Yes12 | 12If requested to participate off-site, but will participate in receipt inspection and on-site installation. | Yes12 | Receive and Inspect GFE, If involved with procuring crane, full involvemenmt in specifications | HOLD POINT - participate in receipt inspection and on-site installation, Mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated. WITNESS POINT-all on-site tests
41 2225 | 1 | Hoist and Trolleys | Yes | Material certifications, NDE procedures, WPS, WPR WQT, shop drawings, QA Plan, design data, O&M manualExaminer qualification, Inspection and Test reports | Yes12 | 12If requested to participate off-site, but will participate in receipt inspection and on-site installation. | Yes12 | Receive and Inspect GFE, If involved with procuring crane, full involvemenmt in specifications | HOLD POINT - participate in receipt inspection and on-site installation, Mechanical inspection per IBC 110.3.8, random inspection unless otherwise stated. WITNESS POINT-all on-site tests
43 3113.37 | 1 | High Efficiency Gas Purification Filters | Yes | Certificate of conformance, certification documentation, QA program, installation instructions, factory test reports | Yes | Verify correct material, installation per instructions against approved submittals |  | Review submittals, receipt inspection, install per specification | Level C packaging,
43 4113 | 1 | Gas and Liquid Pressure Vessels | Yes12 | 12If requested to participate | Yes12 | 12If requested to participate off-site, but will participate in receipt inspection. | Yes12 | Receive and Inspect GFE, If involved with procurement, full involvemenmt in specifications | HOLD POINT - participate in receipt inspection
43 4116 | 1 | Atmospheric Tanks and Vessels | Yes12 | 12If requested to participate | Yes12 | 12If requested to participate off-site, but will participate in receipt inspection. | Yes12 | Receive and Inspect GFE, If involved with procurement, full involvemenmt in specifications | HOLD POINT - participate in receipt inspection
For LANL reference, do not delete: Project TIP based on LANL template dated September, 2013