SECTION 03 1534

POST-INSTALLED CONCRETE ANCHORS – NORMAL CONFIDENCE

*************************************************************************************************************

LANL MASTER SPECIFICATION

This section includes field installation and inspection requirements for normal-confidence post-installed (PI) anchors.  These inspection requirements are not to be confused with the Special Inspections required by associated ICC-ES reports (ESRs), which should appear in a project’s Statement of Special Inspections.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Structural POC.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This Section was developed for ML-3 and ML-4 projects.  For ML-3 applications, additional requirements may be added if additional confidence is desired.  Section 03 1512, which is intended for ML-1 and ML-2 installations, has examples of possible changes that can be made to increase confidence, or it may be used as the starting point when the utmost confidence is desired.  At a minimum, for ML-3 applications, it is recommended that testing be mandated in this Section to provide added assurance as opposed to increased rigor on procurement.

This section is not required for anchors meeting the definition of “non-structural” contained in ESM Chapter 5 Section II Appendix A; instead, non-structural anchorage need only be designed, purchased, and installed per the IBC and manufacturer’s instructions.  At time of writing, Appendix A (A.7) states:

A. 	Non-structural anchors support very light loads and subsequently are exempt from being “designed anchors.”  Post-installed concrete anchors for use in non-structural applications shall be chosen from qualified anchors in compliance with the IBC and ESM Chapter 16, IBC Program.

B. 	A non-structural application must meet the following criteria:

1. 	PC-1 mechanical and electrical components where flexible connections between the components and associated ductwork, piping, and conduit are provided and that are mounted at 4 ft or less above a floor level and weight 400 lb or less.

2. 	PC-1 mechanical and electrical components weighing 20 lb or less where flexible connections between the components and associated ductwork, piping, and conduit are provided, or for distribution systems weighing 5 lb/ft or less.

*************************************************************************************************************

PART 1 GENERAL

# 1.1	SECTION INCLUDES

- The technical requirements for purchasing post-installed concrete anchors for Management Level [ML-3 and] ML-4 and Performance Category (PC)-1 and PC-2 structures, systems, and components (SSC). This specification applies to expansion, adhesive, undercut, and screw.

- The technical requirements for field installation and inspection of post-installed (PI) anchors (including anchor systems consisting of steel reinforcing bars/dowels and grout) in concrete for Management Level (ML) 3 and 4 and PC-1 and 2 SSCs. The inspection requirements of this Section do not apply to non-structural anchors (LANL definition).

- Does not cover cast-in-place anchors, design of post-installed anchorage, or purchase of tools or equipment required for installation or testing.

# 1.2	RELATED SECTIONS

- 01 4000 Quality Requirements

- [03 1512 Post-Installed Concrete Anchors – High Confidence]

- [03 6000  Grout]

- [05 1000  Structural Metal Framing (baseplates, bearing plates, leveling plates).]

# 1.3	DEFINITIONS

Definitions of anchors per ACI 355.2 (as amended by ICC AC 193) apply, and all notations are identical to those used in that document and in ACI 318 Appendix D.  Where additional terms or notations are used, their definitions are included in this Section.

*************************************************************************************************************

NOTE:  If the Project includes non-structural anchors, they must be identified as such by the Engineer of Record (EOR) on the construction drawings.  If the Project does not include non-structural anchors then delete bracketed text.

NOTE:  Prior to concluding an anchor is non-structural, ensure LANL ESM Ch. 5, Sect. II, App. A, para. A.5.B (i.e., ‘II over I’) has been considered.

*************************************************************************************************************

[Non-structural anchors, per Engineering Standards Manual (ESM) Chapter 5, Section II, Appendix A, and ESM Ch. 16, Section 16, IBC Program, are defined as follows and need only be designed and installed per the respective ICC ESR.

Non-structural anchors are those that anchor PC-1 mechanical and electrical components with flexible connections between the components and associated distribution system (e.g., ductwork, piping, conduit, etc.), and can be categorized under one of the following conditions:

- Mounted at 4 ft or less above a floor level and weigh 400 lb or less, or

- Weigh 20 lb or less, or

- Weigh 5 lb/ft or less if the component(s) is a distribution system.]

**********************************************************************************************************

NOTE:  If Project includes an anchorage system consisting of grout and concrete reinforcing steel (i.e., rebar /dowel) then the EOR must ensure completion of the following:

- Design calcs for the anchorage system(s) in accordance with applicable portion of ACI 318.

- Specification of the elements of anchorage system(s) consistent w/design calcs:

  - 03 6000, Grout, utilized (i.e., edit template and include in Proj. Spec) and its strength stated.

  - The rebar specified by editing para. 2.2 (below).  If the rebar will be welded-to (after installation), see ACI 318, para. 3.5.2.

- The requirements for the installation of the anchorage system are included herein (ref. para. 3.5).

*************************************************************************************************************

# 1.4	REFERENCES

| ACI 355.2 | Qualification of Post-Installed Mechanical Anchors in Concrete |
| --- | --- |
| ACI 355.4 | Qualification of Post-Installed Adhesive Anchors in Concrete (ACI 355.4) and Commentary |
| ACI 318 | Building Code Requirements for Structural Concrete and Commentary |
| ASTM A 36 | Standard Specification for Carbon Steel |
| ASTM A 193 | Standard Specification for Alloy-Steel Bolting Materials for High-Temperature or High Pressure Service and Other Special Purpose Applications |
| ASTM A 615 | Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement |
| ASTM B633 | Standard Specification for Electrodeposited Coatings of Zinc on Iron and Steel |
| ASTM C 928 | Standard Specification for Packaged, Dry, Rapid-Hardening Cementitious Materials for Concrete Repairs |
| ASTM E488 | Standard Test Methods for Strength of Anchors in Concrete and Masonry Elements |
| ASTM E1512 | Standard Specification for Testing Bond Performance of Bonded Anchors |
| ASTM F 436 | Standard Specification for Hardened Steel Washers |
| DOE-STD-1021 | Natural Phenomena Hazards Performance Categorization Guidelines for Structures, Systems, and Components |
| IBC | International Building Code |

Other ICC Documents

| ICC ES Reports | International Code Council Evaluation Services Reports (ESRs)* |
| --- | --- |
| ICC ESR-1545 | Hilti HSL-3 Carbon Steel Metric Heavy Duty Concrete Anchors in Concrete (August 2005 or later) |
| ICC ESR-1546 | Hilti HDA Carbon Steel and Stainless Steel Metric Undercut Anchors in Concrete (November 2005 or later) |
| ICC ESR-1917 | Hilti Kwik Bolt TZ Carbon and Stainless Steel Anchors in Concrete (September 2005 or later) |
| ICC ESR-2322 | Hilti HIT-RE 500-SD Adhesive Anchor Systems (November 2007 or later) |
| ICC ESR-3027 | Hilti Kwik HUS-EZ Carbon Steel Screw Anchors for Use in Cracked and Uncracked Concrete (December 2010 or later) |
| ICC AC 193 | Acceptance Criteria for Mechanical Anchors in Concrete Elements |
| ICC AC 308 | Acceptance Criteria for Post-installed Adhesive Anchors in Concrete Elements |

*  The ESR’s Scope must include the specific edition of the IBC applicable to the project.

# 1.4	SUBMITTALS

- Verification Documents

The following verification documentation shall be submitted by the supplier for any anchors not in Table 2.1, Approved Anchors:

  - Submit the ICC-ES Evaluation Report (ESR) for each product.

  - Submit technical documentation of the product, including, but not limited to: anchor design strength in shear and tension, minimum spacing and edge distances, anchor dimensions, materials and coatings used, installation instructions, and all required design parameters.

  - For chemical anchors, also submit information on adhesives, including, but not limited to: elevated temperature versus load capacity effects (80-350(F), fire resistance, radiation effects, sunlight exposure effects, adverse chemical reactions, storage instructions, missing system, injection systems, mixing rations, gel time, setting time, shelf life, and hole cleanliness requirements.

  - For chemical anchors, also submit threaded rod or deformed reinforcing bar information as applicable, including geometry, shape, material properties, and any special requirements.

  - Submit shipping, handling, and packaging procedures as described in Para 1.6 below.

  - Submit cleaning and coating documentation for review.

  - Submit quality assurance program to meet requirements of Para 1.5.

  - Certificates of Compliance certifying that the anchors meet the requirements of this specification.

## QUALITY ASSURANCE

- All material shall be procured as commercial material. The same quality assurance requirements shall be passed down to any lower tier subcontractor.

- The design (and installation) shall be in full compliance with the “Conditions of Use” section of applicable ICC-ESR reports. Any departures must be acknowledged via a formal variance in accordance with ESM Chapter 1 Section Z10.

- The inspection, testing, and documentation requirements for same contained herein are the responsibility of the Subcontractor installing PI anchors (i.e., versus the PI-anchor inspection requirements contained in a project’s Statement of Special Inspections, which is the responsibility of the LANL Special Inspector).

- To reduce delays and potentially redundant LANL inspection effort, notify LANL Inspectors at least 24 hours prior to any Subcontractor installation, inspection, or testing activities associated with Special Inspection and treat such tasks as hold/witness points.

## PACKAGING, SHIPPING, HANDLING, AND STORAGE

- Establish and maintain controls for material handling and storage during fabrication and preparation for shipment to prevent damage and deterioration.

- Prior to packaging an item, remove dirt, oil residue, water, metal chips, or other contamination.

- If nuts, washers, sleeves and anchors are packaged and shipped unassembled, any components that are damaged during handling, shipping & storage, or that don’t fit properly (upon assembly during anchor installation), shall be replaced at no cost to LANL.

- Bolting of different types and/or different sizes shall be packaged separately.

PART 2 	PRODUCTS

## Anchor types including nuts and washers: expansion, adhesive, and undercut and their intended Natural Phenomena Hazards (NPH) Performance Category.

*************************************************************************************************************

Per the ICC-ES Report for the Hilti Kwik HUS-EZ (i.e., ESR-3027), a ductile anchorage design cannot be achieved with this product; therefore, the Engineer of Record must ensure that, for the application in question, ESM Ch. 5, Sect. II, App. A both (a) permits the use of a brittle anchorage, and (b) design complies with provisions for brittle anchorage design.

*************************************************************************************************************

##### A. 	Anchors not listed in Table 2.1 but allowed by other LBO-approved Master or project-specific spec sections may be used, and shall be inspected per the LBO acceptance report (typically ESR, but may be LANL-specific document).

Table 2.1

Approved Anchors

| Anchor Type | Manufacturer | Product Name | Acceptance Report | NPH Performance Category |
| --- | --- | --- | --- | --- |
| Expansion: |  |  |  |  |
| Drop-in | not allowed | n/a | n/a | n/a |
| Heavy-Duty Sleeve | Hilti | HSL-3 | ESR-1545 | PC-1 and PC-2 |
| Wedge | Hilti | Kwik Bolt TZ | ESR-1917 | PC-1 and PC-2 |
| Adhesive | Hilti | HIT-RE 500-SD | ESR-2322 | PC-1 and PC-2 |
| Adhesive | Hilti | HIT-HY 150 MAX-SD | ESR-2262 | PC-1 and PC-2 |
| Screw | Hilti | Kwik HUS-EZ | ESR-3027 | PC-1 and PC-2 |
| Undercut | Hilti | HDA | ESR-1546 | PC-1 and PC-2 |
| Undercut | Drillco | Maxi-Bolt1 | See below | PC-3 and PC-42 |

1For Drillco Maxi-Bolts, LANL accepts the stud-type and flush-mount (coupling-type).

2PC-3 and PC-4 anchors may also be used in lower NPH Performance Category installations.

Note to installer:  In rad and cleanroom areas, use of HILTI dust removal system (vacuum attachment) HIT-DRS (Item No. 362323) during hole blow-out with air is normally required.  Consider purchase along with anchors if DRS is not on hand.

- Supply anchor products of the following types:

- Mechanical anchors: undercut, expansion (drop-in, heavy-duty sleeve, wedge, screw), and screw anchors.

- Bonded or adhesive anchor systems: chemical anchors.

- All material shall be commercial material.

- All anchors shall have a current ICC-ES Evaluation Service Report that contains recommended design capacities [Drillco excepted].  Load tests used in the ICC-ES Reports shall be performed in accordance with ICC AC 193 and ASTM E488 for mechanical anchors; AC 308; and ASTM E1512 for adhesive anchors.

- Provide carbon steel or stainless steel anchors as specified. Submit documentation of materials used.

- Outdoor anchors, or those used in a moist environment, shall be of a material, or possess a protective coating, compliant with the associated Condition of Use in the respective ICC-ES Report [(for the Drillco Maxi-Bolt, comply with manufacturer’s guidance / requirements)].

- Anchor head shall be stamped, or otherwise permanently marked, with the total anchor length of a length code that can be related to the total anchor length.

- Anchor head, nut, or washer shall not be marked with a letter “Q” or be marked with the color blue. If the letter “Q” is contained in the length code, those anchors shall be excluded from use.

- Drypack mortar:  Packaged, dry, rapid-hardening concrete or mortar in accordance with ASTM C928; 7-day strength of [4,000 psi] [5000 psi].

- [Concrete reinforcing steel (rebar /dowel):  ASTM A 615, grade 60 deformed bars.]

## TEST AND INSPECTIONS

- The bolt supplier is responsible for performing inspections, as necessary to ensure compliance with all material and documentation requirements identified in this Specification. Documentations of inspections will be available to LANL if requested.

- LANL representative shall have the option of inspecting anchors for finish, workmanship, and dimensional tolerances before any shipment is made.

- Materials that are not properly marked, have poor workmanship, are corroded, have defective threads, or are improperly documented shall be rejected.

PART 3    EXECUTION

# 3.1	INSTALLERS

- Implement and document a training and/or qualification program for installers. Installers must be made fully familiar with the manufacturer’s installation procedures, additions from the associated ESRs, and additional requirements as noted in this Section (follow most stringent).

# 3.2	EXAMINATION/SITE VERIFICATION OF CONDITIONS

*************************************************************************************************************

NOTE:  Since the design and performance of PI anchorage is dependent upon the (1) concrete type (i.e., normal- vs. light-weight), (2) compressive strength (i.e., f’c) and (3) thickness, these properties / data are included in the Special Inspections section of the ESRs for these products, as well as Table 3.1 herein.  Given this, and the fact the installer and inspector might not know these properties (particularly for projects on / in existing structures), the EOR must indicate them on the construction drawings for every location in which an anchor is to be installed.  In the event that none of these properties change from one anchorage location to another, the EOR need only indicate the ‘concrete properties associated with PI anchors’ once on the drawings. Document the source/bases for these data in the anchorage calculation.

*************************************************************************************************************

  - The use of anchors shall be restricted to the applications and installations defined in the design drawings. Construction aids are exempt from this requirement.

  - Anchors may only be installed in 14-day or older concrete that has attained its minimum specified design strength.

  - Anchors may only be installed in sound concrete.  Surfaces showing obvious distress by way of porosity, disintegration, carbonation and cracks over 0.02 inches in width and 12 inches or longer and within the distance of the embedment depth shall be reported to the Engineer of Record (EOR) for evaluation.

  - Anchors must not be drilled into the bottom of precast and post-tensioned T-beam stems.  Drilling into the sides of the T-beam stems shall be specifically pre-approved by the EOR.  Strand-cutting/nicking is prohibited.

# 3.3	PREPARATION

- Use of a rebar locator or drilling pilot holes is recommended to establish the rebar pattern before drilling in congested areas. Pilot holes shall be drilled with a carbide-tip bit to avoid rebar damage.

- In rad and cleanroom areas, use of Hilti dust removal system (vacuum attachment) HIT-DRS (Item No. 362323) during hole air blow-out is normally required.  Consider purchase along with anchors if DRS is not on hand.

- For safety, consider drill bits/drills that automatically shut off when the bit hits metal, particularly in older construction for which electrical configuration is not well-documented.

- Rebar cutting is only permitted with pre-approval by the EOR. Multi-cutting of the same bar is considered as one cut.  Rebar approved to be cut must be shown on as-built drawings at completion of Project.

- Rebar will be considered to be cut if:

  - For #4 through #7 – Cuts, nicks, or drill into bar body is greater than 1/16”

  - For #8 and larger – Cuts, nicks, or drill into bar body is greater than 1/8”

***********************************************************************************************************
NOTE: Cutting of bar deformations is not considered a cut since the area of steel is not reduced.	
***********************************************************************************************************

- When installing anchors through cut rebar, the anchoring mechanism shall be located at least two anchor diameters clear beyond the cut rebar.

# 3.4	INSTALLATION

***********************************************************************************************************
NOTE:  The only PI anchor permitted for use at LANL when “High Confidence” is required is the Drillco Maxi-Bolt (ref. 03 1512).  Maxi-Bolts are permitted to be used in Normal Confidence applications; however, use of these anchors requires adherence to additional (and, in some cases, different) installation requirements than those stipulated below.  Some examples include the thickness of concrete, and hole depths, vs. embedment depth; and several setting requirements. Thus, in order to use Maxi-Bolts in Normal Confidence applications, the following requirements must be edited as necessary/appropriate (i.e., depending on the applicable ML and PC) using 03 1512.

NOTE:  Just as for installation, the inspection requirements for Maxi-Bolts also differ from what is contained in this Section; therefore, para. 3.6 must also be edited using 03 1512 when these anchors are used in Normal Confidence applications.

***********************************************************************************************************

- Each anchor must be installed in the location, at the spacing, and with the embedment depth and edge distance(s) indicated on the project drawings, and in accordance with, in priority order, 1) this Section, 2) the ESR, 3) the manufacturer’s installation instructions.

- Obtain and comply with LANL Form 2074, Penetration Permit.

- Drill holes and install anchors in accordance with the ESR.

- Clean drilled holes of chips, dust, loose material, and water prior to anchor installation. The hole diameters and depths shall be as those required by the ESR. Verify depth of the concrete member before drilling holes. The embedment depth of the anchor must be in accordance with the ESR and the project drawings.  Contact the EOR if these requirements conflict.

- Anchors must be installed perpendicular to the concrete surface within a ( 5 degree tolerance. Post-installation verification of this criterion may be satisfied by visual inspection to verify proper seating of the nut and washer. When an anchor is replaced with an anchor of diameter one size larger, maintain the spacing requirements of the original size anchor.

- In areas where concrete has been removed, the minimum anchor embedment must be measured from the surface of sound concrete.

- Unless otherwise noted on project drawings, use the spacing requirements per the ESR.  For an anchor located adjacent to a PC-3 or PC-4 anchor or embedded item, use a spacing equal to the sum of 1.5 times the embedment depth of one anchor plus 1.5 times the embedment depth of the other anchor, unless otherwise approved by the EOR.

- Bending and welding of post-installed anchors, except grouted anchors, are not permitted.

- The nut thread engagement for the anchors (studs) shall be such that the bolt threads are flush with or project beyond the outside face of the nut when completely installed.

- Nuts and washers for anchors that are lost or damaged during installation shall be replaced with manufacturer’s specified component or equivalent as pre-approved by the EOR.

- Flat washers supplied with anchors shall be used in all cases except where details of the design drawings specify the use of another washer under the nuts. A washer may be trimmed to clear interferences. The trimmed edge shall not be closer than 7/8 of the bolt diameter from the center of the washer (ref. ASTM F436).

- Do not damage the length identification code on the head of the anchor. Anchor projection may be cut off subject to pre-approval by the EOR and documentation of the location, embedment, and length code on a LANL inspection report by a LANL Construction Inspector prior to cutting.

- Unused adhesive anchors shall be cutoff flush with the surface of the concrete. Unused mechanical anchors shall be driven in and cut-off flush. Cut-off anchors shall be considered an abandoned unrepaired hole for future anchor spacing requirements.

- The center-to-center distance between a new hole and an exploratory or unused hole or an abandoned cut-off anchor shall not be less than three times the diameter of the larger hole or 1” of clear concrete between the holes, whichever is greater, unless approved by the EOR. When exploratory or unused holes are repaired (ref. para. 3.8.A) and the repair material has attained the strength of the surrounding concrete, the center-to-center distance shall not be less than 1.5 times the diameter of the larger hole or 1” of clear concrete between holes, whichever is greater, unless approved by the EOR.

- Anchors may be installed in the upper and lower flutes of metal decking, as indicated on project drawings. Edge distance(s), embedment depth, spacing, etc. must be in accordance with the ESR.  Contact the EOR if any of these requirements conflict with project drawings.  If an installation requires the use of an attachment plate that spans deck ribs then the space between the decking and attachment plate must not be filled with grout or concrete or any other material except that spray-applied fire-resistive materials are permitted.

- Exercise care to avoid bending anchors to match baseplate holes, or loosening of anchors by prying sideways after tightening. Also ensure that the cone nut of an undercut anchor does not become loose from the stud during the setting or tensioning operation.

- Anchors that must be tensioned (via torque or direct tension) in order to be properly set /installed must not be used with leveling nuts placed under mounting plates (in order to preclude interference with pretensioning of the anchor).

- Relocating holes within baseplate:  The baseplate with bolts may be relocated no more than 1” in any direction with respect to the attachment principal axis, unless otherwise noted on the engineering drawings.

- Installation-related devices (e.g., torque wrenches, hammer drills, manufacturer’s setting tools, etc.) must be calibrated and controlled in accordance with LANL standards P 330-2, Control and Calibration of Measuring and Test Equipment (M&TE)] or equivalent.

# [3.5	INSTALLATION OF GROUTED ANCHORS

- Holes shall be drilled as shown on the engineering drawings.

  - For anchors up to 1 inch in diameter, provide 2-inch diameter hole in concrete.

  - For anchors greater than 2 inches in diameter, provide a hole at least 2 inches greater than the anchor diameter.

- Clean all surfaces of anchor to be bonded to grout from oil, grease, or other foreign material.

- The hole surfaces shall be wire brushed to clean them and to remove all loose particles. In addition, for core-drilled holes with diamond-tip bits, the holes shall be visually examined to confirm that there is no smooth glazing on the hole surface, and the sides of the hole may be roughened, as required, to ensure proper bond. Remove all debris, dust, cement, and other foreign materials from the hole.

- Soak the hole to saturation with potable water, and keep damp for a minimum of six hours prior to grouting.  Immediately prior to grouting, remove all free surface water using oil-free compressed air, sponge, or vacuum.

- Anchors shall be properly positioned in the hole prior to grouting, and supported to maintain that position during grouting.

- Mix the grout specified in Section 03 6000, Grout, in accordance with that section and place it in accordance with same.

- Cold bending of grouted anchors is permitted to enable the anchor to clear reinforcing steel, provided that the axis of bent anchor is not more than 30 degrees from straight. Field bent anchors should be inspected by LANL construction inspection to verify radius of bend and lack of surface cracking.]

3.6	INSPECTION

***********************************************************************************************************
NOTE:  Drillco Maxi-Bolts are permitted to be used in normal confidence applications; however, use of these anchors requires adherence to additional (and, in some cases, different) inspection requirements than those stipulated below.  Some examples include verifying the length of the undercutting tool and the undercut size. Thus, in order to use Maxi-Bolts in normal confidence applications, the following requirements must be edited as necessary / appropriate (i.e., depending on the applicable ML and PC) using 03 1512.

NOTE:  For ML-3 anchors, it is recommended that testing be mandated herein to provide added assurance as opposed to increased rigor on procurement.  Refer to the testing requirements contained in 03 1512 for examples of possible changes that can be made to increase confidence, or it may be used as the starting point when the utmost confidence is desired.

***********************************************************************************************************

A.	INSPECTION

1. 	Visually inspect anchors in order to verify and document that they have been installed in accordance with Articles 3.4 and 3.5 as applicable.  Attributes requiring inspection are those shown in Table 3.1 plus any additional attributes imposed by this Section and the EOR. These attributes must be identified in the inspection report documentation.

2.	If visual inspection reveals that the installed anchor does not meet the requirements of this Section, the anchor shall be relocated as permitted by this Section, or shall be removed and replaced by another anchor, or referred to the EOR for evaluation.

Table 3.1 Required Inspection Attributes

For attribute definitions / details above and beyond footnote contents, refer to ESR, manufacturer’s installation instructions, and, where indicated in parenthesis, previous portions of this Section.

| Inspection Attribute | Wedge and Screw | Heavy Duty Sleeve | Adhesive | Undercut |
| --- | --- | --- | --- | --- |
| 1 | Anchor / Anchor system1 type / description | ( | ( | ( | ( |
| 2 | Anchor / Anchor element dimensions | ( | ( | ( | ( |
| 3 | Concrete type (normal- vs. light-weight)2 | ( | ( | ( | ( |
| 4 | Concrete compressive strength2 | ( | ( | ( | ( |
| 5 | Concrete thickness2 | ( | ( | ( | ( |
| 6 | Anchor spacing(s) | ( | ( | ( | ( |
| 7 | Edge distance(s) | ( | ( | ( | ( |
| 8 | Adhesive expiration date |  |  | ( |  |
| 9 | Drill and/or drill bit type, size, power, etc.3 | ( | ( | ( | ( |
| 10 | Drilled hole cleaning (3.4.C) | ( | ( | ( | ( |
| 11 | Drilled hole dimensions | ( | ( | ( | ( |
| 12 | Steel deck hole dia. < concrete hole dia. + 1/8”4 | ( |  |  |  |
| 13 | Adherence to manufacturer’s installation instructions | ( | ( | ( | ( |
| 14 | Anchor embedment | ( | ( | ( | ( |
| 15 | Minimum installation torque | ( | ( |  |  |
| 16 | Maximum installation torque |  |  | ( | ( |
| 17 | Anchor perpendicular to concrete (3.4.D) | ( | ( | ( | ( |
| 18 | Nut thread engagement (3.4.H) | ( | ( | ( | ( |

1Applies to both anchor element (i.e., steel threaded rod, reinforcing bar / rebar dowel, or insert) AND adhesive material.

2Refer to project drawings if not obvious or somehow otherwise known with certainty.

3Refer to ESR for requirements associated with hole (for anchor / rod / rebar / insert) drilling / coring.

4Applies to installation in the soffit of concrete-on-steel-deck assemblies.

NOTE:  Attributes 1-9 are visually inspected prior to the start of the anchor installation process, 10-16 are verified during the process, and 17-18 are verified after the process is complete.

# 3.7 	DOCUMENTATION

## Installation Inspection Record

The Installation Inspection Record shall contain the information listed in Table 3.1.

***********************************************************************************************************

NOTE:  The default repair / restoration material is the drypack mortar from Para. 2.1.  If stronger material is required (e.g., to ensure that the strength of the repair is at least equal to that of the surrounding concrete, etc.) then grout should be used instead.  If grout is used then include 03 6000 Grout in the Project Spec, and edit the text below as necessary.

*************************************************************************************************************

# 3.8	REPAIR/RESTORATION

A.	Repair abandoned holes with material specified in Para 2.1.  Anchors installed near an abandoned repaired or unrepaired hole must be located as specified in Para 3.4.M.  The repair material shall have strength greater than or equal to that of the surrounding concrete.

When anchors are not installed properly, the following repairs may be undertaken:

- Remove the defective anchor, redrill hole and install the same diameter anchor if the integrity of surrounding concrete has not been disturbed.

- For cases where excessive slippage upon torquing is experienced, or usage of the same hole is not possible, fill the existing hole with approved material as specified in Para 2.1 and relocate the anchor location as specified in Para 3.4.M.

  - If breakout of concrete around the anchor occurs during installation, the EOR must develop an appropriate repair. The EOR must be contacted to evaluate the damage and repair method. Local spalling of the concrete around the anchor, up to a maximum depth of 1/4 inch, is not considered a concrete breakout failure.

  - Mislocated anchors may be cut flush with concrete surface, and need not be removed if they do not interfere with subsequent installations.

  - Mislocated anchors or anchors installed for temporary applications may be left in place.  Those anchors that must be removed to accommodate other attachments, aesthetics or safety of personnel, may be removed completely, or abandoned in place by cutting off beneath the surface after chipping the concrete 1” minimum, and patching with approved material (Para. 2.1).  Mislocated anchors that will be covered by a baseplate or an attachment may be cut off flush with the concrete. In the event that an anchor must be removed from the hole and a new anchor installed, the removal and installation of the new anchor shall be in accordance with the manufacturer’s specifications.  The wedges of anchors that are “lost” during anchor removal may be abandoned in place.  The abandoned hole or removed concrete shall be filled with approved material.

  - Removal of installed anchors for inspection or replacement may be performed using Bolt Extractor manufactured by Drillco Devices Ltd. or an equivalent.

END OF SECTION

***********************************************************

Do not delete the following reference information:

***********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 03 1534 Rev. 4 dated April 23, 2012.