SECTION 03 4100

PRECAST STRUCTURAL CONCRETE

*************************************************************************************************************This template must be edited for each project.  In doing so, the specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and the specifier’s notes such as these. To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Structural Specs POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Specification developed for pre-fabricated reinforced structural concrete for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Prime Subcontractor (and Sub-Tier) must ensure that this specification is followed and that required documentation is available before fabrication begins.

# *********************************************************************************************************

********************************************************************************************************

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

************************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Precast structural concrete.

Precast structural concrete with commercial architectural finish.

Related Sections:

************************************************************************************************************

Retain Sections in subparagraphs below that contain requirements Subcontractor might expect to find in this Section but are specified in other Sections.
************************************************************************************************************

01 4000 Quality Requirements

01 4200 References

01 4444 Offsite Welding and Joining Requirements

01 4455 Onsite Welding and Joining Requirements

[03 0521 Post Installed Concrete Anchors – High Confidence] [03 0520 Post Installed Concrete and Grouted-Masonry Anchors – Normal Confidence]

Section 03 3001 Reinforced Concrete for [concrete topping and] placing connection anchors in concrete.

Section 05 1000 Structural Metal Framing for furnishing and installing connections attached to structural-steel framing.

Section 05 5000 Metal Fabrications for kickers and other miscellaneous steel shapes.

Section 07 6200 Sheet Metal Flashing and Trim for flashing receivers and reglets.

Section 07 8400 Firestopping for joint-filler materials for fire-resistance-rated construction.

Section 07 9200 Joint Sealants for elastomeric joint sealants and sealant backings.

DEFINITIONS

Refer to Section 01 4200, References.

*************************************************************************************************************

Retain this article if a design reference sample has been preapproved by EOR for precast structural concrete units with architectural finish.

*************************************************************************************************************

Design Reference Sample:  Sample of approved precast structural concrete color, finish, and texture, preapproved by EOR.

Engineer of Record (EOR): Indicates the Professional Engineer responsible for the overall design of the facility or project.

PERFORMANCE REQUIREMENTS

*************************************************************************************************************

Retain this article if Subcontractor is required to assume responsibility for design.

*************************************************************************************************************

Delegated Design:  Design precast structural concrete, including comprehensive engineering analysis by a qualified Professional Engineer, using performance requirements and design criteria indicated.

Structural Performance:  Precast structural concrete units and connections shall withstand design loads indicated within limits and under conditions indicated.

*************************************************************************************************************

Retain "Fire-Resistance Calculations" Paragraph below if required for units or assemblies. If paragraph is retained then retain related Action Submittal 1.4.K. Fire Resistance Calculations.

*******************************************************************************************************************************************************************************************************************************************************************************************************************

Fire-Resistance Calculations:  Where indicated, provide precast structural concrete units whose fire resistance has been calculated according to PCI MNL 124, "Design for Fire Resistance of Precast Prestressed Concrete," and is acceptable to LANL Fire Protection.

*************************************************************************************************************

Retain paragraph above if design loads are shown on Drawings. Retain paragraph below if including design loads here.  See the LANL Engineering Standards Manual Ch. 5 Structural for required loads.  Revise requirements below to suit Project, and add other performance and design criteria if applicable.

*************************************************************************************************************

Structural Performance:  Provide precast structural concrete units and connections capable of withstanding the following design loads within limits and under conditions indicated:

*************************************************************************************************************

### For members that are to receive concrete topping, state whether all superimposed dead and live

### loads on precast, prestressed members do or do not include the weight of the concrete topping.  It is best to list the live load, superimposed dead load, topping weight, and weight of the member, all as separate loads.  Where there are two different live loads (e.g., roof level of a parking structure) indicate how they are to be combined.  Show hanging utility support loads in addition to loads indicated on drawings.

### *************************************************************************************************************

Dead Loads:  <Insert loads>.

Concrete Topping Load:  <Insert load>.

Live Loads:  <Insert loads>.

Roof Loads:  <Insert loads>.

Snow Loads:  <Insert loads>.

Seismic Loads:  <Insert seismic design data including importance factor, use group, seismic design category, and drift criteria>.

Wind Loads:  <Insert wind loads or wind-loading criteria, positive and negative for various parts of the building as required by applicable building code or ASCE 7, including basic wind speed, importance factor, exposure category, and pressure coefficient>.

<Insert loads or load combinations>.

*****************************************************************************************************************************************************************************************************************************

### Show locations here or on Drawings if different movements are anticipated for different building elements.  Specify deflection limits stricter than ACI 318.

### *****************************************************************************************************************************************************

Design precast structural concrete framing system and connections to maintain clearances at openings, to allow for fabrication and construction tolerances, to accommodate live-load deflection, shrinkage and creep of primary building structure, and other building movements.  Maintain precast structural concrete deflections within limits of ACI 318.

*************************************************************************************************************

### Changes indicated below are based on temperature data from National Climatic Data Center, www.ncdc.noaa.gov, for Los Alamos: -18°F (Jan. ’63) and 102°F (Aug. ’44) are the min and max temperature extremes.

### *************************************************************************************************************

Thermal Movements:  Allow for in-plane thermal movements resulting from annual ambient temperature changes of [minus 18 to plus 102 deg F].

*************************************************************************************************************

### Retain first subparagraph below if fire-resistance rating is required.  Fire ratings depend on occupancy and building construction type, and are generally a building code requirement. When required, fire-rated products should be clearly identified on the Drawings. In the paragraph below “thickness” is with respect to concrete cover, for example, for cast-in place steel cables, reinforcing bars, structural elements, etc.

### *************************************************************************************************************

Fire-Resistance Rating:  Select material and minimum thicknesses to provide indicated fire rating.

*************************************************************************************************************

### Retain subparagraph below if precast units are used in parking structures to resist impact load.  Revise loads to suit Project.

### *************************************************************************************************************

Vehicular Impact Loads:  Design spandrel beams acting as vehicular barriers for passenger cars to resist a single [6000-lbf] <Insert value> load applied horizontally in any direction to the spandrel beam, with anchorages or attachments capable of transferring this load to the structure.  Design spandrel beams assuming the load to act at a height of 18 or 27 inches above the floor or ramp surface, whichever is more severe, on an area not to exceed 1 sq. ft.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.

Design Mixtures:  For each precast concrete mixture. Include compressive strength and water-absorption tests.

Shop Drawings:  Include member locations, plans, elevations, dimensions, shapes and sections, openings, support conditions, and size, location, and types of reinforcement, including special reinforcement.  Detail fabrication and installation of precast structural concrete units.

*************************************************************************************************************

### Delete subparagraphs below not applicable to Project.

### *************************************************************************************************************

Indicate joints, reveals, and extent and location of each surface finish.

Indicate separate face and backup mixture locations and thicknesses.

Indicate welded connections by AWS standard symbols.  Show size, length, and type of each weld.

Detail loose and cast-in hardware, lifting and erection inserts, connections, and joints.

Indicate locations, tolerances, and details of anchorage devices to be embedded in or attached to structure or other construction.

Indicate tendon profile, supports and locations, and clearances required for jack.

Indicate magnitude and location of prestressing forces.

Include and locate openings larger than by 10 inches.

Indicate location of each precast structural concrete unit by same identification mark placed on panel.

Indicate relationship of precast structural concrete units to adjacent materials.

Indicate estimated camber for precast floor slabs with concrete toppings.

Indicate shim sizes and grouting sequence.

<Insert additional drawing detail>

[For prestressed precast structural concrete provide required minimum compressive strength for stated stages of construction. Include magnitude and location of prestressing forces and [stressing sequence for post tensioning tendons].

Design Calculations: [Submit with Shop Drawings] [Need not be submitted] as determined by the LANL Building Official.

Design Modifications:  If design modifications are proposed to meet performance requirements and field conditions, submit design calculations and Shop Drawings.  Do not adversely affect the appearance, durability, or strength of units when modifying details or materials and maintain the general design concept.

Samples: [Not Required] [Required]

*************************************************************************************************************

### Retain first subparagraph below if architectural finishes, colors, and textures are preselected, specified, or scheduled.  Coordinate with sample panels in "Quality Assurance" Article.

### *************************************************************************************************************

For each type of finish indicated on exposed surfaces of precast structural concrete units with architectural finish, in sets of 3, illustrating full range of finish, color, and texture variations expected; approximately 12 by 12 by 2 inches.

Where other faces of precast concrete unit are exposed, include Samples illustrating workmanship, color, and texture of backup concrete as well as facing concrete.

Provide handling procedures, erection sequences, and for special conditions provide temporary bracing and shoring plan.

*************************************************************************************************************

### Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Subcontractor.

### *************************************************************************************************************

Delegated Design Submittal:  For precast structural concrete indicated to comply with the performance requirements and design criteria, the comprehensive engineering design including analysis data, signed and sealed by the qualified Professional Engineer responsible for their preparation.

[Fire Resistance Calculations]

SUSTAINABLE DESIGN SUBMITTALS

LEED Submittals:

Product Data:  For products having recycled content, documentation indicating percentages by weight of postconsumer and pre-consumer recycled content.  Include statement indicating cost for each product having recycled content.

************************************************************************************************************

### Retain "Design Mixtures for Credit ID 1" Subparagraph below if fly ash, ground granulated blast-furnace slag, silica fume, or other materials are used as Portland cement replacements for LEED-NC, LEED-CS, or LEED for Schools Credit ID 1.  To achieve this credit, replacement materials must be substituted for at least 40 percent of the Portland cement that would otherwise be used.

### *************************************************************************************************************

Design Mixtures for Credit ID 1:  For each concrete mixture containing fly ash as a replacement for Portland cement or other Portland cement replacements and for equivalent concrete mixtures that do not contain Portland cement replacements.

Product Data: For adhesives and sealants, including printed statement of VOC content.

INFORMATIONAL SUBMITTALS

************************************************************************************************************

### Coordinate first paragraph below with qualification requirements in Section 01 4000 Quality Requirements and as supplemented in "Quality Assurance" Article.

### *************************************************************************************************************

Qualification Data:  For [Installer] [fabricator] [testing agency].

************************************************************************************************************

### Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

### *************************************************************************************************************

Welding Procedure Specifications (WPS) and Welder Certifications: In accordance with 01 4444 “Offsite Welding and Joining Requirements” and 01 4455 “Onsite Welding and Joining Requirements”.

*************************************************************************************************************

### Retain first paragraph below for material certificates from manufacturers.

### *************************************************************************************************************

Manufacturer’s Material Certificates:  For the following, from manufacturer:

*************************************************************************************************************

### Revise list below to suit Project.

### *************************************************************************************************************

Cementitious materials.

Reinforcing materials and prestressing tendons.

Admixtures.

Bearing pads.

Structural-steel shapes and hollow structural sections.

<insert additional >

*************************************************************************************************************

### Retain first paragraph below for material test reports that are Subcontractor's responsibility.

### Note that PCI MNL 116 requires aggregates conform to several standards and outlines which tests should be included in material test reports.

### *************************************************************************************************************

Material Test Reports: Certified suppliers test reports for aggregates.

***********************************************************************************************************************************************************************************

### Retain paragraph below if Subcontractor is responsible for source quality-control testing and inspecting.

### *****************************************************************************************************************************************************

Source quality-control reports.

*************************************************************************************************************

### Retain paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.

### *************************************************************************************************************

Field quality-control reports.

*************************************************************************************************************

Retain paragraph below if project includes prestressed concrete.

*************************************************************************************************************

[Jack Calibration Records (in accordance with PCI-MNL-116 5.2.7).]

Close-Out Submittals

Maintenance Data: For Precast Structural Concrete [with Commercial Architectural Finish].

[Project Records: Including jacking and tensioning records.]

Warranties:

Submit copy of the Precast Structural Concrete manufacturer’s warranty covering materials.

Submit copy of the Precast Structural Concrete warranty covering workmanship.

QUALITY ASSURANCE

Fabricator Qualifications: A firm that assumes responsibility for engineering precast structural concrete units to comply with performance requirements.  Responsibility includes preparation of Shop Drawings and comprehensive engineering analysis by a qualified professional engineer.

*************************************************************************************************************

### Usually retain first subparagraph below and select category to qualify a fabricator.  A precast concrete plant certified to produce products in Category C2A, for example, is also certified to produce products in Categories C1, C1A, and C2 but not in Category C3, C3A, C4, or C4A.  See PCI’s website, www.pci.org, for discussion of PCI's Groups C and CA categories.

### *************************************************************************************************************

Participates in PCI's Plant Certification program [at time of bidding] and is designated a PCI-certified plant as follows:

*************************************************************************************************************

### Retain first subparagraph and appropriate option if Group C products without architectural finishes are required.  Retain second subparagraph and appropriate option if Group CA products with architectural finishes are required.

### *************************************************************************************************************

### Group C, [Category C1 - Precast Concrete Products (no prestressed reinforcement)] [Category C2 - Prestressed Hollowcore and Repetitively Produced Products] [Category C3 - Prestressed Straight Strand Structural Members] [Category C4 - Prestressed Deflected Strand Structural Members].

Group CA, [Category C1A - Precast Concrete Products (no prestressed reinforcement)] [Category C2A - Prestressed Hollowcore and Repetitively Produced Products] [Category C3A-Prestressed Straight-Strand Structural Members] [Category C4A-Prestressed Deflected-Strand Structural Members].

*************************************************************************************************************

### At the time of publication of 03 4100 Rev. 0 there are no PCI Certified erectors in or near NM. Therefore, installation must be performed by an installer that is qualified per the following paragraph.

### ************************************************************************************************************

Installer Qualifications:  An experienced precast concrete erector who, before erection of precast concrete, has retained a "PCI-Certified Field Auditor" to conduct a field audit of a project installed by erector in [Category S1 - Simple Structural Systems] [Category S2 - Complex Structural Systems] and who produces an Erectors' Post Audit Declaration, according to PCI MNL 127, "PCI Erector's Manual - Standards and Guidelines for the Erection of Precast Concrete Products."

**********************************************************************************************************

### Retain first paragraph below if Subcontractor selects testing agency for testing in addition to that required under PCI's certification program.

### If first paragraph below is retained, ensure the related portion of Section 01 4000, Quality Assurance (i.e., paragraph 1.5.A) is edited accordingly.

### Testing agency is normally engaged by LANL.

### *************************************************************************************************************

Testing Agency Qualifications:  Qualified according to ASTM C 1077 and ASTM E 329 for testing indicated. Testing Agency must be pre-approved by the LANL. This includes any use of testing agencies by sub-tier suppliers, fabricators, etc.

Design Standards:  Comply with ACI 318 and design recommendations in PCI MNL 120, "PCI Design Handbook - Precast and Prestressed Concrete,"[and PTI TAB.1-06, “Post-Tensioning Manual”], applicable to types of precast structural concrete units indicated.

Quality-Control Standard:  For manufacturing procedures and testing requirements, quality-control recommendations, and dimensional tolerances for types of units required, comply with PCI MNL 116, "Manual for Quality Control for Plants and Production of Structural Precast Concrete Products."

*************************************************************************************************************

### Retain "Welding Qualifications" Paragraph below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

### *************************************************************************************************************

Welding Qualifications:  Refer to following specification sections:

01 4444 “Offsite Welding and Joining Requirements”

01 4455 “Onsite Welding and Joining Requirements”

*************************************************************************************************************

### Consider retaining first paragraph below for precast structural concrete units with architectural finish. PCI recommends review of preproduction sample panels to establish range of finish, color, and texture to be expected.  Revise number and size of sample panels in paragraph to suit Project.

### *************************************************************************************************************

Sample Panels:  After sample approval and before fabricating precast structural concrete units with [architectural finish], produce a minimum of [2] <Insert number> sample panels approximately [16 sq. ft.] <Insert size> in area for review by EOR.  Incorporate full-scale details of architectural features, finishes, textures, and transitions in sample panels.

Locate panels where indicated or, if not indicated, as directed by EOR.

Damage part of an exposed-face surface for each finish, color, and texture, and demonstrate adequacy of repair techniques proposed for repair of surface blemishes.

After approval of repair technique, maintain one sample panel at fabricator's plant and one at Project site in an undisturbed condition as a standard for judging the completed Work.

Demolish and remove sample panels when directed.

*************************************************************************************************************

### Consider retaining first paragraph below for precast structural concrete units with architectural finish.  Delete if sample panels in paragraph above will suffice and added expense of mockups is not required.

### *************************************************************************************************************

Mockups:  After sample panel approval but before production of precast structural concrete units [with architectural finish], construct full-sized mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

*************************************************************************************************************

### Revise or delete three subparagraphs below to suit Project.

### *************************************************************************************************************

Build mockup as indicated on Drawings including [sealants] <Insert construction> and precast structural concrete units with an architectural finish complete with anchors, connections, flashings, and joint fillers.

*************************************************************************************************************

### Retain first subparagraph below if mockups are not only for establishing appearance factors.

### *************************************************************************************************************

Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless EOR specifically approves such deviations in writing.

*************************************************************************************************************

### Retain subparagraph below if mockups are installed as part of building rather than erected separately.

### *************************************************************************************************************

Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Welding:  Welding of reinforcing bars will be permitted only with the approval of the LANL-Welding POC. Utilize a procedure that is approved by the EOR and the LANL-Welding POC prior to start of work.

*************************************************************************************************************

### Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

### *************************************************************************************************************

Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

DELIVERY, STORAGE, AND HANDLING

Support units during shipment on non-staining shock-absorbing material in same position as during storage.

Store units with adequate bracing and protect units to prevent contact with soil, to prevent staining, and to prevent cracking, distortion, warping or other physical damage.

Store units with dunnage across full width of each bearing point unless otherwise indicated.

Place adequate dunnage of even thickness between each unit.

Place stored units so identification marks are clearly visible, and units can be inspected.

Handle and transport units in a position consistent with their shape and design in order to avoid excessive stresses that would cause cracking or damage.

Lift and support units only at designated points shown on Shop Drawings.

COORDINATION

Furnish loose connection hardware and anchorage items to be embedded in or attached to other construction before starting that Work.  Provide locations, setting diagrams, templates, instructions, and directions, as required, for installation.

PRODUCTS AND MATERIALS

MANUFACTURERS

*************************************************************************************************************

### Retain this article and one of two options below if naming fabricators.  See PCI's magazine "Ascent" or its Web site, www.pci.org, for current PCI-certified plant listings.

### *************************************************************************************************************

Fabricators:  Subject to compliance with requirements, [provide products by one of the following] [available fabricators offering products that may be incorporated into the Work include, but are not limited to, the following]:

Coreslab Structures, 2800 2nd St.  Sch. P.O. Box 1609, Albuquerque, NM 87103 (505)-247-3725

Ferreri Concrete Structures Inc., 6151 Chappell Rd., Albuquerque, NM 87113, (505)-344-8823

Castillo Prestress, 6 Lopez Loop, Belen, NM 87002, (505)-864-0238

<Insert Fabricator>

MOLD MATERIALS

Molds:  Rigid, dimensionally stable, non-absorptive material, warp and buckle free, that will provide continuous and true precast concrete surfaces within fabrication tolerances indicated; nonreactive with concrete and suitable for producing required finishes.

Mold-Release Agent:  Commercially produced liquid-release agent that will not bond with, stain or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

*************************************************************************************************************

### Retain first paragraph below if using form liners for precast structural concrete with architectural finish.  Form liners may be used to achieve a special off-the-form finish.  Revise to add description of selected form liner if required.

### *************************************************************************************************************

Form Liners:  Units of face design, texture, arrangement, and configuration [indicated] [to match those used for precast concrete design reference sample].  Furnish with manufacturer's recommended liquid-release agent that will not bond with, stain, or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

********************************************************************************************************

### Retain paragraph below if surface retarder is applied to molds to help obtain exposed-aggregate finish for precast structural concrete with architectural finish.

### **********************************************************************************************************

Surface Retarder:  Chemical set retarder, capable of temporarily delaying final hardening of newly placed concrete mixture to depth of reveal specified.

REINFORCING MATERIALS

All reinforcing steel must be traceable to manufacturer approved Certified Material Test Reports (CMTR’s).

### *********************************************************************************************************
Retain one or more paragraphs in this article to suit steel reinforcement requirements.  Distinguish locations of each type of reinforcement here or on Drawings.  If retaining "Performance Requirements" Article, consider reviewing selections with fabricators.

### Retain "Recycled Content of Steel Products" Paragraph below if recycled content is required for LEED Credit MR 4.  USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation.

### ********************************************************************************************************

Recycled Content of Steel Products:  Postconsumer recycled content plus one-half of preconsumer recycled content not less than [25] [60] <Insert number> percent.

************************************************************************************************************

Verify reinforcing steel type and requirements prior to editing subparagraph D. ASTM A706 reinforcing steel is intended for applications where controlled tensile properties, or chemical composition restrictions to enhance weldability, or both, are required.

This distinction is highlighted by the fact that IBC and ACI 318 have additional requirements pertaining to ASTM A615 reinforcing steel used to resist seismic forces and/or to be welded, but ASTM A706 does not have these restrictions.

- For the seismic requirements, reference IBC 1708.2 and ACI 318, 21.1.5

- For the welding requirements, reference IBC 1708.2 and ACI 318, 3.5.2

It is mandatory to use ASTM A706 low-allow steel reinforcing bars if welding is permitted. Welding is only permitted with the permission of LANL. Retain first paragraph below for reinforcement that is welded or if added ductility is sought.

*************************************************************************************************************

Reinforcing Bars:  [ASTM A 615, Grade 60] [ASTM A706], deformed.

### *************************************************************************************************************************************

### Retain galvanized reinforcing bars in first paragraph below where corrosive environment or severe exposure conditions justify extra cost.  Presence of chromate film on the surface of galvanized coating is usually visible as light yellow tint on the surface.  ASTM B 201 describes a test method for determining presence of chromate coatings.

### *************************************************************************************************************

Galvanized Reinforcing Bars:  [ASTM A 615, Grade 60] [ASTM A 706], deformed bars, ASTM A 767, Class II zinc coated, hot-dip galvanized [, and chromate wash treated after fabrication and bending].

### *************************************************************************************************************

### Consider using epoxy coating where corrosive environment or severe exposure conditions justify extra cost.  In first paragraph below, retain ASTM A 775/A 775M for a bendable epoxy coating; retain ASTM A 934/A 934M for a nonbendable epoxy coating.

### *************************************************************************************************************

Epoxy-Coated Reinforcing Bars:  [ASTM A 615, Grade 60] [ASTM A 706], deformed bars, [ASTM A 775] [or] [ASTM A 934] epoxy coated, with less than 2 percent damaged coating in each 12-inch bar length.

1.  	Epoxy-Coated reinforcing steel must come from a CRSI certified plant or the Engineer of Record must approve the facility.

Steel Bar Mats:  ASTM A 184, fabricated from [ASTM A 615/A 615M, Grade 60] [ASTM A 706/A 706M], deformed bars, assembled with clips.

Plain-Steel Welded Wire Reinforcement:  ASTM A 185, fabricated from [as-drawn steel] [galvanized-steel] wire into flat sheets.

Deformed-Steel Welded Wire Reinforcement:  ASTM A 497/A 497M, flat sheet.

Epoxy-Coated-Steel Wire:  ASTM A 884/A 884M, Class A coated, [plain] [deformed], flat sheet, [Type 1 bendable] [Type 2 non-bendable] coating.

Supports:  Suspend reinforcement from back of mold or use bolsters, chairs, spacers, and other devices for spacing, supporting, and fastening reinforcing bars and welded wire reinforcement in place according to PCI MNL 116.

PRESTRESSING TENDONS

### *************************************************************************************************************

### Retain this article if precast concrete units will be prestressed, either pretensioned or post-tensioned.

### Retain materials in this article as required; revise to suit Project.

### Note that PCI MNL 120 states that there is limited use of two and three wire strands conforming to ASTM A910.

### *************************************************************************************************************

Prestressing Strand:  [ASTM A 416, Grade 250 or Grade 270, uncoated, 7-wire] [or] [ASTM A 882, Grade 270, 7-wire], [ASTM A 910, Grade 270, uncoated, weld-less, 2-and 3-wire], low-relaxation strand.

### *************************************************************************************************************

### For aggressive environments (see ACI 423.7), revise subparagraph below by adding an anchorage device encapsulation system consisting of caps and sleeves.

### *************************************************************************************************************

Coat unbonded post-tensioning strand with post-tensioning coating complying with ACI 423.6 and sheath with polypropylene tendon sheathing complying with ACI 423.6.  Include anchorage devices and coupler assemblies.

Post-Tensioning Bars: ASTM A 722, uncoated high-strength steel bar.

CONCRETE MATERIALS

### *************************************************************************************************************

### Retain materials in this article as required; revise to suit Project.

### Type III cement is not an option at LANL as a result of Jul-12 input from NMDOT:

### Pro:  Quick / short-term strength & stiffness gains (i.e., over those associated w/ Type I-II).

### Con:  Less long-term strength & stiffness gains, & less durability (i.e., higher alkali content leads to greater potential for ASR; & higher temperature during curing leads to greater potential for shrinkage cracking, hence less freeze-thaw resistance).

### In short, Type III cement sacrifices long-term performance for early-age strength & stiffness gains.

### *************************************************************************************************************

Portland Cement:  ASTM C 150, Type I or Type II, gray, unless otherwise indicated.

### *************************************************************************************************************

### Retain subparagraph below if mixing white and gray cement will improve color uniformity of precast structural concrete with architectural finish.  White cement has greater color consistency than gray cement and can be used for pastel colors.  For darker colors, variations of gray cement have less effect on final color hue.

### *************************************************************************************************************

For surfaces exposed to view in finished structure, mix gray with white cement, of same type, brand, and mill source.

Supplementary Cementitious Materials:

### *************************************************************************************************************

### Retain mineral or cementitious admixtures in four subparagraphs below.  Because fly ash, gray silica fume, and ground slag affect color uniformity, they are not recommended by PCI where appearance is important.

### *************************************************************************************************************

Fly Ash:  ASTM C 618, Class C or F, with maximum loss on ignition of 3 percent.

Metakaolin Admixture:  ASTM C 618, Class N.

Silica Fume Admixture:  ASTM C 1240, with optional chemical and physical requirement.

Ground Granulated Blast-Furnace Slag:  ASTM C 989, Grade 100 or 120.

### *************************************************************************************************************

### ASTM C 33 limits deleterious substances in coarse aggregate depending on climate severity and in-service location of concrete.  Class 5S is the most restrictive designation for architectural concrete exposed to severe weathering.  PCI MNL 116 also establishes strict limits on deleterious substances for fine and coarse aggregates.

### *************************************************************************************************************

Normal-Weight Aggregates:  Except as modified by PCI MNL 116, ASTM C 33, with coarse aggregates complying with [Class 5S] [Class 5M] [Class 4S] [Class 4M].  Stockpile fine and coarse aggregates for each type of exposed finish from a single source (pit or quarry) for Project.

### *************************************************************************************************************

### Retain two subparagraphs below for face mixtures for precast structural concrete with architectural finish.  Revise to add descriptions of selected coarse- and fine-face aggregate colors and sources if required.

### *************************************************************************************************************

Face-Mixture-Coarse Aggregates:  Selected, hard, and durable; free of material that reacts with cement or causes staining; to match selected finish sample.

### *************************************************************************************************************

### Retain one option in first subparagraph below or insert gradation and maximum aggregate size if known.  Fine and coarse aggregates are not always from same source.

### *************************************************************************************************************

Gradation:  [Uniformly graded] [Gap graded] [To match design reference sample].

Face-Mixture-Fine Aggregates:  Selected, natural or manufactured sand of same material as coarse aggregate unless otherwise approved by EOR.

### *************************************************************************************************************

### Lightweight aggregates in a face mixture are not recommended by PCI in cold or humid climates (if exposed to the weather) unless their performance has been verified by tests or records of previous satisfactory usage in similar environments.  If normal-weight aggregates are used in face mixture, PCI does not recommend lightweight aggregates in backup mixture due to bowing potential.

### *************************************************************************************************************

Lightweight Aggregates:  Except as modified by PCI MNL 116, ASTM C 330, with absorption less than 11 percent.

### *************************************************************************************************************

### Retain first paragraph below if coloring admixture is required for precast structural concrete with architectural finish.  Add color selection if known.

### *************************************************************************************************************

Coloring Admixture:  ASTM C 979, synthetic or natural mineral-oxide pigments or colored water-reducing admixtures, temperature stable, and nonfading.

Water:  Potable; free from deleterious material that may affect color stability, setting, or strength of concrete and complying with chemical limits of PCI MNL 116.

Air-Entraining Admixture:  ASTM C 260, certified by manufacturer to be compatible with other required admixtures.

Chemical Admixtures:  Certified by manufacturer to be compatible with other admixtures and to not contain calcium chloride, or more than 0.15 percent chloride ions or other salts by weight of admixture.

*************************************************************************************************************

### Retain one or more chemical admixtures in seven subparagraphs below if chemical admixtures are permitted; limit chemical admixture types if required.  Water-reducing admixtures, Types A, D, and E, or a high-range water reducer, Type F, predominate.

### *************************************************************************************************************

Water-Reducing Admixtures:  ASTM C 494, Type A.

Retarding Admixture:  ASTM C 494, Type B.

Water-Reducing and Retarding Admixture:  ASTM C 494, Type D.

Water-Reducing and Accelerating Admixture:  ASTM C 494, Type E.

High-Range, Water-Reducing Admixture:  ASTM C 494, Type F.

High-Range, Water-Reducing and Retarding Admixture:  ASTM C 494, Type G.

Plasticizing and Retarding Admixture:  ASTM C 1017.

Corrosion-Inhibiting Admixture:  Commercially formulated, anodic inhibitor or mixed cathodic and anodic inhibitor; capable of forming a protective barrier and minimizing chloride reactions with steel reinforcement in concrete.

STEEL CONNECTION MATERIALS

*******************************************************************************

### Revise this article to suit Project.  Add other materials as required.

### *******************************************************************************

Carbon-Steel Shapes and Plates:  ASTM A 36.

Carbon-Steel-Headed Studs:  ASTM A 108, AISI 1018 through AISI 1020, cold finished, AWS D1.1, Type A or B, with arc shields and with minimum mechanical properties of PCI MNL 116.

Carbon-Steel Plate:  ASTM A 283.

Malleable-Iron Castings:  ASTM A 47.

Carbon-Steel Castings:  ASTM A 27, Grade 60-30.

High-Strength, Low-Alloy Structural Steel:  ASTM A 572.

Carbon-Steel Structural Tubing:  ASTM A 500, Grade B.

Wrought Carbon-Steel Bars:  ASTM A 675, Grade 65.

Deformed-Steel Wire or Bar Anchors:  ASTM A 496 or ASTM A 706.

*************************************************************************************************************

### ASTM A 307 defines the term "studs" to include stud stock and threaded rods.

### *************************************************************************************************************

Carbon-Steel Bolts and Studs:  ASTM A 307, Grade A; carbon-steel, hex-head bolts and studs; carbon-steel nuts, ASTM A 563; and flat, unhardened steel washers, ASTM F 844.

************************************************************************************************************

### High-strength bolts are used for friction-type connections between steel members and are not recommended by PCI between steel and concrete because concrete creep and crushing of concrete during bolt tightening reduce effectiveness.

### *************************************************************************************************************

High-Strength Bolts and Nuts:  ASTM A 325 or ASTM A 490, Type 1, heavy hex steel structural bolts; heavy hex carbon-steel nuts, ASTM A 563; and hardened carbon-steel washers, ASTM F 436.

Do not zinc coat ASTM A 490 bolts.

***********************************************************************************************************

### Retain first paragraph below if galvanized finish is required.  Revise locations of galvanized items if required.  Field welding is generally not permitted on galvanized elements unless galvanizing is removed or acceptable welding procedures are submitted.  Hot-dip galvanized finish provides greater corrosion resistance than electrodeposited zinc coating.  Electrodeposition is usually limited to threaded fasteners.

### *************************************************************************************************************

Zinc-Coated Finish:  For exterior steel items, [steel in exterior walls], and items indicated for galvanizing, apply zinc coating by [hot-dip process according to ASTM A 123/A 123M or ASTM A 153/A 153M] [electrodeposition according to ASTM B 633, SC 3, Types 1 and 2].

For steel shapes, plates, and tubing to be galvanized, limit silicon content of steel to less than 0.03 percent or to between 0.15 and 0.25 percent or limit sum of silicon and 2.5 times phosphorous content to 0.09 percent.

Galvanizing Repair Paint:  High-zinc-dust-content paint with dry film containing not less than 94 percent zinc dust by weight, and complying with DOD-P-21035B or SSPC-Paint 20.

*************************************************************************************************************

### Retain first paragraph below if paint finish is required.  Revise locations of priming if required.  MPI 79 in first option provides some corrosion protection, while SSPC-Paint 25, without topcoating, provides minimal corrosion protection.

### *************************************************************************************************************

Shop-Primed Finish:  Prepare surfaces of non-galvanized-steel items, except those surfaces to be embedded in concrete, according to requirements in SSPC-SP 3, and shop apply [lead- and chromate-free, rust-inhibitive primer, complying with performance requirements in MPI 79] [SSPC-Paint 25] according to SSPC-PA 1.

Welding Electrodes:  Comply with AWS standards.

Precast Accessories:  Provide clips, hangers, plastic or steel shims, and other accessories required to install precast structural concrete units.

<insert additional materials>

STAINLESS-STEEL CONNECTION MATERIALS

*************************************************************************************************************

### Retain this article when resistance to staining merits extra cost in parking structures and other high-moisture or corrosive areas.

### *************************************************************************************************************

Stainless-Steel Plate:  ASTM A 666, Type 304, of grade suitable for application.

Stainless-Steel Bolts and Studs:  ASTM F 593, Alloy 304 or 316, hex-head bolts and studs; stainless-steel nuts; and flat, stainless-steel washers.  Lubricate threaded parts of stainless-steel bolts with an antiseize thread lubricant during assembly.

Stainless-Steel-Headed Studs:  ASTM A 276, with minimum mechanical properties of PCI MNL 116.

BEARING PADS

************************************************************************************************************

### Retain this article if applicable.  Coordinate selection of bearing pad with fabricator.

### ************************************************************************************************************

Provide one of the following bearing pads for precast structural concrete units[as recommended by precast fabricator for application]:

Elastomeric Pads:  AASHTO M 251, plain, vulcanized, 100 percent polychloroprene (neoprene) elastomer, molded to size or cut from a molded sheet, 50 to 70 Shore, Type A durometer hardness, ASTM D 2240; minimum tensile strength 2250 psi, ASTM D 412.

Random-Oriented, Fiber-Reinforced Elastomeric Pads:  Preformed, randomly oriented synthetic fibers set in elastomer.  70 to 90 Shore, Type A durometer hardness, ASTM D 2240; capable of supporting a compressive stress of 3000 psi with no cracking, splitting, or delaminating in the internal portions of pad.  Test 1 specimen for every 200 pads used in Project.

Cotton-Duck-Fabric-Reinforced Elastomeric Pads:  Preformed, horizontally layered cotton-duck fabric bonded to an elastomer; 80 to 100 Shore, Type A durometer hardness, ASTM D 2240; complying with AASHTO's "AASHTO Load and Resistance Factor Design (LRFD) Bridge Specifications," Division II, Section 18.10.2; or with MIL-C-882E.

Frictionless Pads:  Tetrafluoroethylene, glass-fiber reinforced, bonded to stainless- or mild-steel plate, of type required for in-service stress.

High-Density Plastic:  Multimonomer, nonleaching, plastic strip.

GROUT MATERIALS

*************************************************************************************************************

### Add other proprietary grout systems to suit Project.  Show locations of each grout in this article or on Drawings if retaining more than one type.  Sand-cement grout in first paragraph below is commonly used in keyed joints between hollow-core floor and roof slabs and wall units.

### *************************************************************************************************************

Sand-Cement Grout:  Portland cement, ASTM C 150, Type I, and clean, natural sand, ASTM C 144 or ASTM C 404.  Mix at ratio of 1 part cement to 2-1/2 parts sand, by volume, with minimum water required for placement and hydration.

*************************************************************************************************************

### Retain first paragraph below if nonshrink grout is required or if cement-grout shrinkage could cause structural deficiency. Grout mixture for bonded tendons shall conform to the most stringent standards as specified in the Post Tensioning Manual PTI TAB.1-06 and PCI MNL-116.  For critical installations, require manufacturer to provide field supervision.

### *************************************************************************************************************

Nonmetallic, Nonshrink Grout:  Premixed, nonmetallic, noncorrosive, nonstaining grout containing selected silica sands, Portland cement, shrinkage-compensating agents, plasticizing and water-reducing agents, complying with ASTM C 1107, Grade A for drypack and Grades B and C for flowable grout and of consistency suitable for application within a 30-minute working time.

Epoxy-Resin Grout:  Two-component, mineral-filled epoxy resin; ASTM C 881/C 881M, of type, grade, and class to suit requirements.

INSULATED FLAT WALL PANEL ACCESSORIES

*************************************************************************************************************

### Retain this article if insulated flat wall panels are required.  Retain insulation material in one of first three paragraphs below; if using more then one type, identify location of each on Drawings.

### *************************************************************************************************************

Molded-Polystyrene Board Insulation:  ASTM C 578, [Type I, 0.90 lb/cu. ft.] [Type VIII, 1.15 lb/cu. ft.] [Type II, 1.35 lb/cu. ft.]; [square] [ship-lap] edges; with R-value of <Insert value> and thickness of <Insert dimension>.

Extruded-Polystyrene Board Insulation:  ASTM C 578, [Type IV, 1.60 lb/cu. ft.] [Type X, 1.30 lb/cu. ft.] [Type VI, 1.80 lb/cu. ft.]; [square] [ship-lap] edges; with R-value of <Insert value> and thickness of <Insert dimension>.

Polyisocyanurate Board Insulation:  ASTM C 591, [Type I, 1.8 lb/cu. ft.] [Type IV, 2 lb/cu. ft.] [Type II, 2.5 lb/cu. ft.] unfaced, with R-value of <Insert value> and thickness of <Insert dimension>.

************************************************************************************************************

### Retain one or more wythe connectors in paragraph below.

### *************************************************************************************************************

Wythe Connectors:  [Glass-fiber connectors] [Vinyl-ester polymer connectors] [Polypropylene pin connectors] [Stainless-steel pin connectors] [Bent galvanized reinforcing bars] [Galvanized welded wire trusses] [Galvanized bent wire connectors] [Cylindrical metal sleeve anchors] manufactured to connect wythes of precast concrete panels.

CONCRETE MIXTURES

Prepare design mixtures for each type of precast concrete required.

*************************************************************************************************************

Alkali-Silica Reactivity: The mix design for LANL precast concrete shall contain from 20% to 30% by weight of total cementitious material Type F fly ash conforming to ASTM C 618 for mitigating the deleterious effects of alkali-silica reaction in concrete that is common with the siliceous nature of aggregates found in northern New Mexico. This requirement allows precast concrete from local fabricators to be used. Alkali silica reaction is the reaction between the alkali hydroxide in Portland cement and certain siliceous rocks and minerals present in the aggregates, such as opal, chert, chalcedony, trydymite, cristobalite, strained quartz, etc.  The products of this reaction often result in significant expansion and cracking of the concrete, and ultimately failure of the concrete structure, including significant potential for foreign object damage.

The Engineer of Record may specify a mix design that does not utilize fly ash or other ASR inhibiting admixtures only if the precast plant can produce certified suppliers test reports that show the aggregate is nonreactive according to a preapproved testing standard and durability tests of long term performance show no deleterious effects. This may be the case for out of state precast manufacturers that use aggregate sources in which reactivity is not a concern.

*************************************************************************************************************

All design mixtures must have a minimum of 20% fly ash to assure against alkali-resistivity.

********************************************************************************************************************************************************************

### Retain subparagraph below if required for LEED-NC, LEED-CS, or LEED for Schools Credit ID 1.  This credit can be achieved by replacing at least 40 percent of the Portland cement, which would otherwise be used in concrete, with other cementitious materials.  40 percent replacement value applies to the average of all concrete used for Project; requirement below can be reduced if requirement for other concrete on Project is increased sufficiently to make up for the reduction.

### *************************************************************************************************************

Use fly ash, pozzolan, ground granulated blast-furnace slag, and silica fume as needed to reduce the total amount of Portland cement, which would otherwise be used, by not less than 40 percent.

*********************************************************************************************************************************************************************

Retain subparagraph below if fly ash, granulated blast-furnace slag, or metakaolin and silica fume are permitted.  Percentages are PCI examples; revise to suit Project.

*************************************************************************************************************

Limit use of fly ash to 30 percent replacement of Portland cement by weight and granulated blast-furnace slag to 40 percent of Portland cement by weight; metakaolin and silica fume to 10 percent of Portland cement by weight.

Design mixtures may be prepared by a qualified independent testing agency or by qualified precast plant personnel at precast structural concrete fabricator's option.

Design mixtures must be approved by the New Mexico State Materials Bureau and the Engineer of Record.

Limit water-soluble chloride ions to maximum percentage by weight of cement permitted by ACI 318 or PCI MNL 116 when tested according to ASTM C 1218.

*********************************************************************************************************

Precast structural concrete with architectural finish may be manufactured with a separate face mixture and a structural backup mixture.  Face and backup mixtures require similar shrinkage and expansion coefficients.  Similar water-cementitious materials ratios and cement-aggregate ratios are recommended by PCI to limit bowing or warping.

Retain first option in first paragraph below if lightweight backup concrete mix is required; second option if normal-weight face and backup mixtures are required; third option if full-depth, normal-weight mixture is required; or fourth option if choice of normal-weight face and backup mixtures or full-depth mixtures is fabricator's option.

*******************************************************************************************************

Normal-Weight Concrete Mixtures:  Proportion [face mixtures] [face and backup mixtures] [full-depth mixture] [face and backup mixtures or full-depth mixtures, at fabricator's option] by either laboratory trial batch or field test data methods according to ACI 211.1, with materials to be used on Project, to provide normal-weight concrete with the following properties:

*********************************************************************************************************

Retain first subparagraph below or revise to suit Project.  Higher-strength mixtures may be available; verify availability with fabricators.

*********************************************************************************************************

Compressive Strength (28 Days):  5000 psi.

*********************************************************************************************************

Water-cementitious materials ratio of 0.40 to 0.45 is usual for precast structural concrete.  Lower ratios may be possible with use of high-range water reducers.  Revise ratio in subparagraph below to suit Project.

*********************************************************************************************************

Maximum Water-Cementitious Materials Ratio:  0.45.

*********************************************************************************************************

Water absorption indicates susceptibility to weather staining.  PCI states that limits in first paragraph below are suitable for average exposures.  Different parts of a single panel cannot be produced with different absorptions.  Verify that fabricators can produce units with lower water absorption because special consolidation techniques to increase concrete density are required.

*********************************************************************************************************

Water Absorption:  6 percent by weight or 14 percent by volume, tested according to PCI MNL 116.

*********************************************************************************************************

To minimize bowing or warping, PCI does not recommend lightweight backup mixtures with normal-weight face mixtures.  Retain first paragraph below if required or as an option if satisfactory durability and in-service performance are verified by fabricator.  Coordinate with selection of normal-weight face mixture option above.

**********************************************************************************************************

Lightweight Concrete Backup Mixtures:  Proportion mixtures by either laboratory trial batch or field test data methods according to ACI 211.2, with materials to be used on Project, to provide lightweight concrete with the following properties:

*********************************************************************************************************

Retain first subparagraph below or revise to suit Project.  Higher-strength mixtures may be available; verify availability with fabricators.

*********************************************************************************************************

Compressive Strength (28 Days):  5000 psi.

*********************************************************************************************************

Increase or decrease unit weight in subparagraph below to suit Project.  Coordinate with lightweight-aggregate supplier and precast structural concrete fabricator.  Lightweight concretes with lightweight and normal-weight aggregate in mixture will usually be heavier than unit weight below.

*********************************************************************************************************

Unit Weight:  Calculated equilibrium unit weight of 115 lb/cu. ft., plus or minus 3 lb/cu. ft., according to ASTM C 567.

Add air-entraining admixture at manufacturer's prescribed rate to result in concrete at point of placement having an air content complying with PCI MNL 116.

When included in design mixtures, add other admixtures to concrete mixtures according to manufacturer's written instructions.

Concrete Mix Adjustments: Concrete mix design adjustments may be proposed if characteristics of materials, Project conditions, weather, test results, or other circumstances warrant.

*********************************************************************************************************

### ACI 318, Ch. 4, Durability, requires the EOR to “…assign exposure classes based on the severity of the anticipated exposure of structural concrete members for each exposure category according to Table 4.2.1.”  The typical exposure category in Table 4.2.1 of concern at LANL is F, Freezing and Thawing, and the typical upper-bound severity of exposure is Severe, F2.

### The EOR will specify the concrete exposure category and class in the design.

### The Engineer of Record will specify if durability testing of the concrete mix is required.

*********************************************************************************************************

Durability: Ensure concrete mixture complies with ACI 318 Chapter 4 and PCI MNL 116 for durability.

Durability Testing: [Not Required.] [Test in accordance with ASTM C666 and other applicable standards.]

MOLD FABRICATION

Molds:  Accurately construct molds, mortar tight, of sufficient strength to withstand pressures due to concrete-placement operations and temperature changes and for prestressing and detensioning operations.  Coat contact surfaces of molds with release agent before reinforcement is placed.  Avoid contamination of reinforcement and prestressing tendons by release agent.

*********************************************************************************************************

Retain form liners in subparagraph below if needed to produce exposed surface finish on precast structural concrete with architectural finish.

*********************************************************************************************************

Place form liners accurately to provide finished surface texture indicated.  Provide solid backing and supports to maintain stability of liners during concrete placement.  Coat form liner with form-release agent.

Maintain molds to provide completed precast structural concrete units of shapes, lines, and dimensions indicated, within fabrication tolerances specified.

*********************************************************************************************************

Retain first subparagraph below for precast structural concrete with architectural finishes.

*********************************************************************************************************

Form joints are not permitted on faces exposed to view in the finished work.

********************************************************************************************************

Retain one option from subparagraph below; show details on Drawings or revise description to add dimensions.  Sharp edges or corners of precast concrete units are vulnerable to chipping.

*********************************************************************************************************

Edge and Corner Treatment:  Uniformly [chamfered] [radiused].

FABRICATION

Cast-in Anchors, Inserts, Plates, Angles, and Other Anchorage Hardware:  Fabricate anchorage hardware with sufficient anchorage and embedment to comply with design requirements.  Accurately position for attachment of loose hardware, and secure in place during precasting operations.  Locate anchorage hardware where it does not affect position of main reinforcement or concrete placement.

Weld-headed studs and deformed bar anchors used for anchorage according to 01 4455 “Onsite Welding and Joining Requirements”, and AWS D1.1 and AWS C5.4, "Recommended Practices for Stud Welding."

**********************************************************************************************************

Coordinate first paragraph below with Section 05 5000 Metal Fabrications for furnishing and installing loose hardware items.

*********************************************************************************************************

Furnish loose hardware items including steel plates, clip angles, seat angles, anchors, dowels, cramps, hangers, and other hardware shapes for securing precast structural concrete units to supporting and adjacent construction.

Cast-in reglets, slots, holes, and other accessories in precast structural concrete units as indicated on the Contract Drawings.

*********************************************************************************************************

Retain first paragraph below if applicable.

*********************************************************************************************************

Cast-in openings larger than 10 inches in any dimension.  Do not drill or cut openings or prestressing strand without EOR's approval.

Reinforcement:  Comply with recommendations in PCI MNL 116 for fabricating, placing, and supporting reinforcement.

Clean reinforcement of loose rust and mill scale, earth, and other materials that reduce or destroy the bond with concrete.  When damage to epoxy-coated reinforcement exceeds limits specified, repair with patching material compatible with coating material and epoxy coat bar ends after cutting.

Accurately position, support, and secure reinforcement against displacement during concrete-placement and consolidation operations.  Completely conceal support devices to prevent exposure on finished surfaces.

Place reinforcing steel and prestressing strand to maintain at least 3/4-inch minimum concrete cover.  Increase cover requirements for reinforcing steel to 1-1/2 inches when units are exposed to corrosive environment or severe exposure conditions.  Arrange, space, and securely tie bars and bar supports to hold reinforcement in position while placing concrete.  Direct wire tie ends away from finished, exposed concrete surfaces.

Install welded wire fabric in lengths as long as practicable.  Lap adjoining pieces at least one full mesh spacing and wire tie laps, where required by design.  Offset laps of adjoining widths to prevent continuous laps in either direction.

Reinforce precast structural concrete units to resist handling, transportation, and erection stresses.

*********************************************************************************************************

Retain first paragraph below if precast, prestressed structural concrete units are required.  Decision to prestress may be left to fabricator if objective is to aid handling and to control cracking of units during installation.

*********************************************************************************************************

Prestress tendons for precast structural concrete units by either pretensioning or post-tensioning methods.  Comply with PCI MNL 116 and [PTI TAB.1-06].

*********************************************************************************************************

In accordance with IBC paragraph 1901.4 and ACI 318 paragraph 16.2, the minimum concrete compressive strength at the time of transfer/release of the prestressing force shall be indicated on the drawings, in the first subparagraph below, or both.

For information on the subject of, and the requirements associated with, ‘transfer/release’ and associated ‘compressive strength’ refer to the following:

- 	Pre-tensioning (i.e., detensioning and minimum concrete transfer strength): ACI 318 paragraphs 12.9 and 18.4, PCI MNL-120 paragraphs 5.2.2 and 5.2.3, and PCI MNL-116 paragraphs 4.1.2 and 5.3.17.

- 	Post-tensioning (i.e., tensioning and minimum concrete transfer strength/ concrete strength at jacking): ACI 318 paragraphs 18.4 and 18.13, and PCI MNL-116 paragraphs 4.1.2 and 5.4.4.

*********************************************************************************************************

Do not detension pre-tensioning tendons, or tension post-tensioning tendons, of precast, prestressed structural concrete units until concrete has achieved [     ]psi [the associated indicated] compressive strength as established by test cylinders cured under same conditions as concrete.

[Detension pretensioned tendons either by gradually releasing tensioning jacks or by heat cutting tendons, using a sequence and pattern to prevent shock or unbalanced loading.]

[If concrete has been heat cured, detension while concrete is still warm and moist to avoid dimensional changes that may cause cracking or undesirable stresses.]

[Perform post-tensioning in steps and measure the prestressing force, elongation of tendons, and indicate actual location of tendons. Maintain jacking and tensioning records for Project Records Submittals.]

[Jack against tendon pressure plate.]

**********************************************************************************************************

Note that for bonded tendons the Post Tensioning Manual PTI TAB.1-06 gives a very thorough discussion regarding grouting when bonded tendons are used, including equipment and construction procedures.

*********************************************************************************************************

[Bonded tendons: Inject grout continuously, in one direction, and in one stage.]

Protect strand ends and anchorages with bituminous, zinc-rich, or epoxy paint to avoid corrosion and possible rust spots.

*********************************************************************************************************

#### Retain subparagraph below only when appearance of member ends is critical or when exposed to severe environment.

#### *********************************************************************************************************

Protect strand ends and anchorages with a minimum of 1-inch-thick, nonmetallic, nonshrink, grout mortar and sack rub surface.  Coat or spray the inside surfaces of pocket with bonding agent before installing grout.

Comply with requirements in PCI MNL 116 and in this Section for measuring, mixing, transporting, and placing concrete.  After concrete batching, no additional water may be added.

*********************************************************************************************************

#### Retain first paragraph below if a separate face mixture is proposed for precast structural concrete with architectural finish.

#### *********************************************************************************************************

Place face mixture to a minimum thickness after consolidation of the greater of 1 inch or 1.5 times the maximum aggregate size, but not less than the minimum reinforcing cover specified.

Place concrete in a continuous operation to prevent seams or planes of weakness from forming in precast concrete units.

*********************************************************************************************************

#### Retain subparagraph below if a separate face mixture is proposed for precast structural concrete with architectural finish.

#### *********************************************************************************************************

Place backup concrete mixture to ensure bond with face-mixture concrete.

Thoroughly consolidate placed concrete by internal and external vibration without dislocating or damaging reinforcement and built-in items, and minimize pour lines, honeycombing, or entrapped air on surfaces.  Use equipment and procedures complying with PCI MNL 116.

*********************************************************************************************************

#### Retain subparagraph below if permitting self-consolidating concrete.

#### *********************************************************************************************************

Place self-consolidating concrete without vibration according to PCI TR-6, "Interim Guidelines for the Use of Self-Consolidating Concrete in Precast/Prestressed Concrete Institute Member Plants."

Comply with ACI 306.1 procedures for cold-weather concrete placement.

Comply with PCI MNL 116 procedures for hot-weather concrete placement.

Identify pickup points of precast structural concrete units and orientation in structure with permanent markings, complying with markings indicated on Shop Drawings.  Imprint or permanently mark casting date on each precast structural concrete unit on a surface that will not show in finished structure.

Cure concrete, according to requirements in PCI MNL 116, by moisture retention without heat or by accelerated heat curing using low-pressure live steam or radiant heat and moisture.  Cure units until compressive strength is high enough to ensure that stripping does not have an effect on performance or appearance of final product.

Discard and replace precast structural concrete units that do not comply with requirements, including structural, manufacturing tolerance, and appearance, unless repairs meet requirements in PCI MNL 116 and meet EOR's approval.

CASTING INSULATED WALL PANELS

*********************************************************************************************************

#### Retain this article if integrally insulated wall panels are required.

#### *********************************************************************************************************

Cast and screed wythe supported by mold.

Place insulation boards abutting edges and ends of adjacent boards.  Insert wythe connectors through insulation, and consolidate concrete around connectors according to connector manufacturer's written instructions.

Ensure bottom wythe and insulation layer are not disturbed after bottom wythe reaches initial set.

Cast and screed top wythe to meet required finish.

FABRICATION TOLERANCES

Fabricate precast structural concrete units straight and true to size and shape with exposed edges and corners precise and true so each finished unit complies with PCI MNL 116 product dimension tolerances.

COMMERCIAL FINISHES

*************************************************************************************************************

#### Retain type of commercial structural finish, grouped by PCI as a "C" designation, in one or more of first four paragraphs below.  If more than one finish is required, create a finish schedule, add locations to finish descriptions, or indicate on Drawings.  Finishes below are in ascending order of finish quality and cost.  Insert other specific finish requirements to suit Project.

#### Retain "Commercial Grade" Paragraph below when product will not be visible in completed structure or when function of structure does not require an enhanced surface.  This finish is essentially an "as-cast" one.

#### *************************************************************************************************************

Commercial Grade:  Remove fins and large protrusions and fill large holes.  Rub or grind ragged edges.  Faces must have true, well-defined surfaces.  Air holes, water marks, and color variations are permitted.  Limit form joint offsets to 3/16 inch.

*********************************************************************************************************

Retain "Standard Grade" Paragraph below where products are exposed to view but function of structure does not require a special finish.  Surface is suitable for an applied textured coating but not necessarily suitable for painting.  This finish is typical for structural products.

*********************************************************************************************************

Standard Grade:  Normal plant-run finish produced in molds that impart a smooth finish to concrete.  Surface holes smaller than 1/2 inch caused by air bubbles, normal color variations, form joint marks, and minor chips and spalls are permitted.  Fill air holes greater than 1/4 inch in width that occur more than once per 2 sq. in.  Major or unsightly imperfections, honeycombs, or structural defects are not permitted.  Limit joint offsets to 1/8 inch.

*********************************************************************************************************

Retain "Grade B Finish" Paragraph below for visually exposed structural members such as columns or walls.

*********************************************************************************************************

Grade B Finish:  Fill air pockets and holes larger than 1/4 inch in diameter with sand-cement paste matching color of adjacent surfaces.  Fill air holes greater than 1/8 inch in width that occur more than once per 2 sq. in..  Grind smooth form offsets or fins larger than 1/8 inch.  Repair surface blemishes due to holes or dents in molds.  Discoloration at form joints is permitted.

*********************************************************************************************************

Retain "Grade A Finish" Paragraph below where surface will be painted or coated with a textured or sanded coating; some surface blemishes will be visible.  If a surface with fewer imperfections than permitted Grade A finish is needed, retain a finish from "Commercial Architectural Finishes" Article.  Grade A finish is not applicable to extruded precast structural concrete products using zero-slump concrete in their process.

*********************************************************************************************************

Grade A Finish:  Fill surface blemishes with the exception of air holes 1/16 inch in width or smaller, and form marks where the surface deviation is less than 1/16 inch.  Float apply a neat cement-paste coating to exposed surfaces.  Rub dried paste coat with burlap to remove loose particles.  Discoloration at form joints is permitted.  Grind smooth all form joints.

*********************************************************************************************************

Retain one of first two paragraphs below.  Screed or float finish in first paragraph is standard with PCI for unformed surfaces.  Revise to describe extent to which float or trowel marks, variations of texture, or other surface blemishes will be permitted.  Require samples to establish acceptance criteria for any exposed finish.  Revise finish below to light-broom or as-cast finish if float finish is unnecessary.

*********************************************************************************************************

Screed or float finish unformed surfaces.  Strike off and consolidate concrete with vibrating screeds to a uniform finish.  Hand screed at projections.  Normal color variations, minor indentations, minor chips, and spalls are permitted.  Major imperfections, honeycombing, or defects are not permitted.

*********************************************************************************************************

Retain first paragraph below if upgrading unformed surfaces to smooth, steel trowel finish.

*********************************************************************************************************

Smooth, steel trowel finish unformed surfaces.  Consolidate concrete, bring to proper level with straightedge, float, and trowel to a smooth, uniform finish.

*********************************************************************************************************

Retain paragraph below if composite concrete topping is required.

*********************************************************************************************************

Apply roughened surface finish according to ACI 318 to precast concrete units that will receive concrete topping after installation.

COMMERCIAL ARCHITECTURAL FINISHES

*********************************************************************************************************

Retain this article if precast structural concrete receives an architectural finish.  Indicate on Drawings which members require architectural finish.

*********************************************************************************************************

Manufacture member faces free of joint marks, grain, and other obvious defects with corners, including false joints, uniform, straight, and sharp.  Finish exposed-face surfaces of precast concrete units to match approved [design reference sample] [sample panels] [mockups] and as follows:

*********************************************************************************************************

Retain first subparagraph below if EOR has preapproved one or more design reference samples.  Include complete description of design reference sample here.  If preapproving fabricators, coordinate with "Manufacturers" Article.  Revise if multiple samples are approved.

*********************************************************************************************************

Design Reference Sample:  <Insert description and identify fabricator and code number of sample>.

*********************************************************************************************************

Retain first subparagraph below if required.  If retaining, revise and add reference number; PCI publishes numbered, color photographs of hundreds of precast concrete finishes; see PCI's Web site, www.pci.org.  Add reference number combinations if more than one finish is required.

*********************************************************************************************************

PCI's "Architectural Precast Concrete - Color and Texture Selection Guide," of plate numbers indicated.

*********************************************************************************************************

Select type of finish from nine subparagraphs below if needed.  If more than one finish is required, create a finish schedule, add locations to finish descriptions, or indicate on Drawings.  Add more-detailed descriptions of finishes outlined below if greater definition, such as light, medium, or deep reveal to finishes that expose the aggregate, is required.  See PCI MNL 117 for more information on architectural finishes.

Retain first subparagraph below if a smooth-surface finish, an as-cast finish, which generally results in a mottled surface or non-uniform finish, is required.

*********************************************************************************************************

Smooth-Surface Finish:  Provide surfaces free of excessive air voids, sand streaks, and honeycombs, with uniform color and texture.

Textured-Surface Finish:  Impart by form liners or inserts to provide surfaces free of pockets, streaks, and honeycombs, with uniform color and texture.

Bushhammer Finish:  Use power or hand tools to remove matrix and fracture coarse aggregates.

Exposed-Aggregate Finish:  Use chemical-retarding agents applied to concrete molds and washing and brushing procedures to expose aggregate and surrounding matrix surfaces after form removal.

Abrasive-Blast Finish:  Use abrasive grit, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces.

Acid-Etched Finish:  Use acid and hot-water solution, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces.  Protect hardware, connections, and insulation from acid attach.

Honed Finish:  Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

Polished Finish:  Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

Sand-Embedment Finish:  Use selected stones placed in a sand bed in bottom of mold, with sand removed after curing.

SOURCE QUALITY CONTROL

************************************************************************************************************

Always retain first paragraph below because it establishes a minimum standard of plant testing and inspecting.  PCI MNL 116 mandates source testing requirements and a plant "Quality Systems Manual."  PCI plant certification also ensures periodic auditing of plants complying with PCI MNL 116.

************************************************************************************************************

Quality-Control Testing:  Test and inspect precast structural concrete according to PCI MNL 116 requirements.

*************************************************************************************************************

Retain subparagraph below if permitting self-consolidating concrete.

*************************************************************************************************************

Test and inspect self-consolidating concrete according to PCI TR-6.

Special Inspections: In addition to PCI Certification, Owner will engage a qualified Special Inspector to evaluate the structural precast concrete fabricator’s quality-control and testing methods.

Allow Owner’s Special Inspectors access to material storage areas, concrete production equipment, concrete placement, and curing facilities. Cooperate with Owner’s Special Inspectors and provide samples of materials and concrete mixtures as may be requested for additional testing and evaluation.

Strength of precast structural concrete units will be considered deficient if units fail to comply with ACI 318 requirements for concrete strength.

*************************************************************************************************************

Revise testing and acceptance criteria in first paragraph below if required.  Revise to add criteria for load tests if required.

*************************************************************************************************************

If there is evidence that strength of precast concrete units may be deficient or may not comply with ACI 318 requirements, employ a qualified testing agency to obtain, prepare, and test cores drilled from hardened concrete to determine compressive strength according to ASTM C 42.

A minimum of three representative cores will be taken from units of suspect strength, from locations directed by EOR.

Cores will be tested in an air-dry condition or, if units will be wet under service conditions, test cores after immersion in water in a wet condition.

*************************************************************************************************************

PCI's recommendations in first subparagraph below are more stringent than ACI's.

*************************************************************************************************************

Strength of concrete for each series of 3 cores will be considered satisfactory if average compressive strength is equal to at least 85 percent of 28-day design compressive strength and no single core is less than 75 percent of 28-day design compressive strength.

Test results will be made in writing on same day that tests are performed, with copies to EOR, Subcontractor, and precast concrete fabricator.  Test reports will include the following:

Project identification name and number.

Date when tests were performed.

Name of precast concrete fabricator.

Name of concrete testing agency.

Identification letter, name, and type of precast concrete unit(s) represented by core tests; design compressive strength; type of break; compressive strength at breaks, corrected for length-diameter ratio; and direction of applied load to core in relation to horizontal plane of concrete as placed.

Patching:  If core test results are satisfactory and precast structural concrete units comply with requirements, clean and dampen core holes and solidly fill with same precast concrete mixture that has no coarse aggregate, and finish to match adjacent precast concrete surfaces.

Defective Units:  Discard and replace precast structural concrete units that do not comply with requirements, including strength, manufacturing tolerances, and color and texture range.  Chipped, spalled, or cracked units may be repaired, subject to EOR's approval.  EOR reserves the right to reject precast units that do not match approved samples, sample panels, and mockups.

EXECUTION

EXAMINATION

Examine supporting structural frame or foundation and conditions for compliance with requirements for installation tolerances, true and level bearing surfaces, and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

Do not install precast concrete units until supporting, cast-in-place, building structural framing has attained minimum allowable design compressive strength or until supporting steel or other structure is complete.

INSTALLATION

Install clips, hangers, bearing pads, and other accessories required for connecting precast structural concrete units to supporting members and backup materials.

Erect precast structural concrete level, plumb, and square within specified allowable tolerances.  Provide temporary structural framing, supports, and bracing as required to maintain position, stability, and alignment of units until permanent connection.

Install temporary steel or plastic spacing shims or bearing pads as precast structural concrete units are being erected.  Tack-weld steel shims to each other to prevent shims from separating.

Maintain horizontal and vertical joint alignment and uniform joint width as erection progresses.

Remove projecting lifting devices and grout fill voids within recessed lifting devices flush with surface of adjacent precast surfaces when recess is exposed.

*********************************************************************************************************

Retain subparagraph below if voids of hollow-core slabs are used for electrical raceways or mechanical ducts.

*********************************************************************************************************

For hollow-core slab voids used as electrical raceways or mechanical ducts, align voids between units and tape butt joint at end of slabs.

Connect precast structural concrete units in position by bolting, welding, grouting, or as otherwise indicated on Shop Drawings.  Remove temporary shims, wedges, and spacers as soon as practical after connecting and grouting are completed.

Do not permit connections to disrupt continuity of roof flashing.

Field cutting of precast units is not permitted without approval of the EOR.

*******************************************************************************************************

First paragraph below refers to fastening under the control of precast concrete erector.  Coordinate with and repeat warning in other Sections if additional construction will be fastened to precast, prestressed concrete units.

*********************************************************************************************************

Fasteners:  Do not use drilled or powder-actuated fasteners for attaching accessory items to precast, prestressed concrete units.

Welding:  Comply with applicable AWS D1.1 and AWS D1.4 for welding, welding electrodes, appearance, quality of welds, and methods used in correcting welding work.

Protect precast structural concrete units and bearing pads from damage by field welding or cutting operations, and provide noncombustible shields as required.

Clean weld-affected steel surfaces with chipping hammer followed by brushing, and apply a minimum 4.0-mil- thick coat of galvanized repair paint to galvanized surfaces according to ASTM A 780.

*********************************************************************************************************

Retain subparagraph above or first subparagraph below.

*********************************************************************************************************

Clean weld-affected steel surfaces with chipping hammer followed by brushing, and re-prime damaged painted surfaces.

Remove, reweld, or repair incomplete and defective welds.

At bolted connections, use lock washers, tack welding, or other approved means to prevent loosening of nuts after final adjustment.

Where slotted connections are used, verify bolt position and tightness.  For sliding connections, properly secure bolt but allow bolt to move within connection slot.  For friction connections, apply specified bolt torque and check 25 percent of bolts at random by calibrated torque wrench.

*********************************************************************************

In paragraph below, revise locations and extent of grouting if required.

**********************************************************************************

Grouting:  Grout connections and joints and open spaces at keyways, connections, and joints where required or indicated on Shop Drawings.  Retain grout in place until hard enough to support itself.  Pack spaces with stiff grout material, tamping until voids are completely filled.

Place grout to finish smooth, level, and plumb with adjacent concrete surfaces.

Fill joints completely without seepage to other surfaces.

Trowel top of grout joints on roofs smooth and uniform.  Finish transitions between different surface levels not steeper than 1 to 12.

*******************************************************************************

Retain first subparagraph below if end grouting hollow-core slabs is required.

********************************************************************************

Place grout end cap or dam in voids at ends of hollow-core slabs.

Promptly remove grout material from exposed surfaces before it affects finishes or hardens.

Keep grouted joints damp for not less than 24 hours after initial set.

ERECTION TOLERANCES

Erect precast structural concrete units level, plumb, square, true, and in alignment without exceeding the noncumulative erection tolerances of PCI MNL 135.

Minimize variations between adjacent slab members by jacking, loading, or other method recommended by fabricator and approved by EOR.

FIELD QUALITY CONTROL

********************************************************************************************************

Retain first option in first paragraph below if Owner engages special inspector.  Consider retaining second option if authorities having jurisdiction allow Subcontractor to engage special inspector.  If retaining second option, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

*********************************************************************************************************

Special Inspections:  Owner will engage a qualified Special Inspector to perform the following special inspections:

Erection of precast structural concrete members.

<Insert special inspections>.

*********************************************************************************************************

Retain first paragraph below, with or without paragraph above, to identify who shall perform tests and inspections.  If retaining second option in first paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

*********************************************************************************************************

Testing Agency:  Owner will engage a qualified testing agency to perform tests and inspections.

Field welds will be visually inspected and nondestructive tested according to ASTM E 165 or ASTM E 709 as well as 01 4455 “Onsite Welding and Joining Requirements”.  High-strength bolted connections will be subject to inspections.

Testing agency will report test results promptly and in writing to Subcontractor and EOR.

Repair or remove and replace work where tests and inspections indicate that it does not comply with specified requirements.

Additional testing and inspecting, at Subcontractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

Prepare test and inspection reports.

REPAIRS

*********************************************************************************************************

Blemishes occurring after delivery are normally repaired after erecting units.  Repairs of production chips, cracks, and spalls take place at manufacturer's plant.

*********************************************************************************************************

Repair precast structural concrete units if permitted by EOR.

Repairs may be permitted if structural adequacy, serviceability, durability, and appearance of units has not been impaired.

*********************************************************************************************************

Precast concrete manufacturer develops appropriate repair mixtures and techniques during production sample approval process.

*********************************************************************************************************

Mix patching materials and repair units so cured patches blend with color, texture, and uniformity of adjacent exposed surfaces and show no apparent line of demarcation between original and repaired work, when viewed in typical daylight illumination from a distance of 20 feet.

Prepare and repair damaged galvanized coatings with galvanizing repair paint according to ASTM A 780.

*********************************************************************************************************

Retain paragraph above if using galvanized anchors, connections, and other items; retain first paragraph below if items are prime painted.

*********************************************************************************************************

Wire brush, clean, and paint damaged prime-painted components with same type of shop primer.

Remove and replace damaged precast structural concrete units that cannot be repaired or when repairs do not comply with requirements as determined by EOR.

CLEANING

Clean mortar, plaster, fireproofing, weld slag, and other deleterious material from concrete surfaces and adjacent materials immediately.

Clean exposed surfaces of precast concrete units after erection and completion of joint treatment to remove weld marks, other markings, dirt, and stains.

Perform cleaning procedures, if necessary, according to precast concrete fabricator's written recommendations.  Clean soiled precast concrete surfaces with detergent and water, using stiff fiber brushes and sponges, and rinse with clean water.  Protect other work from staining or damage due to cleaning operations.

Do not use cleaning materials or processes that could change the appearance of exposed concrete finishes or damage adjacent materials.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 03 4100 Rev. 1, dated 
November 6, 2014.