SECTION 08 3323

OVERHEAD COILING DOORS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project, add specification requirements not included herein as well as delete specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - [Service doors [with integral pass doors].]

          - [Insulated service doors [with integral pass doors].]

          - [Fire-rated service doors [with integral pass doors].]

          - [Fire-rated, insulated service doors [with integral pass doors].]

        - Related Requirements:

Retain Sections in subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 05 5000 Metal Fabrications for [miscellaneous steel supports,] [door-opening framing,] [corner guards,] [and] [bollards].

          - [Section 08 7100 Door Hardware for lockset, exit hardware and lock cylinder requirements]

          - [Section 09 9100 Painting for finish painting of factory-primed doors.]

          - [Section 111200 Parking Control Equipment for parking control equipment interlocked to overhead coiling doors.]

      - REFERENCES

- ********************************************************************************************************* Edit the references to include only those that apply to the edited specification section.

- *********************************************************************************************************

        - American Aluminum Manufacturer’s Association (AAMA)

      - AAMA 611 – Voluntary Specification for Anodized Architectural Aluminum.

        - American Society of Civil Engineers / Structural Engineering Institute (ASCE/SEI)

          - ASCE/SEI 7 – Minimum Design Loads For Buildings and Other Structures.

        - ASTM International

          - ASTM A 653 – Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-coated (Galvanized) by the Hot-Dip Process.

          - ASTM A 666 – Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar.

          - ASTM B 209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

          - ASTM B 221 – Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

          - ASTM E 84 – Standard Test Method for Surface Burning Characteristics of Building Materials.

          - ASTM E 90 – Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements.

          - ASTM E 283 – Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

          - ASTM E 330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference.

          - ASTM E 413 – Classification for Rating Sound Insulation.

          - ASTM E 1996 - Standard Specification for Performance of Exterior Windows, Curtain Walls, Doors, and Impact Protective Systems Impacted by Windborne Debris in Hurricanes.

        - National Association of Architectural Metal Manufacturers / National Ornamental and Miscellaneous Metals Association (NAAMM / NOMMA)

          - NAAMM Metal Finishes Manual

        - National Electrical Manufacturer’s Association (NEMA)

          - NEMA ICS 1 – Industrial Control and Systems General Requirements.

          - NEMA ICS 2 - Controllers, Contactors and Overload Relays Rated Not More Than 2,000 V AC or 750 V DC, Part 8: Disconnect Devices for Use in Industrial Control Equipment.

          - NEMA ICS 6 – Enclosures.

        - National Fire Protection Association (NFPA)

          - NFPA 70 – National Electrical Code.

          - NFPA 80 – Standard for Fire Doors and Other Opening Protectives.

          - NFPA 105 – Standard for Smoke Door Assemblies and Other Opening Protectives

          - NFPA 252 – Standard Methods of Fire Tests of Door Assemblies.

        - Underwriters Laboratory (UL)

          - UL 325 – Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

          - UL 723 – Standard for Test for Surface Burning Characteristics of Building Materials.

          - UL 1784 – Standard for Air Leakage Tests of Door Assemblies and Other Opening Protectives

- ************************************************************************************************************

- Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

- ************************************************************************************************************

      - ACTION SUBMITTALS

        - [Product Data: For each type and size of overhead coiling door and accessory.

          - Include construction details, material descriptions, dimensions of individual components, profiles for slats, and finishes.

Retain first subparagraph below for power-operated doors.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished accessories.

Retain subparagraph below for fire-rated doors.

          - Include description of automatic-closing device and testing and resetting instructions.]

        - [Shop Drawings: For each installation and for special components not dimensioned or detailed in manufacturer's product data.

          - Include plans, elevations, sections, and mounting details.

          - Include details of equipment assemblies, and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include points of attachment locations.

          - For exterior components, include details of provisions for assembly expansion and contraction and for excluding and draining moisture to the exterior.

Retain option in first subparagraph below for fire-rated doors.

          - Show locations of controls, locking devices [, detectors or replaceable fusible links], and other accessories.

Retain subparagraph below if equipment includes wiring.

          - Include diagrams for power, signal, and control wiring.]

Retain "Samples for Initial Selection" and "Samples for Verification" paragraphs below for two-stage Samples.

        - [Samples for Initial Selection: Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes.

          - Include similar Samples of accessories involving color selection.]

        - [Samples for Verification: For each type of exposed finish on the following components, in manufacturer's standard sizes:

Revise subparagraphs below to suit Project; delete items not required.

          - Curtain slats [, including full vision window secured to slat].

Retain option in first subparagraph below if required for electric door operators.

          - Bottom bar [with sensor edge].

          - Guides.

          - Brackets.

          - Hood.

          - Locking device(s).

          - Include similar Samples of accessories involving color selection.]

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - [Qualification Data: For Installer.]

        - [[Oversize Construction Certification: For door assemblies required to be fire-rated and that exceed size limitations of labeled assemblies.]

        - [Sample Warranty: For special warranty.]

      - CLOSEOUT SUBMITTALS

        - [Maintenance Data: For overhead coiling doors to include in maintenance manuals.]

        - [Warranty: For overhead doors and all components.]

      - QUALITY ASSURANCE

        - Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.

Retain "Maintenance Proximity" Subparagraph below if retaining "Maintenance Service" Article.

          - Maintenance Proximity: Not more than [four] <Insert number> hours' normal travel time from Installer's place of business to Project site.

Retain "Fire-Rated Door Assemblies" Paragraph below if applicable. Overhead coiling doors are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 feet 6 inches (4.11 m). See the Evaluations.

        - Fire-Rated Door Assemblies: Complying with NFPA 80; listed and labeled by qualified testing agency, for fire-protection ratings indicated, based on testing at as close to neutral pressure as possible according to NFPA 252.

Retain "Oversize Fire-Rated Door Assemblies" Subparagraph below if required and acceptable to authorities having jurisdiction.

          - Oversize Fire-Rated Door Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

Retain "Temperature-Rise Limit" Subparagraph below if required. The IBC allows an exception for buildings equipped throughout with fire-suppression sprinklers.

          - Temperature-Rise Limit: [Where indicated] [At exit enclosures and exit passageways], provide doors that have a maximum transmitted temperature end point of not more than 450 deg F above ambient after 30 minutes of standard fire-test exposure.

          - Smoke Control: Where indicated, provide doors that are listed and labeled with the letter "S" on the fire-rating label by a qualified testing agency for smoke- and draft-control based on testing according to UL 1784; with maximum air-leakage rate of 3.0 cfm/sq. ft. of door opening at 0.10-inch wg for both ambient and elevated temperature tests.

Retain "Sound-Control Doors" Paragraph below if acoustically rated doors are required.

        - Sound-Control Doors: Assemblies tested in a laboratory for sound-transmission-loss performance according to ASTM E 90, calculated according to ASTM E 413, and rated for not less than the STC value indicated.

Generally, retain only one of first two options in "Accessibility Standard" Paragraph below. Retain first option for facilities covered under the Americans with Disabilities Act (ADA) of 1990. Retain second for facilities covered under the Architectural Barriers Act (ABA). Retain last option for compliance with the IBC.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer agrees to repair or replace components of doors that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for lifts and components.

          - Warranty Period: [Two] <Insert number> years from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Subcontractor's product selection, see Section 01 6000 "Product Requirements."

      - MANUFACTURERS

        - Source Limitations: Obtain overhead coiling doors from single source from single manufacturer.

Retain subparagraph below or revise to suit Project.

          - Obtain operators and controls from overhead coiling-door manufacturer.

      - PERFORMANCE REQUIREMENTS

Retain "Structural Performance, Exterior Doors" Paragraph below for exterior doors.

        - Structural Performance, Exterior Doors: Capable of withstanding the following design wind loads:

- Second option in "Design Wind Load" Subparagraph below is minimum design pressure advertised by manufacturers. Usually indicate on Drawings the design wind loads, as determined by Project's structural engineer. Verify requirements of authorities having jurisdiction. See the Evaluations.

- Design Wind Load: As indicated on Drawings, acting inward and outward.

Retain "Testing" Subparagraph below if required by authorities having jurisdiction. Consult manufacturers for availability of tested assemblies.

- Testing: According to ASTM E 330.

Revise "Deflection Limits" Subparagraph below to suit Project; verify deflection limits with manufacturer. If using doors as storm shutters to protect glass, stricter deflection limits may be required.

- Deflection Limits: Design overhead coiling doors to withstand design wind load without evidencing permanent deformation or disengagement of door components.

"Operability under Wind Load" Subparagraph below is an uncommon requirement; verify availability with manufacturer. See "Wind Loads" Article in the Evaluations.

- Operability under Wind Load: Design overhead coiling doors to remain operable under design wind load, acting inward and outward.

Retain "Windborne-Debris Impact Resistance" Paragraph below if required for Project. The IBC establishes criteria for buildings in hurricane-prone locations. Retain only one of first four options; retain DASMA 115 option only for glazed garage doors. Wind Zone 4 criteria (hurricane exposure) is now optional according to ASTM E 1996. Verify requirements of authorities having jurisdiction.

        - Windborne-Debris Impact Resistance: Provide [glazed] [and] [impact-protective] overhead coiling doors that pass missile-impact and cyclic-pressure tests according to ASTM E 1996 utilizing wind design criteria as indicated on Drawings.

"Large-Missile Test" and "Small-Missile Test" subparagraphs below refer only to ASTM E 1996 testing. DASMA 115 testing includes only large missiles.

          - Large-Missile Test: For overhead coiling doors located within 30 feet of grade.

          - Small-Missile Test: For overhead coiling doors located more than 30 feet above grade.

Retain "Seismic Performance" Paragraph below if required for Project. Nonstructural architectural components in Seismic Design Category A are exempt from seismic design requirements; and in Seismic Design Category B, nonstructural architectural components are generally exempt if the Component Importance Factor is 1.0. Coordinate requirements with Project's structural engineer.

        - Seismic Performance: Overhead coiling doors shall withstand the effects of earthquake motions determined according to ASCE/SEI 7 based on seismic criteria indicated on Drawings.

The value in "Component Importance Factor" Subparagraph below is determined according to ASCE/SEI 7 based on anticipated risk and need. Revise subparagraph if more than one coiling door is required and they have different component importance factors. Coordinate requirement with Project's structural engineer.

      - DOOR ASSEMBLY

Copy this article and re-edit for each non-fire-rated coiling-door unit. This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities. For each door assembly, retain required options in this article and their related requirements in other Part 2 articles. Consult manufacturers for recommendations and availability.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - [Fire Rated] [and] [Non-Fire Rated] [Service] [Insulated Service] Door: Overhead coiling door formed with curtain of interlocking metal slats. Acceptable manufacturers include:

          - Cookson Company.

          - Overhead Door Company.

          - Wayne-Dalton Door Company.

        - [Fire Rating: [3/4 hour] [1 hour] [1-1/2 hours] [3 hours] [4 hours] [with temperature-rise limit] [and] [with smoke control].]

Retain one of five options in "Operation Cycles" Paragraph below. First option is standard with some manufacturers; second option is more commonly used. Last three options are for high-cycle operation, corrosive environments, and severe or abusive use. Consult manufacturer for recommendations.

Retain subparagraph below if high-cycle doors are specified.

Retain "Air Infiltration" Paragraph below if required for exterior doors. Rates in first two options are examples only. First option is for "garage doors" and second is for "rolling doors" according to the International Energy Conservation Code. Coiling-door manufacturers typically comply with second option. Retain "DASMA 105" option for garage doors. According to DASMA 105, air-infiltration testing is based on ASTM E 283 but is performed at wind velocities of 15 and 25 mph (24.1 and 40.2 km/h) across the specimen, not at specified pressure differences as required by ASTM E 283. Manufacturers generally do not publish air-infiltration testing or values according to ASTM E 283 or DASMA 105. Verify availability of tested assemblies and tested values with manufacturer.

        - Air Infiltration: Maximum rate of 1.0 cfm/sq. ft. at 15 and 25 mph when tested according to ASTM E 283.

Retain "STC Rating" Paragraph below for acoustically insulated doors. Verify STC rating availability with manufacturers.

        - STC Rating: 20 minimum.

Retain "Curtain R-Value" Paragraph below for thermally insulated doors.

        - [Curtain R-Value: Minimum 7.0 deg F x h x sq. ft. /Btu.]

        - Door Curtain Material: [Galvanized steel] [Stainless steel] [Aluminum].

Slat profile and sizes in "Door Curtain Slats" Paragraph below vary among manufacturers. Revise size to a range if exact size is not important. Curved slats are not insulated.

        - Door Curtain Slats: [Curved] [Flat] profile slats of [1-7/8-inch] [2-5/8-inch] [3-1/4-inch] <Insert dimension> center-to-center height.

          - [[Perforated Slats: Approximately [1/16-inch pinholes] [3/32-inch pinholes] [7/8-inch wide by 3/8-inch high slots] <Insert dimensions>.]

          - [Fenestrated Slats: Approximately [3- by 5/8-inch] [4- by 5/8-inch] [10- by 1-inch] <Insert dimensions> openings spaced approximately [1-1/2 inches] <Insert dimension> apart and beginning 12 inches from jamb guides.]

Retain opening size and spacing in "Vision Panels" Subparagraph below or revise to suit Project. Retain last option for use in thermally insulated doors.

          - [Vision Panels: Approximately 10- by 1-inch openings spaced approximately 2 inches apart and beginning 12 inches from end guides; in [two] [three] <Insert number> rows of slats at height indicated on Drawings; installed with[ insulated] vision-panel glazing.

Revise "Insulated-Slat Interior Facing" Subparagraph below to suit Project. This facing functions as a thermal barrier and its material is restricted for garage doors according to the IBC. See the Evaluations.

          - Insulated-Slat Interior Facing: [Metal] [Plastic].

Feature in "Gasket Seal" Subparagraph below is available from some manufacturers and can improve overall performance but may be less durable than entirely metal-on-metal slats. Verify availability with manufacturer.

          - Gasket Seal. Manufacturer's standard continuous gaskets between slats.

        - Bottom Bar: Two angles, each not less than [1-1/2 by 1-1/2 by 1/8 inch thick] <Insert dimensions>; fabricated from [hot-dip galvanized steel] [stainless steel] [or] [aluminum extrusions] and finished [to match door] <Insert requirement>.

First two options in "Curtain Jamb Guides" Paragraph below are most commonly used for service doors.

        - Curtain Jamb Guides: [Galvanized steel] [Stainless steel] [Aluminum] with exposed finish matching curtain slats.

If used for emergency egress, pass doors must comply with the egress door requirements of the local code.

        - Pass Door(s): [Hinged] [Rigid] frame with [lockset] [exit hardware].

        - Hood: [Match curtain material and finish] [Galvanized steel] [Stainless steel] [Aluminum].

First option in "Shape" Subparagraph below is standard. Verify availability of second option with manufacturer.

          - Shape: [Round] [Square] [As indicated on Drawings] <Insert shape>.

          - Mounting: [Face of wall] [Between jambs] [As indicated on Drawings].

Retain one of first two options in "Locking Devices" Paragraph below. Retain last option for chain-hoist-operated doors or emergency chain-hoist operation. The industry generally discourages using locks on motor-operated coiling doors; see the Evaluations.

        - Locking Devices: Equip door with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain "Locking Device Assembly" Subparagraph below if retaining "locking device assembly" option in "Locking Devices" Paragraph above.

          - Locking Device Assembly: [Single-jamb side] [both jamb sides] locking bars, operable from [inside with thumbturn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain "Manual Door Operator" or "Electric Door Operator" Paragraph below.

        - [Manual Door Operator: [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator] [Wall-crank operator].

Retain first subparagraph below for chain or crank operator if located on other side of wall from door curtain.

          - Provide operator with through-wall shaft operation.

Retain subparagraph below for crank operator if required.

          - Provide operator with manufacturer's standard removable operating arm.]

        - [Electric Door Operator:

Retain one of four options in "Usage Classification" Subparagraph below or revise to suit Project. Usage classification varies among manufacturers and for each operator design; it is a durability requirement separate from whole-door "operation cycles." Consult manufacturer for specific recommendations.

          - Usage Classification: [Heavy duty, 25 or more cycles per hour and more than 90 cycles per day] [Standard duty, up to 25 cycles per hour and up to 90 cycles per day] [Medium duty, up to 12 cycles per hour and up to 50 cycles per day] [Light duty, up to 10 cycles per hour] <Insert classification>.

          - Operator Location: [Top of hood] [Front of hood] [Wall] [Bench] [Through wall] [As indicated on Drawings].

Retain "Safety" Subparagraph below if door is used as an automatic garage door; consider retaining it for all power-operated doors. Option is requirement of UL 325; revise to suit Project. The IBC requires listing for automatic garage door openers.

          - Safety: Listed according to UL 325 by a qualified testing agency for commercial or industrial use [with moving parts of operator enclosed or guarded if exposed and mounted at 8 feet or lower].

Retain one of two options in "Motor Exposure" Subparagraph below or revise to suit Project. The operating environment, including hazardous conditions, may require other motor types and enclosure modifications.

          - Motor Exposure: [Interior] [Exterior, wet, and humid].

Retain "Motor Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

          - Motor Electrical Characteristics:

            - Horsepower: [1/2] [1] [2] [3] <Insert value> hp.

Retain one of two "Voltage" subparagraphs below for ac systems.

            - Voltage: [115-V ac] [208-V ac] [230-V ac], single phase, 60 Hz.

            - Voltage: [208-V ac] [230-V ac] [460-V ac], three phase, 60 Hz.

          - Emergency Manual Operation: [Push-up] [Chain] [Crank] type.

Retain "Obstruction-Detection Device" Subparagraph below if door is used as an automatic garage door; consider retaining it for other door uses.

          - Obstruction-Detection Device: Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring type] <Insert type>.

Retain "Sensor Edge Bulb Color" Subparagraph below if retaining second or third option in "Obstruction-Detection Device" Subparagraph above.

            - Sensor Edge Bulb Color: [Black] [As selected by Architect from manufacturer's full range] <Insert color>.

          - Control Station(s): [Interior mounted] [Exterior mounted] [Where indicated on Drawings] <Insert location>.

          - Other Equipment: [Audible and visual signals] [Portable radio-control system] <Insert device>.]

See "Curtain Accessories" Article for where each option in "Curtain Accessories" Paragraph below is used.

        - Curtain Accessories: Equip door with [smoke seals] [weatherseals] [astragal] [push/pull handles] [pull-down strap] [polel hook] [and] [automatic-closing device] <Insert item>.

        - Door Finish:

Retain one of first four subparagraphs below. These include advertised materials and finishes; available materials and finishes vary with each manufacturer. If retaining more than one, indicate location of each on Drawings or by inserts.

Second option in "Aluminum Finish" Subparagraph below is standard; verify availability of other aluminum finishes with manufacturer.

          - Aluminum Finish: [Mill] [Clear anodized] [Light bronze anodized] [Medium bronze anodized] [Dark bronze anodized] [Black anodized] [Anodized color matching Architect's sample] [Anodized color as selected by Architect from full range of industry colors and color densities] <Insert color>.

          - Baked-Enamel or Powder-Coated Finish: [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color>.

          - Factory Prime Finish: Manufacturer's standard color.

Second option in "Stainless-Steel Finish" Subparagraph below is standard; verify availability of other stainless-steel finishes with manufacturer.

          - Stainless-Steel Finish: [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain "Interior Curtain-Slat Facing" Subparagraph below for insulated door curtains.

          - Interior Curtain-Slat Facing: [Match finish of exterior curtain-slat face] [Finish as indicated by manufacturer's designations] [Finish matching Architect's sample] [Finish as selected by Architect from manufacturer's full range] <Insert finish>.

      - MATERIALS, GENERAL

Retain this article for motorized operator.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - DOOR CURTAIN MATERIALS AND CONSTRUCTION

- Curtains: Fabricate overhead coiling-door curtain of interlocking metal slats, designed to withstand wind loading indicated, in a continuous length for width of door without splices. Unless otherwise indicated, provide slats of thickness and mechanical properties recommended by door manufacturer for performance, size, and type of door indicated, and as follows:

Retain one or more of "Steel Door Curtain Slats," "Stainless-Steel Door Curtain Slats," and "Aluminum Door Curtain Slats" subparagraphs below for required slat materials. Consult manufacturers' data and revise subparagraphs to specify other materials if needed. Verify sheet thicknesses with manufacturer.

          - [Steel Door Curtain Slats: Zinc-coated (galvanized), cold-rolled structural-steel sheet; complying with ASTM A 653, with G90 zinc coating; nominal sheet thickness (coated) of 0.028 inch.]

          - [Stainless-Steel Door Curtain Slats: ASTM A 666, Type 304; sheet thickness of 0.025 inch.]

Aluminum is not applicable to fire-rated assemblies.

          - [Aluminum Door Curtain Slats: ASTM B 209 sheet or ASTM B 221 extrusions, alloy and temper standard with manufacturer for type of use and finish indicated; thickness of 0.050 inch.]

Retain "Vision-Panel Glazing" Subparagraph below if vision panels are required for curtain slats. Vision-panel availability may be limited to some manufacturers and according to type of slat. Verify availability with manufacturer.

          - [Vision-Panel Glazing: Manufacturer's standard clear glazing, fabricated from transparent acrylic sheet or fire-protection-rated glass as required for type of door; set in glazing channel secured to curtain slats.]

Retain "Insulation," "Metal Interior Curtain-Slat Facing," and "Plastic Interior Curtain-Slat Facing" subparagraphs below as required for thermally or acoustically insulated doors; revise to suit Project.

          - [Insulation: Fill slats for insulated doors with manufacturer's standard thermal insulation complying with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, according to ASTM E 84 or UL 723. Enclose insulation completely within slat faces.]

"Metal Interior Curtain-Slat Facing" and "Plastic Interior Curtain-Slat Facing" subparagraphs below describe different interior facings for insulated slats; facing in first subparagraph is most common. For garage doors, the IBC requires a minimum thickness of aluminum, steel, or wood as a thermal barrier over foam-plastic insulation (polystyrene or polyurethane foam or board) or testing according to DASMA 107. Aluminum is not applicable to fire-rated assemblies. See the Evaluations.

          - Metal Interior Curtain-Slat Facing: Match metal of exterior curtain-slat face, with [minimum steel thickness of 0.010 inch [and] [minimum aluminum thickness of 0.032 inch].

- Curtain Jamb Guides: Manufacturer's standard angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading. Slot bolt holes for guide adjustment. Provide removable stops on guides to prevent overtravel of curtain[, and a continuous bar for holding windlocks].

Retain "Pass Door(s)" Paragraph below if pass doors are required.

- Pass Door(s): Swinging-door and frame assembly constructed integrally with the coiling-door assembly [and bearing the same fire rating]. Comply with the accessibility standard of authorities having jurisdiction.

          - Door Frame and Integral Jamb Guide: Fabricate of angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading.

Frame in "Hinged Frame" Subparagraph below is available from many manufacturers. See the Evaluations.

          - Hinged Frame: Hinged pass door and frame that swings out of the way, as a unit, to allow use of the full coiling-door opening width. One jamb of the pass-door frame is hinged and the other jamb includes a guide for the lower, narrower part of the coiling-door curtain.

Retain "Rigid Frame" Subparagraph below only if there is sufficient headroom above door to accommodate rigid lower part of coiling door that contains the pass door. This type is available from McKeon; verify availability with other manufacturers.

          - Rigid Frame: Rigid pass door and frame that are built into the rigid, lower part of the door curtain and that raise with the curtain.

          - Locking Hardware:

Consult manufacturer on hardware that can be installed in pass doors.

            - [Lockset] [Exit Hardware]: [As specified in Section 08 7100 "Door Hardware."] [As selected by Architect from manufacturer's full range.] <Insert requirement.>

Retain one of first three options in "Lock Cylinders" Subparagraph below.

            - Lock Cylinders: As [specified in Section 08 7100 "Door Hardware"] [standard with manufacturer] [and keyed to building keying system].

Retain "Keys" Subparagraph below if cylinders are provided by door manufacturer.

            - Keys: [Two] [Three] <Insert number> for each cylinder.

Revise "Thresholds" Subparagraph below to suit Project.

          - Thresholds: Equip pass doors with integral thresholds that comply with the accessibility standard of authorities having jurisdiction.

      - HOODS

Retain requirements in this article to suit Project. If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

Retain "General" Paragraph below if coiled curtain and operating mechanism are exposed (not concealed in ceiling or soffit); consider retaining a hood even if coiled door is above ceiling.

        - General: Form sheet metal hood to entirely enclose coiled curtain and operating mechanism at opening head. Contour to fit end brackets to which hood is attached. Roll and reinforce top and bottom edges for stiffness. Form closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting that projects beyond wall face. Equip hood with intermediate support brackets as required to prevent sagging.

Retain required material(s) in "Galvanized Steel," "Stainless Steel," and "Aluminum" subparagraphs below. Thicker steel sheet is available from some manufacturers; verify availability.

          - [Galvanized Steel: Nominal 0.028-inch thick, hot-dip galvanized-steel sheet with G90 zinc coating, complying with ASTM A 653.]

          - [Stainless Steel: 0.025-inch thick, stainless-steel sheet, Type 304, complying with ASTM A 666.]

"Aluminum" Subparagraph below is for non-fire-rated doors only. Clear- and color-anodized finishes are available.

          - [Aluminum: 0.040-inch thick aluminum sheet complying with ASTM B 209, of alloy and temper recommended by manufacturer and finisher for type of use and finish indicated.]

Retain first subparagraph below for fire-rated assemblies.

          - Include automatic drop baffle on fire-rated doors to guard against passage of smoke or flame.

Retain "Exterior-Mounted Doors" Subparagraph below for exterior-mounted doors.

          - Exterior-Mounted Doors: Fabricate hood to act as weather protection and with a perimeter sealant-joint-bead profile for applying joint sealant.

Retain "Removable Metal Soffit" Paragraph below for concealed installations only. Metal soffit is not often used. Indicate location, details, and size on Drawings.

        - Removable Metal Soffit: Formed or extruded from same metal and with same finish as curtain if hood is mounted above ceiling unless otherwise indicated.

      - LOCKING DEVICES

Retain requirements in this article to suit Project. If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

Retain one of or both "Slide Bolt" and "Locking Device Assembly" paragraphs below for required locking device(s); revise to suit Project. First paragraph is standard for push-up doors; revise if no padlock is required or if manufacturer's standard is a bolt on one side. Second paragraph describes a locking device with choice of locations and operation as retained in door assembly articles in Part 2.

        - Slide Bolt: Fabricate with side-locking bolts to engage through slots in tracks for locking by padlock, located on both left and right jamb sides, operable from coil side.

        - Locking Device Assembly: Fabricate with cylinder lock, spring-loaded dead bolt, operating handle, cam plate, and adjustable locking bars to engage through slots in tracks.

Retain one of first three options in "Lock Cylinders" Subparagraph below.

          - Lock Cylinders: As [specified in Section 08 7100 "Door Hardware"] [standard with manufacturer] [and keyed to building keying system].

Retain "Keys" Subparagraph below if cylinders are provided by door manufacturer.

          - Keys: [Two] [Three] <Insert number> for each cylinder.

Retain "Chain Lock Keeper" Paragraph below for chain-hoist-operated doors or emergency chain-hoist operation.

        - Chain Lock Keeper: Suitable for padlock.

Retain "Safety Interlock Switch" Paragraph below for power-operated doors.

        - Safety Interlock Switch: Equip power-operated doors with safety interlock switch to disengage power supply when door is locked.

      - CURTAIN ACCESSORIES

Retain requirements in this article to suit Project. If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

Retain "Smoke Seals" Paragraph below for fire-rated doors.

        - [Smoke Seals: Equip each fire-rated door with replaceable smoke-seal perimeter gaskets or brushes for smoke and draft control as required for door listing and labeling by a qualified testing agency.]

Retain "Weatherseals for Exterior Doors" Paragraph below if required.

        - Weatherseals for Exterior Doors: Equip each exterior door with weather-stripping gaskets fitted to entire exterior perimeter of door for a weather-resistant installation unless otherwise indicated.

          - At door head, use 1/8-inch thick, replaceable, continuous-sheet baffle secured to inside of hood or field-installed on the header.

          - At door jambs, use replaceable, adjustable, continuous, [flexible, 1/8-inch thick seals of flexible vinyl, rubber, or neoprene] [nylon brushes] <Insert material>.

Retain "Astragal for Interior Doors" Paragraph below for interior doors.

        - [Astragal for Interior Doors: Equip each door bottom bar with a replaceable, adjustable, continuous, compressible gasket of flexible vinyl, rubber, or neoprene as a cushion bumper.]

Retain "Push/Pull Handles" Paragraph below for push-up-operated doors or emergency push-up operation.

        - [Push/Pull Handles: Equip each push-up-operated or emergency-operated door with lifting handles on each side of door, finished to match door.]

Retain "Pull-Down Strap" or "Poll Hooks" Paragraph below if required. Consult manufacturer for recommendations.

        - [Pull-Down Strap: Provide pull-down straps for doors more than 84 inches high.]

        - [Pole Hooks: Provide pole hooks and poles for doors more than 84 inches high.]

Retain "Automatic-Closing Device" Paragraph below for fire-rated doors.

        - [Automatic-Closing Device: Equip each fire-rated door with an automatic-closing device or holder-release mechanism and governor unit complying with NFPA 80 and an easily tested and reset release mechanism.[ Testing for manually operated doors shall allow resetting by opening the door without re-tensioning the counterbalance mechanism][ Release mechanism for motor-operated doors shall allow testing without mechanical release of the door.] Automatic-closing device shall be designed for activation by the following:

Retain one or more of four subparagraphs below and insert others if required to suit Project. If more than one type of activation (or combination) is required, identify primary and secondary closing devices. Verify requirements of authorities having jurisdiction. See the Evaluations.

Retain first subparagraph below to comply with NFPA 80 requirement for fusible links on both sides of door opening. Revise if not required on both sides of door opening or to add fusible-link ceiling unit for use with suspended ceilings.

          - Replaceable fusible links with temperature rise and melting point of [165 deg F] <Insert temperature> interconnected and mounted on both sides of door opening.

          - Manufacturer's standard UL-labeled smoke detector and door-holder-release devices.

          - Manufacturer's standard UL-labeled heat detector and door-holder-release devices.

          - Building fire-detection, smoke-detection, and -alarm systems.]

Insert other accessories to suit Project.

      - COUNTERBALANCE MECHANISM

Retain this article for all doors.

        - General: Counterbalance doors by means of manufacturer's standard mechanism with an adjustable-tension, steel helical torsion spring mounted around a steel shaft and contained in a spring barrel connected to top of curtain with barrel rings. Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

In "Counterbalance Barrel" Paragraph below, retain "seamless" option for greatest durability and "welded" option for lower cost and smaller doors. Consult manufacturer for recommendations.

        - Counterbalance Barrel: Fabricate spring barrel of manufacturer's standard hot-formed, structural-quality, seamless or welded carbon-steel pipe, of sufficient diameter and wall thickness to support rolled-up curtain without distortion of slats and to limit barrel deflection to not more than 0.03 in./ft. of span under full load.

        - Counterbalance Spring: One or more oil-tempered, heat-treated steel helical torsion springs. Size springs to counterbalance weight of curtain, with uniform adjustment accessible from outside barrel. Secure ends of springs to barrel and shaft with cast-steel barrel plugs.

          - Fire-Rated Doors: Equip with auxiliary counterbalance spring and prevent tension release from main counterbalance spring when automatic-closing device operates.

        - Torsion Rod for Counterbalance Shaft: Fabricate of manufacturer's standard cold-rolled steel, sized to hold fixed spring ends and carry torsional load.

        - Brackets: Manufacturer's standard mounting brackets of either cast iron or cold-rolled steel plate.

      - [MANUAL DOOR OPERATORS

Retain this article for manually operated doors, not including emergency manual operation for electric door operators.

Retain requirements in this article to suit Project. If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

        - General: Equip door with manual door operator by door manufacturer.

Requirement in "Push-up Door Operation" Paragraph below is common for service doors with area of not more than 80 sq. ft. (7.4 sq. m). Standard operation force as high as 35 lbf (156 N) is offered by manufacturers.

        - Push-up Door Operation: Lift handles and pull rope for raising and lowering doors, with counterbalance mechanism designed so that required lift or pull for door operation does not exceed 25 lb.

Items in "Chain-Hoist Operator" and "Crank Operator" paragraphs below are common for manually operated doors with area of more than 80 sq. ft. (7.4 sq. m).

        - Chain-Hoist Operator: Consisting of endless steel hand chain, chain-pocket wheel and guard, and gear-reduction unit with a maximum 25-lb force for door operation. Provide alloy-steel hand chain with chain holder secured to operator guide.

"Awning" and "box" are the two types of crank operators. Indicate required type in door assembly articles retained in Part 2.

        - Crank Operator: Consisting of crank and crank gearbox, steel crank drive shaft, and gear-reduction unit, of type indicated. Size gears to require not more than 25-lb force to turn crank. Fabricate gearbox to be oil-tight and to completely enclose operating mechanism. Provide manufacturer's standard crank-locking device.]

      - [ELECTRIC DOOR OPERATORS

Retain this article for electric door operators, including emergency manual operation, and for larger units and remotely controlled or frequently operated doors. Coordinate with Project's electrical engineer for interface of electric door operators and equipment with fire-protection system.

Retain requirements in this article to suit Project. If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

        - General: Electric door operator assembly of size and capacity recommended and provided by door manufacturer for door and operation-cycles requirement specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, control stations, control devices, integral gearing for locking door, and accessories required for proper operation.

Consider naming a door-operator model or manufacturer or basis-of-design door-operator model or manufacturer only if known and available from coiling-door manufacturer and other operators are unacceptable. Specific operators may not be available from all door manufacturers; operator features may not be common to all operator manufacturers. Consult door manufacturers for recommendations.

          - Comply with NFPA 70.

          - Control equipment complying with NEMA ICS 1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24-V AC or DC.

Durability requirement in "Usage Classification" Paragraph below is separate from "operation cycles," which apply to the whole door system and are specified in door assembly articles.

        - Door Operator Location(s): Operator location indicated for each door.

Retain one or more of five subparagraphs below to suit Project. Delete all subparagraphs if operator location(s) is indicated on Drawings.

          - [Top-of-Hood Mounted: Operator is mounted to the right or left door head plate with the operator on top of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets. Headroom is required for this type of mounting.]

          - [Front-of-Hood Mounted: Operator is mounted to the right or left door head plate with the operator on coil side of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets. Front clearance is required for this type of mounting.]

          - [Wall Mounted: Operator is mounted to the inside front wall on the left or right side of door and connected to door drive shaft with drive chain and sprockets. Side room is required for this type of mounting. Wall-mounted operator can also be mounted above or below shaft; if above shaft, headroom is required.]

          - [Bench Mounted: Operator is mounted to the right or left door head plate and connected to the door drive shaft with drive chain and sprockets. Side room is required for this type of mounting.]

          - [Through-Wall Mounted: Operator is mounted on other side of wall from coil side of door.]

Retain option in "Motors" Paragraph below unless external controller (disconnect switch) is indicated on Drawings. Coordinate with Project's electrical engineer.

        - Motors: Reversible-type motor [with controller (disconnect switch)] for motor exposure indicated for each door assembly.

Speed in "Electrical Characteristics" Subparagraph below is for standard-speed doors. Consult manufacturer and revise for higher-speed operation.

          - Electrical Characteristics: Minimum as indicated for each door assembly. If not indicated, large enough to start, accelerate, and operate door in either direction from any position, at a speed not less than 8 in./sec. and not more than 24 in./sec., without exceeding nameplate ratings or service factor.

Revise "Operating Controls, Controllers, Disconnect Switches, Wiring Devices, and Wiring" Subparagraph below if required; coordinate requirements with Project's electrical engineer. Verify which electrical devices, connections, and wiring, if any, are furnished or installed by other than coiling-door manufacturer; these devices must comply with requirements for electrical devices and connections specified elsewhere.

          - Operating Controls, Controllers, Disconnect Switches, Wiring Devices, and Wiring: Manufacturer's standard unless otherwise indicated.

          - Coordinate wiring requirements and electrical characteristics of motors and other electrical devices with building electrical system and each location where installed.

        - Limit Switches: Equip each motorized door with adjustable switches interlocked with motor controls and set to automatically stop door at fully opened and fully closed positions.

Retain "Obstruction-Detection Devices" Paragraph below if required; revise if required for fire-rated door applications according to requirements of authorities having jurisdiction.

        - Obstruction-Detection Devices: External entrapment protection consisting of indicated automatic safety sensor capable of protecting full width of door opening.[ For non-fire-rated doors, activation of device immediately stops and reverses downward door travel.][For fire-rated doors, activation delays closing.]

Retain one of or both "Photoelectric Sensor" and "Electric Sensor Edge" subparagraphs below to suit Project.

          - Photoelectric Sensor: Manufacturer's standard system designed to detect an obstruction in door opening without contact between door and obstruction.

Retain "Self-Monitoring Type" Subparagraph below if a self-monitoring system to detect failure of sensing device is required.

            - Self-Monitoring Type: Designed to interface with door operator control circuit to detect damage to or disconnection of sensing device. When self-monitoring feature is activated, door closes only with sustained or constant pressure on close button.

          - Electric Sensor Edge: Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor activates device. Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

Retain "Self-Monitoring Type" Subparagraph below if a self-monitoring system to detect failure of sensing device is required.

            - Self-Monitoring Type: Four-wire-configured device designed to interface with door operator control circuit to detect damage to or disconnection of sensor edge.

Device in "Pneumatic Sensor Edge" Subparagraph below may be limited to a width of 18 feet (5.5 m); verify availability with manufacturer.

          - Pneumatic Sensor Edge: Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor activates device.

Retain "Control Station" Paragraph for control stations in fixed locations. A sustained- or constant-pressure (in lieu of a momentary-contact) switch is required for closing according to UL 325 for commercial doors and may also be required for opening cycles according to authorities having jurisdiction; revise requirements and door assembly articles retained in Part 2 as needed.

        - Control Station: Three-button control station in fixed location with momentary-contact push-button controls labeled "Open" and "Stop" and sustained- or constant-pressure push-button control labeled "Close."

Retain "Interior-Mounted Units" Subparagraph below for interior, clean, and dry installations. Revise to suit Project.

          - Interior-Mounted Units: Full-guarded, surface-mounted, heavy-duty type, with general-purpose NEMA ICS 6, Type 1 enclosure.

Retain "Exterior-Mounted Units" Subparagraph below for exterior, dusty, wet, or humid installations. Revise to suit Project.

          - Exterior-Mounted Units: Full-guarded, standard-duty, surface-mounted, weatherproof type, NEMA ICS 6, Type 4 enclosure, key operated.

        - Emergency Manual Operation: Equip each electrically powered door with capability for emergency manual operation. Design manual mechanism so required force for door operation does not exceed 25 lb. force.

        - Emergency Operation Disconnect Device: Equip operator with hand-operated disconnect mechanism for automatically engaging manual operator and releasing brake for emergency manual operation while disconnecting motor without affecting timing of limit switch. Mount mechanism so it is accessible from floor level. Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

        - Motor Removal: Design operator so motor may be removed without disturbing limit-switch adjustment and without affecting emergency manual operation.

Insert additional equipment for door operation if required; verify availability with manufacturer. Remaining paragraphs are examples only; retain or revise to suit Project.

        - Audible and Visual Signals: Audible alarm and visual indicator lights in compliance with the accessibility standard.

Retain "Portable Radio-Control System" Paragraph below if required as an auxiliary device; revise to suit Project.

        - Portable Radio-Control System: Consisting of [one] [two] <Insert number> of the following per door operator:

          - Three-channel universal coaxial receiver to open, close, and stop door.

          - Portable control device to open and stop door may be momentary-contact type; control to close door shall be sustained- or constant-pressure type.

Retain subparagraph below if antenna is required.

          - Remote-antenna mounting kit.]

      - GENERAL FINISH REQUIREMENTS

        - Comply with NAAMM/NOMMA 500 for recommendations for applying and designating finishes.

        - Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

      - ALUMINUM FINISHES

Retain finishes in this article to suit Project. If retaining more than one for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2. Revise finish designation if custom anodized finish is required and availability is verified.

        - Mill Finish: Manufacturer's standard.

Retain one of two options in "Clear Anodic Finish" Paragraph below. Class II finish is standard with many manufacturers; Class I finish is heavy anodized. Verify availability with manufacturer.

        - Clear Anodic Finish: AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in "Color Anodic Finish" Paragraph below. Verify availability with manufacturer.

        - Color Anodic Finish: AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

"Baked-Enamel or Powder-Coat Finish" Paragraph below references AAMA standard for pigmented organic coating on extrusions and panels.

        - Baked-Enamel or Powder-Coat Finish: AAMA 2603. Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

      - STEEL AND GALVANIZED-STEEL FINISHES

Revise article title if galvanized surfaces are not finish painted.

Retain "Factory Prime Finish" or "Baked-Enamel or Powder-Coat Finish" Paragraph below, or both. If retaining both paragraphs for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

        - Factory Prime Finish: Manufacturer's standard primer, compatible with field-applied finish. Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

        - Baked-Enamel or Powder-Coat Finish: Manufacturer's standard baked-on finish consisting of prime coat and thermosetting topcoat. Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

For exact finish, insert names of coating manufacturers and products.

      - STAINLESS-STEEL FINISHES

        - Surface Preparation: Remove tool and die marks and stretch lines, or blend into finish.

Retain "Polished Finishes" or "Bright, Cold-Rolled, Unpolished Finish" Paragraph below, or both. Directional satin finish is the standard stainless-steel finish for all manufacturers. Verify availability of other finishes with manufacturer. If retaining more than one for different doors and to identify optional requirements for a single door, revise requirements below and insert text as needed in door assembly articles retained in Part 2.

        - Polished Finishes: Grind and polish surfaces to produce uniform finish, free of cross scratches.

Retain first subparagraph below for directional finishes.

          - Run grain of directional finishes with long dimension of each piece.

          - When polishing is completed, passivate and rinse surfaces. Remove embedded foreign matter and leave surfaces chemically clean.

          - Directional Satin Finish: No. 4.

Retain "Bright, Cold-Rolled, Unpolished Finish" Paragraph below for nondirectional finish.

        - Bright, Cold-Rolled, Unpolished Finish: No. 2B.

- EXECUTION

      - EXAMINATION

        - Examine substrates areas and conditions, with Installer present, for compliance with requirements for substrate construction and other conditions affecting performance of the Work.

        - Examine locations of electrical connections.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install overhead coiling doors and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports; according to manufacturer's written instructions and as specified.

        - Install overhead coiling doors, hoods, controls, and operators at the mounting locations indicated for each door.

        - Accessibility: Install overhead coiling doors, switches, and controls along accessible routes in compliance with the accessibility standard.

Retain "Fire-Rated Doors," "Smoke-Control Doors," and "Power-Operated Doors" paragraphs below if required.

        - Fire-Rated Doors: Install according to NFPA 80.

        - Smoke-Control Doors: Install according to NFPA 80 and NFPA 105.

Option in "Power-Operated Doors" Paragraph below is according to minimum IBC requirement for "automatic garage door openers." Delete option to include all power-operated doors.

        - Power-Operated Doors: Install [automatic garage doors openers] according to UL 325.

      - STARTUP SERVICE

        - Engage a factory-authorized service representative to perform startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

          - Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

Retain subparagraph below for fire-rated doors. Verify whether testing is required by authorities having jurisdiction; revise accordingly.

          - Test door closing when activated by detector or alarm-connected automatic-closing system. Reset door-closing mechanism after successful test.

      - ADJUSTING

        - Adjust hardware and moving parts to function smoothly so that doors operate easily, free of warp, twist, or distortion.

Retain subparagraph below for exterior doors.

          - Adjust exterior doors and components to be weather resistant.

        - Lubricate bearings and sliding parts as recommended by manufacturer.

Retain paragraph below if weather-resistant installation or smoke-control doors are required.

        - Adjust seals to provide tight fit around entire perimeter.

      - MAINTENANCE SERVICE

Verify with Owner that maintenance service is required for Project.

        - Initial Maintenance Service: Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of coiling-door Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper door operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.

Retain one of two subparagraphs below. Generally retain second subparagraph, which adds appreciable cost, only for critical locations.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, seven-day-per-week, emergency callback service.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead coiling doors.

end of section

************************************************************
Do not delete the following reference information:

************************************************************

THE FOLLOWING REFERENCE IS for lanl use only

This project specification is based on LANL Master Specification Section 08 3323 Rev. 3, dated May 11, 2017.