SECTION 09 5100

ACOUSTICAL CEILINGS

*************************************************************************************************************

LANL GUIDE SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements. It is the responsibility of the Design Agency’s Structural Engineer of Record to design the ceiling suspension system to accommodate all anticipated loading including seismic restraint and provide adequate calculation and drawing documentation to support the design. Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Suspended metal grid ceiling system and perimeter trim.

Acoustic [tile] [panels] [metal pans]

Supplementary acoustic insulation over system units.

related requirements

[Section 03 1512 Post-Installed Concrete Anchors – High Confidence]

[Section 03 1534 Post-Installed Concrete Anchors – Normal Confidence]

07 2100 Insulation

07 9200 Joint Sealants

08 3100 Access Doors and Panels

09 2116 Gypsum Board Systems

21 1313 Wet Pipe Sprinkler System: Sprinkler Heads in Ceiling Systems

23 3700 Air Outlets and Inlets: Air Diffusion Devices in Ceiling Systems

26 5100 Interior Lighting: Light Fixtures in Ceiling System

27 3000 Voice Communications: Speakers in Ceiling System

28 3100 Fire Detection and Alarm: Fire Alarm Components in Ceiling System

rEFERENCE STANDARDS

ASTM International:

ASTM C635 - Standard Specification for the Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-in Panel Ceilings.

ASTM C636 - Standard Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-In Panels.

ASTM E84 – Standard Test Method for Surface Burning Characteristics of Building Materials.

ASTM E119 – Standard Test Methods for Fire Tests of Building Construction and Materials.

ASTM E580/E580M - Standard Practice for Application of Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels in Areas Requiring Seismic Restraint.

ASTM E1264 - Standard Classification for Acoustical Ceiling Products.

American Society of Civil Engineers:

ASCE 7 - Minimum Design Loads for Buildings and Other Structures.

Ceilings and Interior Systems Construction Association:

CISCA - Acoustical Ceilings: Use and Practice.

UL – Underwriters Laboratory Directory of Construction Materials.

**************************************************************************************************
Include the following paragraph as required to coordinate acoustical ceiling installation with other trades.
***************************************************************************************************

[ADMINISTRATIVE REQUIREMENTS]

[Pre-installation Conference: Conduct conference at Project site to:

Review interfaces with mechanical and electrical systems.

Review and finalize construction schedule and verify availability of materials, Installer’s personnel, equipment, and facilities needed to meet the schedule and avoid delays.]

ACTION / INFORMATIONAL SUBMITTALS

    - [Product Data: Unless providing exactly as specified, submit data for grid system, panels, and accessories; electrical resistance characteristics and ground connection requirements.]

    - Shop Drawings: Indicate ceiling layout, interruptions to grid, [special sized panels,] panels requiring drilling or cut-out for services, appurtenances or interruptions, edge details, [elevation differences,] [location of mechanical and electrical interfaces,] [and] [________].

*************************************************************************************************************

Include the following paragraph for submission of physical samples for selection of finish, color, texture, and other properties unless selected during design and specified in 2.1.A below.

*************************************************************************************************************

    - [Samples: Submit two [____x____] inch in size of ceiling grid and panel, illustrating finishes and color.]

    - Manufacturer's Installation Instructions: Submit special procedures, perimeter conditions requiring special attention, and [________].

  - SUSTAINABLE DESIGN SUBMITTALS

Manufacturer's Certificate: Certify products meet or exceed specified sustainable design requirements.

*************************************************************************************************************

Edit material certifications list to suit products specified in this section and Project sustainable design requirements.

*************************************************************************************************************

      - Materials Resources Certificates:

  - Certify source and origin for [salvaged] [and] [reused] products.

  - Certify recycled material content for recycled content products.

  - Certify source for local and regional materials and distance from Project site.

      - Indoor Air Quality Certificates: Certify volatile organic compound content for each interior sealant and related primer.

  - CLOSEOUT SUBMITTALS

- Operation and Maintenance Data

- Warranty Documentation

- Project Records Documentation

  - EXTRA STOCK MATERIALS Submittals

    - Furnish [________] sq ft of extra [tile] [panels] [metal pans] to the LANL Subcontract Technical Representative (STR).

****** [OR] ******

    - Furnish [________] percent of total acoustic unit area of extra [tile] [panels] [metal pans] to the LANL Subcontract Technical Representative (STR).

  - QUALITY ASSURANCE

    - QUALIFICATIONS

      - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum three years [documented] experience.

      - Installer: Company specializing in performing Work of this section [with minimum [________] years [documented] experience [approved by manufacturer].

    - Source Limitations:  Obtain ceiling system through one source from a single manufacturer.

    - Seismic Standard:  Provide acoustical panel ceilings designed including typical 2 foot by 4 foot electrical ceiling light (maximum design weight 35 lbs.) and installed to withstand the effects of earthquakes according to the following:

      - Standard for Ceiling Suspension Systems Requiring Seismic Retraint:  Comply with ASTM C635, ASTM C636 and ASTM E580.

      - CISCA’s Guidelines for Systems Requiring Seismic Restraint:  Comply with CISCA’s “Guidelines for Seismic Restraint of Direct-Hung Suspended Ceiling Assemblies – Seismic Zones 3 & 4>

      - ASCE 7, “Minimum Design Loads for Buildings and Other Structures”, Section 9, “Earthquake Loads”.

      - Seismic-Restraint Loading:

        - Occupancy Category as Defined in IBC:  II

        - Site Class as Defined in IBC:  D

        - Seismic Design Category as Defined in the IBC: D

        - Component Importance Factor:  1.0

        - Component Response Modification Factor 2.5

        - Component Amplification Factor: 1.0.

********************************************************************************************************** Fire rated ceiling system includes all elements above ceiling including floor or roof construction and can include specially constructed gypsum box or acoustic panel surrounding light fixtures and mechanical work. 
***********************************************************************************************************

    - Fire Rated [Floor] [Roof] Construction: [Rating as indicated on Drawings] [[_________] hour rating].

      - Tested Rating: Determined in accordance with ASTM E119.

************************************************************************************************************* Refer to IBC for tables of fire resistance ratings for various material and assemblies. Tables use item numbers to identify each assembly.
*************************************************************************************************************

      - Prescriptive Rating: [Item Number [________];] determined in accordance with [applicable] [_________] code.

      - Installed System: Conform to [UL] [WH] Design [________] for [ceiling and floor] [ceiling and roof] [_________] assembly.

************************************************************************************************************ IBC requires surface burning to be tested in accordance with ASTM E84 for individual materials or NFPA 286 for wall and ceiling assemblies.
*************************************************************************************************************

    - Surface Burning Characteristics: Maximum [25/450] [75/450] [200/450] flame spread/smoke developed index when tested in accordance with ASTM E84.

    - Surface Burning Characteristics: Comply with the following when tested in accordance with NFPA 286.

      - During 40 kW Exposure: No flame spread to ceiling.

      - During 160 kW Exposure: No flame spread to perimeter of tested sample and no flashover.

      - Total Smoke Release: Maximum 1,000 cu m.

************************************************************************************************************

Include following paragraph if a mock-up is required for approval of final acoustical ceiling design.
*************************************************************************************************************

    - [Mockups:  Build mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

      - Construct mock-up, 12 feet x 12 feet, including typical field and edge conditions.

      - Locate where indicated on Drawings.

      - Approved mockups may become part of the completed Work if undisturbed up to time of Substantial Completion.]

  - delivery, storage, and handling

    - Deliver acoustical panels, suspension-system components, and accessories to Project site in original, unopened packages and store them in a fully enclosed, conditioned space where they will be protected against damage from moisture, humidity, temperature extremes, direct sunlight, surface contamination, and other causes.

    - Before installing acoustical panels, permit them to reach room temperature and stabilized moisture content.

    - Handle acoustical panels carefully to avoid chipping edges or damaging units in any way.

  - SITE CONDITIONS

    - Install ceiling panels only after building is enclosed, sufficient heat is provided, dust generating activities have been finished, overhead work is completed, tested and approved, and interior wet work is dry.

    - Maintain uniform temperature of minimum 60 degrees F and a maximum humidity of 40 percent prior to, during, and after ceiling panel installation.

  - WARRANTY:  Provide manufacturer’s standard, all inclusive warranty.

- PRODUCTS

  - MANUFACTURERS:

      - [Armstrong World Industries Inc.], Model [________].

      - [CertainTeed], Model [_________].

      - [United States Gypsum Company], Model [________].

      - Chicago Metallic Corporation, Model [________].

      - [____________________] Model [________].

  - PERFORMANCE / DESIGN CRITERIA

    - Seismic Performance: Acoustical ceiling shall withstand the effects of earthquake motions determined according to [ASCE 7] and as designed and shown on the Drawings.

    - Surface-Burning Characteristics: Comply with ASTM E 84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

    - Fire-Resistance Ratings: Comply with ASTM E 119; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

      - Indicate design designations from UL’s “Fire Resistance Directory” or from the listings of another qualified testing agency.

  - acoustical panels, general

    - Low-Emitting Materials: Acoustical panel ceilings shall comply with the testing and product requirements of the California Department of Health Services’ “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers.”

    - Recycled Content:

      - Acoustical Panels:  Minimum 20% recycled content.

    - Glass-Fiber-Based Panels: Made with binder containing no urea formaldehyde.

************************************************************************************************************

Biobased acoustical panels are Designated Green Products for Federal Procurement by the EPA.  However biobased acoustical panels are currently a cost premium to industry standard mineral or glass fiber acoustical panels.  In addition use of biobased products in wet areas, clean rooms and/or laboratories should be used with caution.  Include following paragraph only if use of biobased product is cost effective and will not impact the environmental quality or programmatic requirements of the proposed usage.
*************************************************************************************************************

    - [Biobased Panels:  Minimum 37% biobased content.]

    - Acoustical Panel Standard: Provide manufacturer’s standard panels of configuration indicated that comply with ASTM E 1264 classifications as designated by types, patterns, acoustical ratings, and light reflectance unless otherwise indicated.

      - Mounting Method for Measuring NRC: Type E-400; plenum mounting in which face of test specimen is 15-3/4 inches away from test surface according to ASTM E 795.

    - Acoustical Panel Colors and Patterns: Match appearance characteristics indicated for each product type.

      - Where appearance characteristics of acoustical panels are indicated by referencing pattern designations in ASTM E 1264 and not manufacturer’s proprietary product designations, provide products selected by Architect from each manufacturer’s full range that comply with requirements indicated for type, pattern, color, light reflectance, acoustical performance, edge detail, and size.

  - acoustical TILES

    - Acoustic Tile: [ASTM E1264,] conforming to the following:

      - Size: 12 x 12 inches.

      - Thickness: [5/8] [_________] inches.

      - Composition: [Mineral] [_________].

      - Density: [________] lb/cu.ft.

******************************************************************************************** Comply with LANL ESM Chapter 7, Electrical Section D5020, Paragraph 7.1.B to obtain initial surface reflectance recommended in the IES Lighting Handbook of 90%.
********************************************************************************************

      - Light Reflectance: [________] percent.

      - NRC Range: [________] to [________].

      - STC Range: [________] to [________].

      - Joint: [Kerfed] [Rabbeted] [_________].

      - Edge: [Square] [Beveled].

      - Surface Color: [White] [________].

      - Surface Finish: [Perforated] [Non-directional fissured] [Directional fissured] [________], [plastic wrapped].

******** [AND / OR] ********

    - Acoustic Panels: [ASTM E1264,] conforming to the following:

      - Size: [12 x 24] [24 x 48] [24 x 24] [____x____] inches.

      - Thickness: [3/4] [5/8] [________].

      - Composition: [Mineral] [________________]

      - Density: [_______] lb/cu.ft.

******************************************************************************************** Comply with LANL ESM Chapter 7, Electrical Section D5020, Paragraph 7.1.B to obtain initial surface reflectance recommended in the IES Lighting Handbook of 90%.
********************************************************************************************

      - Light Reflectance: [________] percent.

      - NRC Range: [________] to [________].

      - STC Range: [________] to [________].

      - Edge: [Square.] [Rabbeted.] [________________]

      - Surface Color: [White] [________] color [as selected].

  - metal suspension systems, general

    - Recycled Content:

      - Steel:  Minimum 25% recycled content.

      - Aluminum: Minimum 50% recycled content.

    - Metal Suspension-System Standard: Provide manufacturer’s standard direct-hung metal suspension systems of types, structural classifications, and finishes indicated that comply with applicable requirements in ASTM C 635/C 635M.

      - High-Humidity Finish: Comply with ASTM C 635/C 635M requirements for “Coating Classification for Severe Environment Performance” where high-humidity finishes are indicated.

    - Attachment Devices

      - Comply with seismic design requirements as shown on drawings.

      - Comply with [Section 03 1512 Post-Installed Concrete Anchors Purchase- High Confidence] [Section 03 1534 Post Installed Concrete Anchors Purchase – Normal Confidence] and Section 03 1550 Post Installed Concrete Anchors; Installation and Testing.

    - Wire Hangers, Braces, and Ties: Provide wires complying with the following requirements:

      - Zinc-Coated, Carbon-Steel Wire: ASTM A 641/A 641M, Class 1 zinc coating, soft temper.

      - Stainless-Steel Wire: ASTM A 580/A 580M, Type 304, nonmagnetic.

      - Nickel-Copper-Alloy Wire: ASTM B 164, nickel-copper-alloy UNS No. N04400.

      - Size: Select wire diameter so its stress at three times hanger design load (ASTM C 635/C 635M, Table 1, “Direct Hung”) will be less than yield stress of wire, but provide not less than [0.106-inch] [0.135-inch] <Insert dimension> diameter wire.

    - [Hanger Rods] [Flat Hangers]: Mild steel, zinc coated or protected with rust-inhibitive paint.

    - Angle Hangers: Angles with legs not less than 7/8 inch wide; formed with 0.04-inch thick, galvanized-steel sheet complying with ASTM A 653/A 653A, G90 (Z275) coating designation; with bolted connections and 5/16-inch diameter bolts.

    - Seismic Stabilizer Bars: Manufacturer’s standard perimeter stabilizers designed to accommodate seismic forces as shown on drawings.

    - Seismic Struts: Manufacturer’s standard compression struts designed to accommodate seismic forces as shown on drawings.

    - Seismic Clips: Manufacturer’s standard seismic clips designed and spaced to secure acoustical panels in place.

    - Hold-Down Clips: Where indicated, provide manufacturer’s standard hold-down clips spaced 25 inches o.c. on all cross tees.

    - Impact Clips: Where indicated, provide manufacturer’s standard impact-clip system designed to absorb impact forces against acoustical panels.

  - metal suspension system

    - Non-fire Rated Grid: [ASTM C635, [light] [intermediate] [heavy] duty]; [exposed T] [exposed T/one direction] [concealed T and G] [concealed H and T] [paired access T] [downward access removable T] [concealed Z] [concealed T] [metal pan T] [________]; components die cut and interlocking.

******** [AND/OR] ********

    - Fire Rated Grid: [ASTM C635, [light] [intermediate] [heavy] duty], listed by UL for use in [________] hour assembly, [two directional concealed] [exposed T] [exposed T/one direction] [________]; components die cut and interlocking.

*************************************************************************************
Only steel grid material can be used in fire rated systems.
*************************************************************************************

    - Grid Materials: [Commercial quality cold rolled steel with galvanized coating.] [Cold rolled aluminum.] [Extruded aluminum.] [________].

    - Exposed Grid Surface Width: [15/16] [9/16] [________] inch [with reveal].

    - Grid Finish: [White] [Anodized] [________].] [[________] color [as selected].]

    - Accessories: [Stabilizer bars,] [clips,] [splices,] [perimeter moldings,] [hold down clips,] and [_______] required for suspended grid system.

    - Support Channels and Hangers: [Galvanized] [Primed] steel; size and type to suit application, seismic requirements, and ceiling system flatness requirement specified.

  - accessories

***************************************************************************************************
Acoustic batt insulation placed over acoustic suspension ceiling systems may absorb moisture over time and induce loads or collapse ceiling systems.  Use with caution
***************************************************************************************************

    - [Acoustic Batt Insulation: Specified in Section 07 2100.]

    - [Gypsum Board: Fire rated type; [5/8] [________] inch thick, ends and edges square, paper faced.]

    - Acoustic Sealant For Perimeter Moldings: Specified in Section 07 9200.

***** [OR] *****

    - Gasket for Perimeter Moldings: [Closed cell rubber sponge tape.] [________________.]

*******************************************************************************************

Touch-up paint is required when field cutting and exposing edges of tegular acoustic units.
*******************************************************************************************

    - Touch-up Paint: Type and color to match acoustic and grid units.

- EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, including structural framing to which acoustical panel ceilings attach or abut, with Installer present, for compliance with requirements specified in this and other Sections that affect ceiling installation and anchorage and with requirements for installation tolerances and other conditions affecting performance of acoustical panel ceilings.

Examine acoustical panels before installation. Reject acoustical panels that are wet, moisture damaged, or mold damaged.

Verify layout of hangers will not interfere with other work.

Proceed with installation only after unsatisfactory conditions have been corrected.

DEMOLITION

************************************************************************************************************* Use this article for demolition work of limited scope. For major or complicated demolition, consider specifying demolition in Section 02 4119 Selective Structure Demolition only.

Carefully coordinate work specified in this article to avoid duplication in other sections. 
*************************************************************************************************************

Extend existing acoustical ceiling installations using materials and methods as specified.

Clean and repair existing acoustical ceilings which remain or are to be reinstalled.

Ceiling tile removal.

Verify with LANL STR that asbestos and radiological surveys have been completed and the results allow free release.

Remove ceiling tiles and separate clean (untreated, unpainted, and uncontaminated with water, adhesives, oils, solvents, mastics, and like products) ceiling tile for recycling. Coordinate potential LANL reuse with LANL STR.

Stack clean ceiling tiles on pallets for handling.

Store clean ceiling tiles off ground and under cover to prevent contamination of materials by water, freezing, foreign matter or other causes.

preparation

Measure each ceiling area and establish layout of acoustical panels to balance border widths at opposite edges of each ceiling. Avoid using less-than-half-width panels at borders, and comply with layout shown on reflected ceiling plans.

Installation

General: Install acoustical panel ceilings to comply with ASTM C 636/C636M and seismic design requirements indicated, according to manufacturer’s written instructions and CISCA’s “Ceiling Systems Handbook.”

Fire-Rated Assembly: Install fire-rated ceiling systems according to tested fire-rated design.

************************************************************************************************************* Select and edit one of the following two paragraphs for lay-in or concealed grid.
*************************************************************************************************************

[Lay-In Grid Suspension System:

Install suspension system in accordance with ASTM C635, ASTM C636 and as supplemented in this section.

************************************************************************************************************ The following paragraph is required for ceiling systems subject to seismic loading. 
************************************************************************************************************

Install system in accordance with the Contract Drawings and ASTM E580/E580M.

Install system capable of supporting imposed loads of deflection of [1/360] [1/240] [_________] maximum.

************************************************************************************************************* Include first paragraph below when reflected ceiling plan is not included with drawings; or subsequent paragraph when reflected ceiling plan is included.
*************************************************************************************************************

[Lay out system to balanced grid design with edge units no less than 50 percent of acoustic unit size. Arrange system with long dimension of tile [parallel] [perpendicular] to long dimension of the space.]

***** [OR] *****

[Locate system on room axis according to reflected ceiling plan.]

Install after major above ceiling work in complete. Coordinate location of hangers with other work.

************************************************************************************************************* Certain metal deck types are fabricated to accommodate ceiling hanger tabs. When tabs are not provided, include following paragraph.
*************************************************************************************************************

[Install hanger clips during steel deck erection. Install additional hangers and inserts as required.]

Hang suspension system independent of walls, columns, ducts, pipes and conduit. Where carrying members are spliced, avoid visible displacement of face plane of adjacent members.

Where ducts or other equipment prevent regular spacing of hangers, reinforce nearest affected hangers [and related carrying channels] to span extra distance.

Do not support components on main runners or cross runners when weight causes total dead load to exceed deflection capability. [Support fixture loads by supplementary hangers located within [6] [<insert number>] inches of each corner; or support components independently.]

Do not eccentrically load system, or produce rotation of runners.

Perimeter Molding:

Install edge molding at intersection of ceiling and vertical surfaces [into bed of acoustic sealant] [with continuous gasket].

Use longest practical lengths.

[Miter] [Overlap [and rivet]] corners.

Install at junctions with other interruptions.

Form expansion joints [as detailed] [________]. Form to accommodate plus or minus [1] [<insert number>] inch movement. Maintain visual closure.

************************************************************************************************************ UL requirements for fire rated ceilings may necessitate constructing gypsum board boxes over ceiling light fixtures to ensure continuity of fire resistance at suspension system level. Refer to assembly requirements.
*************************************************************************************************************

[Install light fixture boxes constructed of [gypsum board] [acoustic panel] above light fixtures in accordance with UL assembly requirements and light fixture ventilation requirements.]

***** [OR] ******

[Concealed Grid Suspension System:

Install suspension system in accordance with ASTM C635, ASTM C636 and as supplemented in this section.

************************************************************************************************************* The following paragraph is required for ceiling systems subject to seismic loading.
*************************************************************************************************************

[Install system in accordance with the Contract Drawings and ASTM E580/E580M.]

Install system capable of supporting imposed loads of deflection of [1:360] [1:240] [________] maximum.

************************************************************************************************************* Include first paragraph below when reflected ceiling plan is not included with drawings; or subsequent paragraph when reflected ceiling plan is included.
*************************************************************************************************************

Lay out system to balanced grid design with edge units no less than 50 percent of acoustic unit size.]

***** [OR] ******

[Locate system on room axis according to reflected ceiling plan.]

Install after major above ceiling work in complete. Coordinate location of hangers with other work.

************************************************************************************************************ Certain metal deck types are fabricated to accommodate ceiling hanger tabs. When tabs are not provided, include following paragraph.
*************************************************************************************************************

[Install hanger clips during steel deck erection. Install additional hangers and inserts as required.]

Hang suspension system independent of walls, columns, ducts, pipes and conduit. Where carrying members are spliced, avoid visible displacement of face plane of adjacent members.

Where ducts or other equipment prevent regular spacing of hangers, reinforce nearest affected hangers [and related carrying channels] to span extra distance.

Do not support components on main runners or cross runners when weight causes total dead load to exceed deflection capability. Support fixture loads by supplementary hangers located within [6] [________] inches of each corner; or support components independently.

Do not eccentrically load system, or produce rotation of runners.

Perimeter Molding:

Install [concealed] edge molding at intersection of ceiling and vertical surfaces [into bed of acoustic sealant] [with continuous gasket].

Use longest practical lengths.

[Miter] [Overlap [and rivet]] corners.

Install [concealed] at junctions with other interruptions.

Form expansion joints [as detailed] [________]. Form to accommodate plus or minus [1] [<insert number>] inch movement. Maintain visual closure.]

Acoustic Units:

Fit acoustic units in place, free from damaged edges or other defects detrimental to appearance and function.

Lay directional patterned units [one way with pattern parallel to [longest] [shortest] room axis] [in basket weave pattern]. Fit border trim neatly against abutting surfaces.

Install units after above ceiling work is complete.

Install acoustic units level, in uniform plane, and free from twist, warp, and dents.

Cutting Acoustic Units:

Cut to fit irregular grid and perimeter edge trim.

Cut [square reveal] [bevel] edges to field cut units.

[Double cut and field paint exposed edges of tegular units.]

Where [bullnose concrete block corners] [round obstructions] occur, install preformed closures to match perimeter molding.

************************************************************************************************************* Include the following paragraph when acoustic insulation is required above suspended ceiling system and adjacent to acoustic partitions. Coordinate with partition section. 
*************************************************************************************************************

[Lay acoustic insulation for distance of [48] [<insert number>] inches on both sides of acoustic partitions [as indicated on Drawings].]

************************************************************************************************************* Include the following paragraph for fire rated ceiling assemblies; most UL assemblies require hold-down clips throughout system. This paragraph may be waived when acoustic units are in excess of 1 lb/sq.ft, depending on UL rating.
*************************************************************************************************************

Install hold-down clips to retain panels tight to grid system [within [20] [<insert number>] ft of exterior door] [________].]

erection tolerances

************************************************************************************************************* Coordinate this article with suspension system members selected and performance statements indicated.
*************************************************************************************************************

Maximum Variation from Flat and Level Surface: [1/8] [________] inch in 10 feet.

Maximum Variation from Plumb of Grid Members Caused by Eccentric Loads: [2] [________] degrees.

field quality control

Special Inspections: [LANL will engage] [Engage] a qualified special inspector to perform the following special inspections:

Compliance of seismic design.

Testing Agency: [LANL will engage] [Engage] a qualified testing agency to perform tests and inspections and prepare test reports.

Perform the following tests and inspections of completed installations of acoustical panel ceiling hangers and anchors and fasteners in successive stages. Do not proceed with installations of acoustical panel ceiling hangers for the next area until test results for previously completed installations show compliance with requirements.

Extent of Each Test Area: When installation of ceiling suspension systems on each floor has reached 20 percent completion but no panels have been installed.

Within each test area, testing agency will select one of every 10 power-actuated fasteners and postinstalled anchors used to attach hangers to concrete and will test them for 200 lbf of tension; it will also select one of every two postinstalled anchors used to attach bracing wires to concrete and will test them for 440 lbf of tension.

When testing discovers fasteners and anchors that do not comply with requirements, testing agency will test those anchors not previously tested until 20 pass consecutively and then will resume initial testing frequency.

Acoustical panel ceiling hangers and anchors and fasteners will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

cleaning

Clean exposed surfaces of acoustical panel ceilings, including trim, edge moldings, and suspension-system members. Comply with manufacturer’s written instructions for cleaning and touchup of minor finish damage. Remove and replace ceiling components that cannot be successfully cleaned and repaired to permanently eliminate evidence of damage.

END OF SECTION

*************************************************************

Do not delete the following reference information:

*************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 09 5100 Rev. 2, dated July 23, 2012.