SECTION 22 0813

TESTING PIPING SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

In Word file, select Tools-Options-View and select Hidden Text to see blue specifiers notes.

In Word 2007, click Office button on the top left hand corner, click Word Options, and on Display tab check the box for Hidden Text.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Pressure testing [and holiday testing] of the following systems:

Fire protection piping

Plumbing piping (sewer lines, water lines, rainwater lines)

Natural gas piping

Compressed air piping

Instrument air piping

Hydronic piping

Steam and condensate piping

Steam and condensate steel pre-insulated conduit system

Refrigerant piping

Vacuum piping

Hazardous waste and vent double wall containment piping (gravity system)

Laboratory gas piping

Holiday testing (buried coated steel piping)

SUBCONTRACTOR REQUIREMENTS

Notify LANL Subcontract Technical Representative (STR) at least 24 hours (1 working day) in advance to arrange for witnessing of the piping test.

For discharge requirements of water used for pressure testing comply with Section 01 3545, Water Discharge Requirements.

Notify STR immediately in the event of any accidental discharge.

SUBMITTALS

Submit the following in accordance with Section 01 3300, Submittal Procedures:

Pneumatic test plan for approval that includes:

Material of construction

Design pressure

Test pressure and duration of test

Test medium and method of achieving the test pressure

Certification on calibration of pressure gauges

Method to exclude personnel from the area containing the system to be tested.

Over pressurization protection/prevention: Device make/model number, certification, pressure relief set point, point of installation in system.

Test Reports: Submit test results within 10 working days of successful test.

PRODUCTS

  - MATERIALS

Furnish instruments, equipment, material and labor necessary to conduct tests.

Calibrate testing equipment at reasonable intervals with devices of accuracy traceable to National Institute of Standards and Technology (NIST).

Test gauges used in conducting test shall be in accordance with IAPMO UPC.

EXECUTION

  - FIELD QUALITY CONTROL

Piping being tested shall remain exposed until LANL has approved the piping test results.

Trenches may be backfilled between joints before testing to prevent movement of pipe during testing.  Ensure that thrust blocks are sufficiently hardened before testing.

Piping being tested shall not leak nor show any loss in test pressure for duration specified unless otherwise noted.

Where portion of piping system is to be concealed before completion, the portion shall be tested separately as specified for the entire system.

Ensure piping supports are in place.

Isolate system gages, sensors, etc., from pressure tests so instruments and devices are not damaged.  Test pressure shall not exceed the maximum allowable test pressure for any vessel, pump, valves, or other component in the system.

Hydrostatic (Water) Testing:

Use potable water as test medium.  Do not fill system until the LANL STR has approved the source of water supply.

Provide vents at high points to release trapped air while filling system.

Provide drains at low points for complete removal of test liquid.

Drain system if there is a potential for freezing, i.e., no heat in building, coil in outside air stream, or other similar situations.

Pneumatic (Air) Testing:

Use clean dry air (Excluded from use with natural gas pipe testing) or inert gas as the test medium.

Barricade the area around the system to be tested.

Prior to application of full air test pressure, apply a preliminary test of not more than 10 psig to reveal possible major leaks.

After preliminary test, raise pressure in stages not more than 25 percent up to full test pressure, allowing at least 10 minutes for equalization of strain and detection of major leaks at each intermediate stage.  Hold final test pressure for time specified.

Examine piping for leakage using soap bubble solution, or by test gage monitoring.

If leaks are found, they shall be eliminated by tightening, repair, or replacement, as appropriate and test repeated until no leakage is found.

PRESSURE TESTING

Fire Protection Piping:

Below Grade: Test with water at 200 psig for 2 hours. Piping shall maintain test pressure +/- 5 psi for the duration of the test and there shall be no visible signs of leakage per NFPA 24.

Above Grade: Test with water at 200 psig for 2 hours and shall maintain that pressure without loss per NFPA 13.

Plumbing Piping:

Sanitary Waste and Vent Piping Within Building to Building Wall, including condensate drain line from cooling coils:

Test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 1 hour.

Note: This alternative method may not be used for plastic piping,

For modifications to existing plug the outlet of the drain piping, and fill pipe with water to the point of overflow. After 15 minutes, check piping for leaks. No loss of water from the piping for the duration of the test indicates that the system meets the requirements of the project. (Per UPC)

Sanitary Sewer Piping Beyond Building Wall (other than Force Main): Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

For partial system tests, test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 1 hour

Note: This alternative testing method may not be used for plastic piping.

Sanitary Sewer Force Main: Test with water at [    ] psig for 4 hour.

*************************************************************************************************************

Test force main piping to 1.5 times operating pressure, 25 psig minimum.

*************************************************************************************************************

Potable Water Inside Building to Site Main: Test with water at [    ] psig for 4 hour.

*************************************************************************************************************

Test potable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Nonpotable Water: Test with water at [    ] psig for 4 hour.

*************************************************************************************************************

Test nonpotable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Rainwater Piping:

Rainwater Piping Inside Building to 5 Feet Outside Building: Test with water in accordance with the IAPMO UPC.  Fill the entire system with water to the point of overflowing.  Keep water in system for at least 1 hour before inspection starts.  If the system is tested in sections, no piping (except the uppermost 10 foot of the system) shall have been submitted to a test of less than 10 foot head of water.  Acceptable Alternate:  Test with air at 5 psig and hold pressure for at least 1 hour.

Note: pneumatic testing may not be used for plastic piping.

Rainwater Piping Beyond 5 feet of Building: Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

Natural Gas Piping From Mel Smithour email 1/24/08: 
(1) NFPA 54 governs gas systems not exceeding 5 psi reference NFPA 54 Section 5.5 and is limited to systems from point of delivery to the appliance connection NFPA 54 Section 1.1.1.  The POD is outlet of service meter or outlet of service regulator. Thus covered by 22 0813, Part C.1., the psi and time are allowable and approved by the SME.

(2) 49 CFR 192 governs the Transportation of Natural and Other Gas by Pipeline. The LANL system is a nominal 88 psi with some areas at 60 psi and 20 psi and the MAOP is 100 psi. The lower pressure systems could be upgraded to the 88 psi if needed and to meet the requirements of LANL mission, 49 CFR and the MAOP the psi and time are thus covered appropriately by 22 0813 Part C.2. and approved by the SME

Operating Pressure to 5 psig: Test with air or inert gas at 60 psig for 8 hours

Operating Pressure Greater than 5 psig to 100 psig: Test with inert gas at 160 psig for 24 hour.  Bring pressure to 160 psig and equalize to ambient temperature before starting pressure test; repressure as necessary to attain 160 psig.  Record test with a continuous (24 hour) calibrated pressure recording chart calibrated and certified per LANL requirements prior [From Mel Smithour email 1/24/08 regarding previous verbiage: (1) Not sure what the reference is in the first sentence about the dead-weight cal. The type of recording chart has always been in the gas test Part for the higher pressure, Part C.2, and a calibration method is dead weighted. If there is confusion in Part C.2 third sentence the "dead weighted" could/should be deleted. (2) The last revised Spec. Part C.2 has an addition for 30 day prior-to-use calibration.  The unit is calibrated on a yearly basis.  From what was found a monthly calibration schedule for this type of unit is not required by the LANL Calibration Program.  What is the justification for the 30 day calibration requirement?] to each pressure test.  Recorded pressure line shall be continuous, even and virtually “straight” without abrupt glitches, jogs or changes.  Pressure line shall return to its starting position pressure at end of 24 hour period.

Compressed Air: Test with air at [    ] psig for 4 hours.

If using soap bubble solution for detecting leaks, hold pressure for a minimum of 10 minutes prior to applying soap bubble solution.

*************************************************************************************************************

Test compressed air piping to 1.25 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Instrument Air: Test with air at [    ] psig for 4 hours.

If using soap bubble solution for detecting leaks, hold pressure for a minimum of 10 minutes prior to applying soap bubble solution.

*************************************************************************************************************

Test instrument air to 1.25 times operating pressure, 50 psig minimum.

*************************************************************************************************************

Hydronic Piping (heating hot water, chilled water, tower water, condenser water, make-up water and equipment drains): Test with water at [   ] psig for 4 hours

*************************************************************************************************************

Test hydronic piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

1.    For modifications to existing piping bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project. Per ASME 31.9, paragraph 937.5.

Steam and Condensate Service Piping: Test with water at [    ] psig for 4 hours.

*************************************************************************************************************

Test steam and condensate service piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Steam and Condensate Distribution Piping Systems:In part H. the steam and condensate distribution system and pressure test are covered by ASME B31.1. The steam system has a normal OP of 100 psi and in winter can be 110-115 psi.  The design pressure is 150 psi and being the steam and condensate are tied at numerous points and are sometimes tested together. Also during the review of B31.1 the parameter for the test in the design pressure not operation pressure at this time.  Please change Part H.1 from “150 psig” to “180 psig” which is the minimum test pressure per B31.1, Part 137.5.

Distribution Piping: Test with air or inert gas at 180 psig minimum for 4 hours This would be the appropriate pressure if the distribution piping design pressure is 120 psig.  If the design pressure is different, this test pressure should be adjusted.

Pre-insulated Conduit Systems: Outer steel casing, test with air at 15 psig for 4 hours or as otherwise specified in manufacture’s written instructions.

Refrigerant Piping:

Test in accordance with the Uniform Mechanical Code (IAPMO UMC).

Pressure test with dry nitrogen mixed with a trace of halocarbon (HCFC-22) gas for 24 hours.  Test the high and low side of each system at not less than the lower of the pressure noted in the IAPMO UMC or the pressure relief valve.  Record test with a pressure-recording chart and check system with an electronic halogen leak detector or ultrasonic leak detector.

Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

40 CFR 82.156 (b)(I)(B) prohibits use of refrigerants for leak testing.  It does allow the use of trace quantities of HCFC-22 as a tracer gas.

After successful completion of nitrogen test, remove pressurization gas and evacuate system to 1 mm Hg. (1Torr or 1000 microns) or less to remove moisture and non-condensables.  After 30 minutes, if the vacuum level has not risen higher than 2.5 mm Hg. (2.5 Torr or 2500 microns), the leak rate is acceptable.  Check system with an electronic manometer or thermocouple gauge.

After successful completion of vacuum test, charge piping with system refrigerant.  If start up is not within 24 hour, temporarily pressurize to 5 psig with system refrigerant.

Provide a dated test report to the STR for systems containing 50 pounds or more of refrigerant.  Include in report the name and number designation of refrigerant used and the field pressure test applied to the high and low side of the system.  The installer shall sign the test report.

Vacuum Piping: Evacuate to 1mm Hg. (1 Torr or 1000 microns) measured with an electronic manometer or thermocouple gauge.  After 2 hours, if vacuum level has risen to no higher than 2.5 mm Hg. (2.5 Torr or 2500 microns), the leak test is acceptable.

Hazardous Waste and Vent Double Wall Containment Piping - Gravity System:

Inner Pipe and Vent: Test with air at 5 psig for 4 hours or as otherwise specified in manufacturer’s written instructions.

Outer Pipe: Test with air at 5 psig for 4 hours or as otherwise specified in manufacturer’s written instructions.

Laboratory Gas Piping:

Test [           ] piping with cylinder nitrogen at [    ] psig for 24 hours.

************************************************************************************************************

Test laboratory gas piping to 1.25 times operating pressure, 50 psig minimum.

*************************************************************************************************************

      - After test has been satisfactorily completed, temporarily reduce pressure to 5 psig with system nitrogen.

Testing for Holidays:

Test the following buried coated steel piping systems for holidays:

Natural gas.

[List other piping systems].

Perform holiday test in accordance with the following procedure:

After pipe has been welded, joints wrapped, and pipe is ready for lowering into trench, test coating for flaws (holidays). Test coated piping system throughout its length for flaws in coating system by means of a high-potential flaw detector that can impress a maximum of 8,000 volts across coating.  One electrode of tester shall maintain complete circumferential contact with coating while transversing entire length of coating system and other electrode shall be the underlying metal pipe.  An electrical discharge through coating detected visually or by instrument, shall constitute failure of this test.

Actual working voltage of detector on pipe will depend upon thickness of coating and size of pipe.  A thin coating on a large pipe will offer a capacitive load to the detector that will drop the working voltage several thousand volts below the "no-load" voltage.  Detector output may also have to be increased to overcome conditions such as extremely dry rock, or sandy soil.

Important!  Do not cut ground cable to a shorter length.  The length supplied is important to proper operation of the detector.  Keep as much of the cable as possible in contact with the earth.  Straighten out kinks where possible and do not let it ride up over skids.  In dry areas it will help to drag the cable in the ditch where there is more moisture.  The pipe should be grounded.

Mark holidays as they are found and repair prior to lowering pipe into trench.  Repair holidays in factory coating by removing initial coating and undercoating for a minimum of 4 inches on each side of holiday.  Remove coating around holiday and feather edge to pipe wall for sufficient distance to make a satisfactory repair.  Apply primer (Polyken 1027) to the holiday to form a bond over the entire surface of the holiday and then spirally wrap pipe with a double layer of half-lapped 35 mil polyethylene tape (Polyken 934) for a minimum of 2 inches on each side of the holiday.

Repair holidays in joint wrappings by removing field applied coating in area of holiday and rewrapping.  LANL STR or designated representative will approve all areas of joint coating.

RETESTING

If piping does not pass test, locate and repair leaks and repeat testing procedure until satisfactory results are obtained.

Make repairs to piping with new materials.  Caulking on screwed joints, cracks, or holes is not acceptable.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0813 Rev. 2, dated March 7, 2008.