SECTION 22 4200

PLUMBING FIXTURES

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specific requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  This specification template is tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM). To seek a variance from requirements of the ESM that are applicable, contact the ESM Mechanical POC. Contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections. *************************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Water closets

Urinals

Lavatories

Sinks

Showers

Electric water coolers

Service sinks

Emergency showers

Emergency Eye and Face Wash

Emergency Combination Shower with Eye and Face Wash

Tepid Water Blending System

RELATED SECTIONS

10 2800, Toilet & Bath Accessories (e.g., lavatory piping guards)

ACTION SUBMITTALS

Product Data: Submit catalog illustrations of fixtures, sizes, [rough-in dimensions], utility sizes, trim, and finishes.

Manufacturer's Installation Instructions: Submit installation methods and procedures.

Manufacturer's Certificate: Certify products meet or exceed specified requirements (e.g., flow test for [      ] gallons or gpm).

CLOSEOUT SUBMITTALS

Submit in accordance with Section 01 7700, Closeout Procedures.

Operation and Maintenance Data: Submit fixture, trim, exploded view and replacement parts lists. See Section 01 7823, Operation and Maintenance Data.

QUALITY ASSURANCE

Provide products requiring electrical connections listed and classified by a nationally recognized testing laboratory (e.g., Underwriters Laboratories Inc.) as suitable for purpose specific and indicated.

Provide ADA-compliant products.

Provide water conserving fixtures and fittings complying with the Uniform Plumbing Code or exceeding UPC where noted.

Comply with ADA/ABA Accessibility Guidelines dated 9/15/10 for mounting heights and locations of Plumbing Fixtures

PRODUCTS

*************************************************************************************************************

Coordinate plumbing fixture selections with the architect regarding casework, handicapped approach, ADA requirements if applicable.

*************************************************************************************************************

FLUSH VALVE WATER CLOSETS

*************************************************************************************************************

Low voltage flushometers (24Vac) may be used in new construction. Consult with the FOD.

*************************************************************************************************************

Wall Hung Bowl: ASME A112.19.2; white, wall hung, vitreous china closet bowl, with elongated rim, 1-1/2 inch top spud, china bolt caps.

Manufacturer: Kohler, Model K-4325-0, Kingston.

Floor Mounted Bowl: ASME A112.19.2; white, floor mounted, vitreous china closet bowl with elongated rim.

Manufacturer: Kohler, Model K-96053-0, Wellcomme Ultra

Sensor-Operated Flush Valve: ASME A112.18.1, concealed, diaphragm type with battery operated solenoid operator, infrared sensor and over-ride button in chrome plated plate, wheel handle stop and vacuum breaker; maximum [1.28 gpf, wall mount] [1.6 gpf , floor mount] gallon flush volume.

Manufacturer: Sloan, Model 8111–[1.28, wall mount bowl] [1.6, floor mount bowl], G2 Optima Plus.

Seat: ANSI Z124.5, Solid white plastic, elongated open-front, self-sustaining hinge, stainless steel hardware, without cover.

Manufacturer: Kohler, Model K-4670-C.

Wall Mounted Carrier: ASME A112.6.1M; adjustable cast iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers. [wall hung bowl only]

FLUSH TANK WATER CLOSETS

**************************************************************************************************** 
Use floor-mounted flush tank water closets only in existing facilities when replacing fixtures of this type. ****************************************************************************************************

Pressure Light Toilet: ASME A112.19.2; white, floor mounted, vitreous china closet bowl, with elongated rim. Pressure flush, 1.6 gpf.

Manufacturer: Kohler, Model K-3505-TR, Wellworth.  Includes:

Toilet Bowl : Kohler, Model K-4303

Toilet Tank: Kohler, Model K-4645-TR

Tank cover, trip lever, tank accessory pack, bolt cap accessory pack

Elongated Seat: Solid white propylene plastic, elongated open-front, stainless steel hinge arms and hardware, without cover.

Manufacturer: Kohler, Model K-4731-C, Stronghold.

Angle Supply with Stop (single)

Manufacturer: Kohler, Model K-7637-CP.

WALL-HUNG URINALS

*************************************************************************************************************

Low voltage flushometers (24Vac) may be used in new construction. Consult with the FOD.

*************************************************************************************************************

Urinal: ASME A112.19.2; vitreous china, wall hung, washout urinal with shields, integral trap, removable stainless steel strainer, and 3/4 inch top spud, steel supporting hanger. Urinal shall use 0.125 gallon per flush.

Manufacturer: Kohler, Model K-4991-ET, Bardon.

Sensor Operated Flush Valve: ASME A112.18.1; exposed chrome plated, diaphragm type with battery operated solenoid operator, infrared sensor and over-ride button in chrome plated plate; maximum 0.125 gallon flush volume.

Manufacturer: Sloan, Model 8186-0.125, Optima Plus.

LAVATORIES

************************************************************************************************************

Low voltage faucets (24Vac) may be used in new construction. Consult with the FOD.

*************************************************************************************************************

Vitreous China Wall Hung Lavatory: ASME A112.19.2; vitreous china wall mount lavatory, with 4 inch high back, 21 x 18 inches with drillings on 4 inch centers, rectangular basin with splash lip and front overflow.

Manufacturer: Kohler, Model K-2005 (4 inch centers), Kingston.

****** [OR] ******

Vitreous China Countertop Lavatory: ASME A112.19.2; vitreous china self-rimming countertop lavatory, 20 1/4 x 17 1/2 inches with drillings on 4 inch centers, front overflow, seal of putty, caulking, or concealed vinyl gasket.

Manufacturer: Kohler, Model K-2196-4, Pennington.

******************************************************************************************** Metered faucets are not suitable for use with electric, tankless water heaters. Coordinate with water heater specification

********************************************************************************************

Metered Faucet: ASME A112.18.1; chrome-plated, metered mixing faucet, maximum  0.25 gallons per use, 30 second automatic shut off, battery-operated solenoid operator and infrared sensor, aerator, trim plate, open grid strainer, back check for hot and cold supply, and thermostatic mixing valve.

Manufacturer: Sloan, Model EBF-85-A, Optima Plus.

Accessories:

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon.

Chrome plated rigid supplies to fixtures with chrome plated brass [loose key] [screwdriver] [wheel handle] stops, reducers, and escutcheons.

Offset waste with perforated open strainer.

Trap and waste insulated and offset to meet ADA compliance.

Wall Mounted Carrier: ASME A112.6.1M; cast iron and steel frame with tubular legs, lugs for floor and wall attachment, concealed arm supports, bearing plate and studs.

SINKS

## *************************************************************************************************************

The following are example specifications of different types of sinks. Edit accordingly to suit project.

*************************************************************************************************************

Single Compartment Bowl: ASME A112.19.3, Commercial Grade, [____x____x____] inch outside dimensions, 18 gage, Type 304 stainless steel. Self-rimming and undercoated, with 1-1/2 inch chrome brass drain, 3-1/2 inch crumb cup and chrome brass tailpiece, ledge back drilled for trim.

Manufacturer: Elkay, Model [            ]

****** [OR] ******

Double Compartment Bowl: ASME A112.19.3, Commercial Grade, [____x____x____] inch outside dimensions 18 gage, Type 304 stainless steel. Self-rimming and undercoated, with 1-1/2 inch chrome brass drain, 3-1/2 inch crumb cups and chrome brass tailpiece, ledge back drilled for trim.

Manufacturer: Elkay, Model [            ]

****** [OR] ******

Enameled Bowl: ASME A112.19.1, white, cast iron, porcelain enameled double (equal) compartment, 32 x 22 inch outside dimensions, self-rimming and undercoated, with 4 hole faucet drilling, 3-1/2 inch diameter crumb cup, chrome brass tailpiece, and ledge back drilled for.

Manufacturer: Kohler, Model 5942-4, Brookfield.

Faucet: ASME A112.18.1; chrome plated brass supply with swing spout, aerator with maximum 2.0 gpm flow, indexed lever handles.

Manufacturer: Kohler, K-7304-K, Triton.

Accessories:

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon. Kohler Model K-8998

Chrome plated rigid supplies to fixtures with chrome plated brass [loose key] [screwdriver] [wheel handle] stops, reducers, and escutcheons. Kohler Model K-7605

SHOWERS

Wheelchair Accessible Cabinet: ANSI Z124.2; reinforced glass fiber, [36 x 36 x 80 inch] high, soap dish, integral seat [left hand] [right hand], grab bars, removable chrome plated strainer, tail piece, [________] color [as selected].

Manufacturer: Florestone, Model [3PC-44-52H]

Regular Cabinet: ANSI Z124.2 reinforced glass fiber, 36 x 37-1/2 x 73 inch high, removable chrome plated strainer, tailpiece, [white] color [as selected].

Manufacturer: Florestone, Model 36-3Wtb (36 x 37 inch)

Shower Valve: Concealed shower supply, pressure balanced, anti-scald, brass body, with single lever handle, ceramic disc cartridge, integral stops, bent shower arm with flow control and adjustable spray ball joint showerhead with maximum 2.0 gpm flow, and escutcheon.

Manufacturer: Delta Monitor T-17230.

Shower Valve: Concealed shower supply, pressure balanced, anti-scald, brass body, with single lever handle, ceramic disc cartridge, integral stops, with flow control and adjustable spray ball joint showerhead with maximum 2.0 gpm flow, and escutcheon, hand held shower, 70 inch metal-clad shower hose and 24 inch slide bar, female inlet and vacuum breakers.

Manufacturer: Delta Monitor T-17230 with Delta Model 53001-DS Slide bar/Grab bar.

ELECTRIC WATER COOLERS

Water Cooler:

### *************************************************************************************************************

Other vinyl cabinet colors are available at no extra cost. Stainless steel units are available at an extra charge.

Elkay coolers shown are GreenSpec-designated; EPA Comprehensive Procurement Guidelines do not indicate electrical water coolers are to be Energy Star.

*************************************************************************************************************

Lead-free materials, handicapped wall mounted electric water cooler with stainless steel top and stainless steel cabinet, elevated anti-squirt bubbler with stream guard, bottle filler, automatic stream regulator, mounting bracket, energy efficient cooling system.

Capacity: 8 gph of 50 degrees F water, based upon 80 degrees F inlet water and 90 degrees F ambient.

UL listed in accordance with ANSI/NSF 61 Section 9.

Electrical: Provide with electric cord and 3 prong rubber plug.

Manufacturer: Elkay, Model EZSG8WSLK (High Efficiency Single Station)

Manufacturer: Elkay, Model EZSTL8WSLK (High Efficiency Dual Station)

Accessories:

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon.

Chrome plated rigid supplies to fixtures with chrome plated brass [loose keys] [screwdriver] [wheel handle] stops, reducers, and escutcheons.

Wall Carrier: Elkay Model [MLP100, single station] [MLP200, dual station].

SERVICE SINKS

Bowl: ASME A112.19.1; 22 x 18 x 12 inch deep, white porcelain enameled (inside only) cast iron roll-rim sink, with 12 inch high back, concealed hanger, chrome plated strainer, stainless steel rim guard, cast iron [2] [3] inch P-trap with adjustable floor flange.

Manufacturer: Kohler, K-6714, Bannon, Service Sink, [K-6672, 2 inch P-Trap] [K-6673, 3 inch P-Trap].

****** [OR] ******

Bowl: [36 x 24 x 10 inch] [24 x 24 x 10 inch] high [white] [________] molded stone, floor-mounted, with one-inch-wide shoulders, [vinyl bumper guard,] stainless steel strainer.

Manufacturer: Fiat, Model [MSB-3624] [MSB-2424].

Trim: ASME A112.18.1 exposed wall-type supply with cross handles, spout wall brace, vacuum breaker, hose-end spout, strainers, integral screwdriver stops with covering caps and adjustable threaded wall flanges.

Manufacturer: Fiat, Model 830-AA

Accessories:

5 feet of 1/2 inch diameter plain end reinforced rubber hose, and bracket.

Manufacturer: Fiat, Model 832-AA.

Mop hanger, Manufacturer: Fiat, Model 889-CC.

EMERGENCY SHOWER

## *************************************************************************************************************

Refer to Mechanical Standard Drawing ST-D2010-1 for emergency equipment details. The following are example specifications for emergency equipment. Edit accordingly to suit project. Consult with manufacturer when equipment requires freeze, corrosion or UV protection. Refer to manufacturers installation details for piping tie-in details.

*************************************************************************************************************

ANSI Z358.1; [wall-mounted] [free standing], self cleaning, non-clogging 8 inch diameter [stainless steel] [plastic] drench shower head with elbow, [1 inch] [1-1/4 inch] IPS supply, instant action stay open valve actuated by rigid stainless steel pull rod. Furnish universal emergency sign.

Manufacturer: Haws, 8100 Series.

EMERGENCY EYE AND FACE WASH

ANSI Z358.1; [wall-mounted] [pedestal mounted], [stainless steel bowl] [plastic bowl], [1 inch] [1-1/4 inch] IPS supply, instant action stay open valve actuated by [push flag] [foot pedal] [push flag or foot pedal], twin spray heads [with face spray ring], [dust cover assembly,] [wall mount bracket,] and tailpiece and chrome-plated brass P-trap. Furnish universal emergency sign.

Manufacturer: Haws, [7000 Series (plastic bowl)] [7300 Series (stainless steel bowl)].

EMERGENCY COMBINATION SHOWER WITH EYE AND FACE WASH

Shower: ANSI Z358.1; free standing, self-cleaning, non-clogging, 8-inch-diameter [stainless steel] [plastic] drench shower head, instant action stay open valve actuated by rigid stainless steel pull rod.

Eyewash: ANSI Z358.1; [plastic] [stainless steel] bowl with elbow, instant action stay open valve actuated by [push flag] [foot pedal] [push flag or foot pedal], twin spray heads [with face spray ring], [dust cover assembly].

Supply and Waste Piping: 1-1/4 inch IPS.

Furnish universal emergency sign.

[Furnish corrosion-resistant coating.]

Manufacturer: Haws, 8300 Series.

TEPID WATER BLENDING SYSTEM (Emergency Showers)

Product Description: Provide an assembly with two backup valves, separate high temperature sensing shut-off valve, separate full-flow pressure relief bypass, and temperature and pressure-compensating blending valve to plus or minus 3 degrees F. Water delivery temperature range 60 to 90 degrees F per ANSI Z358.1, Appendix A, over a range of flows to 35 gpm.

Manufacturer: HAWS, TWBS.SH.

EXECUTION

EXAMINATION

Verify walls and floor finishes are prepared and ready for installation of fixtures.

Verify electric power is available and of correct characteristics.

Confirm millwork is constructed with adequate provision for installation of counter top lavatories and sinks.

PREPARATION

Rough-in fixture piping connections in accordance with minimum sizes indicated in fixture rough-in schedule for particular fixtures.

Review millwork shop-drawings. Confirm location and size of fixtures and openings before rough in and installation.

Verify installation of wall supports and/or wall carriers for plumbing fixtures.

INSTALLATION

Install each fixture with trap, easily removable for servicing and cleaning.

Install fixture supplies with smooth bends and no kinks.

Install components level and plumb.

Install and secure fixtures in place with bolts.

Install plumbing fixtures at mounting heights and locations for the handicapped/elderly in accordance with ADA/ABA Accessibility Guidelines.

Seal fixtures to wall and floor surfaces with sealant as specified in Section 07 9200, Joint Sealants, color to match fixture.

Solidly attach water closets with lag screws. Lead flashing is not intended to hold fixture in place.

Provide chrome plated rigid or flexible supplies to fixtures with stops, reducers, and escutcheons.

For water closets, install manual flush valve with handle to wide side of stall.

ADJUSTING

Adjust stops or valves for intended water flow rate to fixtures without splashing, noise, or overflow.

CLEANING

Clean plumbing fixtures and equipment.

PROTECTION OF INSTALLED CONSTRUCTION

Do not permit use of fixtures before final acceptance.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 22 4200 Rev. 7, dated March 11, 2021.