SECTION 23 0593

TESTING, ADJUSTING, AND BALANCING FOR HVAC

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Requirements of Subcontractor, LANL, and LANL-retained TAB Agency.

TAB of [air], [hydronics], [steam], [and] [refrigerating] systems.

[Sound and vibration measurements of equipment operating conditions.]

Definitions

AABC: Associated Air Balance Council.

NEBB: National Environmental Balance Bureau.

TAB: Testing, Adjusting, and Balancing.

LANL PERFORMED WORK

TAB will be performed by an independent AABC or NEBB-certified TAB Agency, subcontracted and directed by LANL under a separate subcontract.

SUBMITTALS

- TAB Agency shall submit the following to the LANL Project Leader in accordance with Section 01 3300, Submittal Procedures:

- Date of expiration of AABC or NEBB certification (prior to starting work).

- TAB instruments that are to be used and calibration dates per AABC or NEBB requirements (prior to starting work).

- Final test reports that are signed and stamped by an AABC or NEBB TAB Supervisor on the latest edition of approved AABC or NEBB Report Forms.

QUALITY ASSURANCE

TAB Agency: Perform Work in accordance with the latest edition of AABC or NEBB procedural standards for TAB of environmental systems.

A LANL representative may witness all or portions of the TAB Agencies Work.

PRODUCT

  - INSTRUMENTS

The TAB Agency shall furnish instruments required for testing, adjusting, and balancing.

Instruments used for measurements shall meet AABC or NEBB-specified accuracy and calibration histories, and shall be available for spot-checking by LANL during testing.

EXECUTION

  - SUBCONTRACTOR RESPONSIBILITIES

    - Provide window in project schedule for completion of TAB services prior to final inspection of project.

Have mechanical, controls, structural and related electrical systems complete and operable before notifying LANL STR that project is ready for TAB Agency services and the requirements of 3.1 have been met.  Advance written notice of not less than 15 calendar days is required.

Complete operational readiness prior to commencement of TAB services.  Verify the following:

Doors, windows and ceilings are installed.

Systems are started and operating in safe and normal condition.

Temperature control systems are installed complete and operating.  Testing and programming of all system components and the overall system has been completed and test reports accepted by the LANL STR.

Laboratory airflow control systems are installed complete and operating.  Testing and programming of all system components and the overall system has been completed and test reports accepted by the LANL STR.

Proper thermal overload protection is in place for electrical equipment.

Construction filters have been replaced and the final filters are clean and in-place.

Duct systems are clean of debris.

Fans are rotating correctly.

Fire, smoke, and volume dampers are in place and open.

Air coil fins are cleaned and combed.

Access doors are closed and duct end caps are in place.

Air outlets and inlets are installed and connected.

Fume hoods and other local exhaust ventilation inlets are installed and connected.

Duct and piping supports are installed.

Duct systems are leak and pressure tested and test reports accepted by LANL STR.

Hydronic systems are leak tested and test reports accepted by LANL STR.

Hydronic systems are flushed, filled and vented.

Refrigerant systems are leak tested and test reports accepted by LANL STR.

Pumps are rotating correctly.

Start-up screens from pump suction diffusers are removed.

Proper strainer baskets are clean and in place.

Service and balance valves are open.

Pressure gauges, temperature gauges, test fittings, etc., are installed.

Put HVAC systems and equipment into full operation and continue operation during times of testing and balancing.

Do not operate equipment until properly lubricated and brought into manufacturer's specified operating conditions.

Provide labor and materials to make any change in sheaves, belts, and dampers, required for correct balance as requested by the TAB Agency.

Provide labor, i.e., remove and reinstall ceiling tiles, etc., to access concealed equipment as requested by TAB Agency.

After TAB Agency is notified and TAB work started, should system(s) be found to not be in readiness or a dispute occurs as to readiness of system(s), the STR may require a joint inspection be made by representatives of LANL, the TAB Agency and the Subcontractor.

Should inspection reveal TAB services notification to have been premature, costs of work previously accomplished by TAB Agency shall be paid for by the Subcontractor.

Such items as are not ready for TAB services shall be completed and placed in operational readiness by Subcontractor, and TAB services shall again be scheduled.

LANL RESPONSIBILITIES

Provide TAB Agency with Subcontract Drawings, approved submittal data, specifications and supplements required for TAB Agency to accomplish review, inspection and TAB services outlined in this specification.

Notify TAB Agency within 48 hours of receipt of written notification from Subcontractor that system(s) will be ready for testing, adjusting and balancing.

TAB AGENCY RESPONSIBILITIES

GENERAL

Review, inspect, test, adjust and balance systems, as outlined in this Section.

Promptly report to LANL STR any conditions that prevent system balancing.

Cooperate with Subcontractor but do not instruct or direct Subcontractor in any of the work, but make such reports as are necessary directly to LANL STR.

Do not provide any construction labor or materials to modify systems.

TOLERANCES

Air Handling Systems: Adjust to within plus or minus 10 percent of design flow rates.

Air Outlets and Inlets: Adjust total to within plus 10 percent and minus 5 percent of design flow rates to space. Adjusts outlets and inlets in space to within plus or minus 10 percent of design flow rates.

Hydronic Systems: Adjust to within plus or minus 10 percent of design flow rates.

ADJUSTING

Permanently mark settings of valves, dampers, and other adjustment devices allowing settings to be restored. Set and lock memory stops.

After adjustment, take measurements to verify balance has not been disrupted. If disrupted, verify correcting adjustments have been made.

Leave systems in proper working order, replacing belt guards, closing access doors, closing doors to electrical switch boxes, and restoring thermostats to specified settings.

AIR SYSTEM PROCEDURE

Adjust air handling and distributions systems to obtain required or design supply, return and exhaust airflow rates.

Make airflow rate measurements in main ducts by Pitot tube traverse of entire cross sectional area of duct.  Use the LOG method for rectangular ducts.  [For existing systems that already have test holes spaced for the Equal Area method, that method may be used.]

Measure airflow rates at air inlets and outlets.

Adjust distribution system to obtain uniform space temperatures free from objectionable drafts.

Use volume control devices to regulate airflow rates only to extent adjustments do not create objectionable air motion or sound levels.  Effect volume control by using volume dampers located in ducts.

Vary total system airflow rates by adjustment of fan speeds. Vary branch airflow rates by damper regulation

Provide system schematic with design and actual airflow rates recorded at each outlet or inlet.

Measure static air pressure conditions on air supply units, including filter and coil pressure drops, and total pressure across fan. Make allowances for 50 percent loading of filters.

Adjust outside air automatic dampers, outside air, return air, and exhaust dampers for design conditions. Check dampers for proper operation.

Check leakage across outside air, return air, and exhaust dampers.

At modulating damper locations, take measurements and balance at extreme conditions. Balance variable volume systems at maximum airflow rate, full cooling, and at minimum airflow rate, full heating.

Measure building static pressure and adjust supply, return, and exhaust air systems to obtain required relationship between each to maintain approximately [0.05] inches positive static pressure [near building entries] [in clean rooms].

Check multi-zone units for motorized damper leakage.  Adjust air quantities with mixing dampers set first for cooling, then heating, then modulating.

For variable air volume system powered units set volume controller to airflow setting indicated. Confirm connections properly made and confirm proper operation for automatic variable-air-volume temperature control.

On fan powered VAV boxes, adjust airflow switches for proper operation.

WATER SYSTEM PROCEDURE

Adjust water systems, after air balancing, to obtain design flow rates.

Use calibrated Venturi tubes, orifices, or other metered fittings and pressure gauges to determine flow rate for system balance.  Where flow-metering devices are not installed, base flow balance on temperature difference across various heat transfer elements in system.

Adjust systems to obtain specified pressure drops and flows through heat transfer elements prior to thermal testing.  Perform balancing by measurement of temperature differential in conjunction with air balancing.

Effect system balance with automatic control valves fully open or in normal position to heat transfer elements.

Effect adjustment of water distribution systems by means of balancing cocks, valves, and fittings.  Do not use service or shut-off valves for balancing unless indexed for balance point.

Where available pump capacity is less than total flow requirements or individual system parts simulate full flow in one part by temporary restriction of flow to other parts.

TAB AGENCY TEST REPORT FORMS

Final report forms shall contain the following minimum data.

Report Forms

Title Page:

Name of Testing, Adjusting, and Balancing Agency

Address of Testing, Adjusting, and Balancing Agency

Telephone and facsimile numbers of Testing, Adjusting, and Balancing Agency

Project name

Project location

Subcontract Technical Representative (STR)

Project Subcontractor

Project altitude

Report date

Summary Comments:

Design versus final performance

Notable characteristics of system

Description of systems operation sequence

Summary of outdoor and exhaust flows to indicate building pressurization

Nomenclature used throughout report

Test conditions

Instrument List:

Instrument

Manufacturer

Model number

Serial number

Range

Calibration date

Electric Motors:

Manufacturer

Model/Frame

HP/BHP

Phase, voltage, amperage; nameplate, actual, no load

RPM

Service factor

Starter size, rating, heater elements

Sheave Make/Size/Bore

V-Belt Drive:

Identification/location

Required driven RPM

Driven sheave, diameter and RPM

Belt, size and quantity

Motor sheave diameter and RPM

Center to center distance

Pump Data:

Identification/number

Manufacturer

Size/model

Impeller size: Include info on how this is determined (i.e. pump curves, etc.)

Service

Design flow rate, pressure drop, BHP

Actual flow rate, pressure drop, BHP

Discharge pressure

Suction pressure

Total operating head pressure

Shut off, discharge and suction pressures

Shut off, total head pressure

Air Cooled Condenser:

Identification/number

Location

Manufacturer

Model number

Serial number

Entering DB air temperature, design and actual

Leaving DB air temperature, design and actual

Number of compressors

Chillers:

Identification/number

Manufacturer

Capacity

Model number

Serial number

Evaporator entering water temperature, design and actual

Evaporator leaving water temperature, design and actual

Evaporator pressure drop, design and actual

Evaporator water flow rate, design and actual

Condenser entering water temperature, design and actual

Condenser pressure drop, design and actual

Condenser water flow rate, design and actual

Cooling Tower:

Tower identification/number

Manufacturer

Model number

Serial number

Rated capacity

Entering air WB temperature, specified and actual

Leaving air WB temperature, specified and actual

Ambient air DB temperature

Condenser water entering temperature

Condenser water leaving temperature

Condenser water flow rate

Fan RPM

Heat Exchanger:

Identification/number

Location

Service

Manufacturer

Model number

Serial number

Steam pressure, design and actual

Primary water entering temperature, design and actual

Primary water leaving temperature, design and actual

Primary water flow, design and actual

Primary water pressure drop, design and actual

Secondary water leaving temperature, design and actual

Secondary water leaving temperature, design and actual

Secondary water flow, design and actual

Secondary water pressure drop, design and actual

Cooling Coil Data:

Identification/number

Location

Service

Manufacturer

Air flow, design and actual

Entering air DB temperature, design and actual

Entering air WB temperature, design and actual

Leaving air WB temperature, design and actual

Leaving air WB temperature, design and actual

Water flow, design and actual

Water pressure drop, design and actual

Entering water temperature, design and actual

Leaving water temperature, design and actual

Saturated suction temperature, design and actual

Air pressure drop, design and actual

Heating Coil Data:

Identification/number

Location

Service

Manufacturer

Air flow, design and actual

Water flow, design and actual

Water pressure drop, design and actual

Entering water temperature, design and actual

Leaving water temperature, design and actual

Entering air temperature, design and actual

Leaving air temperature, design and actual

Air pressure drop, design and actual

Electric Duct Heater:

Manufacturer

Identification/number

Location

Model number

Design kW

Number of stages and readings

Phase, voltage, amperage

Test voltage (each phase)

Test amperage (each phase)

Air flow, specified and actual

Temperature rise, specified and actual

Unit Ventilator and Fan Coil Data:

Manufacturer

Identification/number

Location

Model number

Size

Air flow, design and actual

Water flow, design and actual

Water pressure drop, design and actual

Entering water temperature, design and actual

Leaving water temperature, design and actual

Entering air temperature, design and actual

Leaving air temperature, design and actual

Air Moving Equipment:

Location

Manufacturer

Model number

Serial number

Arrangement/Class/Discharge

Air flow, specified and actual

Return air flow, specified and actual

Outside air flow, specified and actual

Total static pressure (total external), specified and actual

Inlet pressure

Discharge pressure

Sheave Make/Size/Bore

Number of Belts/Make/Size

Fan RPM

Return Air/Outside Air Data:

Identification/location

Design air flow

Actual air flow

Design return air flow

Actual return air flow

Design outside air flow

Actual outside air flow

Return air temperature

Outside air temperature

Required mixed air temperature

Actual mixed air temperature

Design outside/return air ratio

Actual outside/return air ratio

Exhaust Fan Data:

Location

Manufacturer

Model number

Serial number

Air flow, specified and actual

Total static pressure (total external), specified and actual

Inlet pressure

Discharge pressure

Sheave Make/Size/Bore

Number of Belts/Make/Size

Fan RPM

Duct Traverse:  Use Log method for rectangular ducts

System zone/branch

Duct size

Area

Design velocity

Design air flow

Test velocity

Test air flow

Duct static pressure

Air temperature

Air correction factor

Air Monitoring Station Data:

Identification/location

System

Size

Area

Design velocity

Design air flow

Test velocity

Test air flow

Flow Measuring Station:

Identification/number

Location

Size

Manufacturer

Model number

Serial number

Design Flow rate

Design pressure drop

Actual/final pressure drop

Actual/final flow rate

Station calibrated setting

Terminal Unit Data:

Manufacturer

Type, constant, variable, single, dual duct

Identification/number

Location

Model number

Size

Minimum static pressure

Minimum design air flow

Maximum design air flow

Maximum actual air flow

Inlet static pressure

Air Distribution Test Sheet:

Air terminal number

Room number/location

Terminal type

Terminal size

Area factor

Design velocity

Design air flow

Test (final) velocity

Test (final) air flow

Percent of design air flow

*************************************************************************************************************

To clarify equipment included in sound and vibration measurements, consider adding a list to this paragraph.

*************************************************************************************************************

Sound Level Report:

Location

Octave bands - equipment off

Octave bands - equipment on

RC level - equipment on

*************************************************************************************************************

To clarify equipment included in sound and vibration measurements, consider adding a list to this paragraph.

*************************************************************************************************************

Vibration Test:

Location of points:

          - Fan bearing, drive end

          - Fan bearing, opposite end

          - Motor bearing, center (when applicable)

          - Motor bearing, drive end

          - Motor bearing, opposite end

          - Casing (bottom or top)

          - Casing (side)

          - Duct after flexible connection (discharge)

          - Duct after flexible connection (suction)

Test readings:

          - Horizontal, velocity and displacement

Vertical, velocity and displacement

Axial, velocity and displacement

Normally acceptable readings, velocity and acceleration

Unusual conditions at time of test

Vibration source (when non-complying)

END OF SECTION

*********************************************************

Do not delete the following reference information.

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 0593 Rev. 2, dated June 4, 2009.