SECTION 23 2217

STEAM AND CONDENSATE SPECIALTIES

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

The following specialties downstream of first steam shutoff valve inside building:

Steam traps.

Steam air vents.

Vacuum breakers.

Pressure gauges.

Moisture separators.

Pressure reducing valves.

Safety relief valves.

Condensate pressure-motive pumps.

SUBMITTALS

Submit the following in accordance with Section 01 3300, Submittal Procedures:

Catalog data of specialties specified.

Installation instructions for steam traps, pressure reducing valves, and safety relief valves and condensate pressure pumps.

Operating and maintenance data of specialties specified.

QUALITY ASSURANCE

Comply with ASME B31.9, Building Services Piping.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternative products may be accepted; follow Section 01 2500, Substitution Procedures.

FLOAT AND THERMOSTATIC TRAP

Manufacturer: Watson McDaniel, Series FT.

Trap: Cast iron body, with stainless steel interior parts, maximum operating pressure 125 psig at 350 degrees F.

Capacity: [          ] lbs/hr condensate at [           ] psig pressure differential.

Size: [         ] inch.  [Minimum size 3/4 inch.]

THERMOSTATIC TRAP

Manufacturer: Watson McDaniel, Series WT 3000.

B.	Trap: Stainless steel construction, maximum operating pressure 300 psig at 750 degrees F.

Capacity: [             ] lbs/hr condensate at [               ] psig inlet pressure.

Size: [                ] inch.  [Minimum size 3/4 inch.]

STEAM AIR VENTS

Manufacturer: Watson McDaniel, AV2000.

Air Vent: Stainless steel body with stainless steel interior parts, bellows operated, suitable for steam service to 150 psig.

Size: 1/2 inch NPT inlet and outlet.

VACUUM BREAKER

Manufacturer: DFT Inc., No. BSSV.

Vacuum Breaker: Stainless steel body with stainless steel interior parts, suitable for steam service to 150 psig.

Size: 1 inch MNPT.

PRESSURE GAUGE

*************************************************************************************************************

Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the working pressure is recommended, with maximum working pressure not exceeding 75 percent of the range. If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.

*************************************************************************************************************

Manufacturer: Ashcroft, Type 1009

Gauge: ASME B40.100, Grade IA, minimum 2 1/2 inch dial, 1/4 inch NPT brass bottom connection, phosphor bronze bourden tube, maximum plus or minus 1 percent accuracy full scale, stainless steel case, with Schedule 40 steel siphon tube.

Range: [          ] psi or [See Drawings].

MOISTURE SEPARATOR

*************************************************************************************************************

Size moisture separator inlet to match building supply steam piping.

*************************************************************************************************************

Manufacturer: Watson McDaniel, Series WDS.

Moisture Separator: Steam service, cast iron construction, maximum operating pressure 125 psig at 350 degrees F.

Size: [           ] inch [NPT or 125 lb. flanged connections].

PRESSURE REDUCING VALVE

Manufacturer: Watson McDaniel, Type DP.

Pressure Reducing Valve: Steam service, cast iron construction, self operating, external pilot, single seated, normally-closed, maximum inlet pressure 250 psig at 450 degrees F.

Capacity: [             ] lbs/hr at [             ] psig inlet and [              ] psig outlet pressures.

Size: [           ] inch - threaded up to 2 inches, flanged over 2 inches.

Valve Spring: [3 to 25 psig, yellow] [20 to 100 psig, blue] [80-200 psig, red].

SAFETY RELIEF VALVES

Manufacturer: Kunkle, [No. 6010 (threaded ends, bronze body)] [No. 252 
(flanged ends, iron body).

Valve: Steam service, ASME approved, N.B. certified, lever handle, factory tested and adjusted, maximum pressure setting 250 psig at 406 degrees F.

Capacity: [               ] lbs/hr at 10 percent accumulation.

Orifice Size: [                ] sq. inch.

Size: [            ] inch - threaded up to 2 inches, flanged over 2 inches.

Accessories: Drip pan elbow shipped loose, same size as relief valve outlet.

CONDENSATE PRESSURE MOTIVE PUMPS

*************************************************************************************************************

Complete skid-mounted unit, including receiver tanks, pump(s), check valves, etc., all fully piped are available.  It is recommended that a receiver tank be specified when above ground steam/condensate distribution lines feed the building.  Consult with the motive pump distributor for selection guidance.  Specify ASME coded receiver tanks.

*************************************************************************************************************

Manufacturer: Watson McDaniel, [Series PMP C, (Ductile Iron Body)] or  [            ].

EXECUTION

  - INSTALLATION

Install specialties in accordance with manufacturer’s instructions.

Provide condensate piping no smaller than trap inlet.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 2217 Rev. 1, dated June 11, 2008.