SECTION 26 0526

Grounding and Bonding for electrical systems

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The document must also be edited to delete specification requirements for processes, items, or designs that are not included in the project — and specifiers’ notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality Sections.

*************************************************************************************************************

GENERAL

Section Includes

*********************************************************************************************************

Edit the following to match Project requirements; delete articles that are not needed.

*********************************************************************************************************

Main Grounding Electrode System (if present, lightning protection system grounding is specified in Section 26 4100)

System Grounding (connection of the electrical system to the soil/earth)

Enclosure and Equipment Grounding System (components and construction of the effective ground-fault current path)

Isolated Ground System

Signal Reference Grid

Static Electricity Grounding and Bonding

informational SUBMITTALS

************************************************************************************************************

Edit the following to match Project requirements; include submittals only to the extent required to assure quality for the particular project and delete any that are not needed.

************************************************************************************************************

Submit the following in accordance with Section 01 3300 Submittal Procedures:

      - Provide documentation of quality control inspections performed under this Section.  Meet the requirements of 01 0400 Quality Requirements when present in Specification.

REGULATORY REQUIREMENTS

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) where such products are required by the NEC to be listed, or such products enclose an electrical hazard as follows:

For AC circuits – greater than 50 volts

For DC circuits and batteries – greater than 100 volts.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - product options and substitutions

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************

Edit Articles 2.2, 2.3, and 2.4 to match Project requirements. Delete if not applicable to Project.

Chemical ground rods should rarely, if ever, be used.  The maintenance required for them is significant (such that the ongoing cost of having them most likely outweighs the benefit).

*************************************************************************************************************

Ground Rods

ANSI C135.30 with high-strength steel core and electrolytic-grade copper outer sheath, molten welded to core.

Manufacturers: Blackburn, Thomas & Betts, Harger

CHEMICAL GROUND ROD

Provide chemical ground rod(s) as shown on the Drawings.

Furnish chemical ground rods fabricated from Type K copper tubing approximately 10 feet long, 2 inches in diameter and containing a hygroscopic electrolyte material.

Furnish each chemical ground rod with a 24-inch-long, 4/0 AWG copper pigtail, a protective cover box, and sufficient ground ground-enhancing backfill material for installation in a 6-inch augered hole.

Manufacturers: Lyncole Industries Inc.; LEC Inc.; Superior Grounding Systems, Inc.

Electrical system  GROUNDing BAR and Grounding Bar Extensions

Provide grounding bar, 12 inches long or greater length as indicated on the Drawings, fabricated from 1/4 inch thick, 4 inch wide copper stock with 1.75” x 2" bolt-hole pattern to accept NEMA standard lugs. Mount grounding bar on 2,700 volt standoff insulators.

*********************************************************************************************************

Edit the following Articles to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

LOW-VOLTAGE DISTRIBUTION TRANSFORMER GROUNDING TERMINAL BAR

Furnish, if one is not already installed by the factory, a terminal bar that is suitably sized for the type and size of the following conductors:

system bonding jumper

supply side bonding jumper

grounding electrode conductor

primary equipment grounding conductor.

GROUND PLATES

Provide ground plates designed for flush mounting in concrete structures.

Furnish copper alloy castings with four 1/2” x 13 threaded holes at 1.75" x 1.75" NEMA spacing and a welding stud or compression connection suitable for 2 AWG to 250 kcmil copper conductor.

Furnish ground plates that are suitable for direct burial and have been tested successfully according to the requirements of IEEE Std. 837 IEEE Standard for Qualifying Permanent Connections Used in Substation Grounding.

Manufacturer: Burndy “YGF”

***********************************************************************

In the following article, retain either A or B.

***********************************************************************

GROUNDing ELECTRODE conductor

Provide bare-stranded, soft-temper copper conductor that conforms to ASTM B8 Standard Specification for Concentric-Lay Stranded Copper Conductors.

Provide green insulated THWN-2 copper conductor.

Equipment GROUNDING CONDUCTORS

Provide THHN/THWN-2 insulated copper wire.

Use solid equipment grounding conductors 10 AWG and smaller where not subject to vibration or repeated flexing.

Use stranded equipment grounding conductors for 8 AWG and larger.

Use stranded equipment grounding conductors where subject to vibration or repeated flexing.  Use stranded equipment grounding conductors in flexible conduit at motor connections.

Color code equipment grounding conductors as follows:

#### Equipment grounding conductor:

##### Conductors 6 AWG and smaller: Green colored insulation.

##### Conductors 4 AWG and larger: Green colored insulation or other colored insulation, not white, with 3/4-inch-wide band of water and oil-resistant green vinyl electrical tape.

#### Isolated grounding conductor:

##### Conductors 6 AWG and smaller: Green colored insulation with continuous yellow stripe.

##### Conductors 4 AWG and larger, or any size conductor that is part of a cable assembly: Green-colored insulation with continuous yellow stripe—or other-colored insulation (except white,) with ¾-inch wide bands of water- and oil-resistant green and yellow vinyl electrical tape.

CONDUIT GROUNDING BUSHINGS

Provide 150 C rated insulated throat grounding bushings with lay-in type ground cable lugs.

Manufacturers: O-Z/Gedney Type “BLG”.

COMPRESSION GROUNDING CONNECTIONS

Provide wrought copper connectors, terminals, taps, and splices for making compression grounding connections.  Connections, on a ground bar, that are a part of the grounding electrode conductor shall be made with irreversible connections.

Furnish  grounding connectors that are identified for direct burial

Provide connector manufacturer’s hydraulic compression tools and dies that match the connectors.

Match connector and die size to material shapes and conductor sizes to be joined.

Use two-hole, heavy-duty compression lugs for bolted connections to ground bars, ground plates, and equipment ground pads for conductors that are 2 AWG and larger.

Manufacturer: Burndy “Hyground”

EXOTHERMIC WELD GROUNDING CONNECTIONS

Provide molds and welding material for making exothermic weld connections

In interior locations and in vaults, use low smoke emission type welding material

Match mold and weld material to material types, shapes and sizes to be joined

Manufacturer: ERICO Cadweld

Pipe GROUNDing CONNECTORS

Provide copper-alloy connectors for making cable to pipe connections.

Manufacturer: O-Z/Gedney “ABG” or “CG”

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project. Refer to Section D5020 in Chapter 7 of the LANL Engineering Standards Manual for design requirements

*************************************************************************************************************

SIGNAL REFERENCE GRID (SRG)

Provide a pre-fabricated grid of 2-inch-wide by 26-gage copper strips on two foot centers with all crossover connections factory welded.

Provide low impedance risers consisting of 2 inch wide by 26 gage copper strips for connecting equipment to the SRG.

Manufacturers: ERICO Cadweld, Harger.

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project. Refer to Section D5020 in Chapter 7 of the LANL Engineering Standards Manual for static electricity grounding and bonding design requirements.

*************************************************************************************************************

Static Electricity Grounding and Bonding

Furnish static electricity grounding and bonding material as indicated on the Drawings and as required for a complete installation.

Provide static ground bus complete with clamps, connectors, and mounting hardware.

      - Ground bus cable: 1/0 AWG bare stranded, soft temper copper cable that conforms to ASTM B8 Standard Specification for Concentric-Lay Stranded Copper Conductors.

      - Connectors: Copper compression ring tongue terminals. Provide connector manufacturer’s compression tools and dies that match the connectors. Manufacturer: Burndy YAV-L.

      - Cable holders: Preformed copper support loops, 5/8 inch wide. Manufacturer: Thompson Lighting Protection No. 166.

Provide retractable static grounding reels with an enclosed cable drum and [20] [50] feet of 3/32 inch galvanized cable having a spring compression grounding clamp. Manufacturer: Stewart R. Browne Manufacturing type [R-20] [R-50].

Provide spring compression grounding clamps having a plier type cast aluminum body and two stainless steel contact points. Manufacturer: Stewart R. Browne Manufacturing type REB2960.

Provide cast bronze clamps for static bonding of metal pipes. Manufacturer: Stewart R. Browne Manufacturing JR150 series.

Provide cast bronze or galvanized steel C-clamps for making semi-permanent connections to drums and containers. Manufacturer: Stewart R. Browne Manufacturing type EP.

EXECUTION

  - EXAMINATION

    - Measurements shown on Drawings are approximate.  Verify with field measurements.

    - Electrode locations and grounding cable routing shown on Drawings are approximate unless dimensioned.

      - Install electrodes and route cable as required to meet Project conditions.

      - Where electrode location or cable routing is not shown, and destination only is indicated, determine exact locations, routing, and lengths required to meet Project conditions.

  - GENERAL

Install grounding and bonding material according to manufacturer's instructions.  Have the manufacturer’s installation instructions available at the construction site.

    - Do not use the grounding systems specified in this section for lightning protection grounding.

*************************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

    - Use the following connection methods unless otherwise specified or indicated on the Drawings:

      - Use exothermic weld grounding connections for underground or concealed connections of dissimilar materials.

      - Use exothermic weld or compression grounding connections for underground or concealed connections of like materials.

      - Use exothermic weld, compression, or bolted grounding connections for accessible connections.

      - Make bolted connections using bolts, nuts, flat washers, and toothed lock washers suitable for the connector and the installation environment; acceptable materials include high strength silicon bronze and 18-8 alloy stainless steel.

      - Make irreversible bolted connections using stainless steel tamper-resistant bolts and tamper-resistant nuts along with flat washers, and toothed lock washers. Tamper-resistant nuts and bolts must resist loosening with common tools; acceptable tamper-resistant fasteners include penta-head, break-away, and oval designs.

      - Use a connector that is identified for the application

    - Tighten grounding and bonding connectors and terminals, including screws and bolts, in accordance with manufacturer's published torque tightening values for connectors and bolts. Where manufacturer's torquing requirements are not indicated, tighten connections to comply with torque tightening values specified in ANSI/NETA ATS/MTS tables 110.12.1, 110.12.2, 110.12.3, or 110.12.4 as appropriate. Use a calibrated torque wrench.  Manufacturer’s alternate methods for achieving proper torque values are acceptable.
Note:  On older equipment that needs to be re-terminated, the metallurgy or grade isn’t always known.  Types of terminations may also be very unusual and might not fit into one of the categories in the tables.  The system engineer or other authority should be consulted as to how to proceed in cases such as this.

    - Use hydraulic compression tools to provide the correct circumferential pressure for compression connectors. Follow connector manufacturer’s installation instructions and use tools and dies recommended by the manufacturer of the connectors. Provide embossing die code or other standard method to make a visible indication that a connector has been adequately compressed.

    - Install exothermic welds in accordance with manufacturer's instructions and recommendations.

    - Make connections in such a manner as to minimize possibility of galvanic action or electrolysis. Select connectors, connection hardware, conductors, and connection methods so metals in direct contact will be galvanically compatible.

      - Use electroplated or hot-tin-coated materials to assure high conductivity and make contact points closer in order of galvanic series.

      - Make connections with clean bare metal at points of contact.

      - Make aluminum to steel connections with stainless steel separators and mechanical clamps.

      - Make aluminum to galvanized steel connections with tin-plated copper jumpers and mechanical clamps.

      - In underground, damp, or wet locations, coat and seal connections involving dissimilar metals with inert material to prevent future penetration of moisture to contact surfaces.

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - hold points

    - The grounding electrode system must be inspected before the system is covered up, by earthwork, concrete, or building finish.

  - Electrical system GROUNDING ELECTRODE SYSTEM

    - Concrete Encased Electrode: Install in accordance with NEC, as shown on drawings.

*************************************************************************************************************

Use the following paragraph only if it is not possible to install a concrete-encased electrode. Delete if not applicable to Project.

*************************************************************************************************************

    - Ground Rod Electrode:  Install a ground rod electrode system constructed per the State of New Mexico Electrical Code, if applicable.

      - Install at least 20 feet of 2 AWG bare copper conductor in direct contact with the earth at a depth below the earth’s surface of not less than thirty (30) inches.  The 2 AWG bare copper conductor shall be installed in a continuous trench that is at least twenty (20) feet in length and be augmented with a minimum of two (2), eight (8) foot long, minimum, grounds rods one at each end of the 2 AWG conductor.

  - Electrical system GROUNDing BAR and Grounding Bar Extensions

    - Install a grounding bar in an accessible location in the main electrical room adjacent to the service equipment or main equipment.

    - Make an irreversible connection between the grounding bar and the grounding electrode conductor; use exothermic weld connection or compression grounding lug with tamper-resistant fasteners.

    - Do not connect the lightning protection system at this location; make the connection between the building grounding electrode system and the lightning protection electrode system at a point outside the building.

*********************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

    - Main ground electrode bar extensions may be established at additional locations by installing main ground bars or ground plates connected to the main electrode ground bar using 4/0 AWG ground conductor with an irreversible connection to each ground bar.

    - Connections to the main ground electrode ground bar [or extensions] will be considered as connections directly to the main ground electrode.

    - Bond exterior underground metal fire protection and potable water service pipes to the main ground electrode bar; use pipe grounding fittings and ground conductor as indicated on the Drawings, or not smaller than the grounding electrode conductor required by the NEC and not smaller than 4 AWG.  Make bond to each water pipe at an accessible location within 5 ft of where it enters the structure.  Comply with NEC requirements for bonding around water meters and insulating joints.

*********************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

    - Bond the nearest building perimeter structural steel column or effectively grounded metal structure to the main ground electrode ground bar; use ground conductor as indicated on the Drawings, or not smaller than the grounding electrode conductor required by the NEC and not smaller than 4 AWG.

*********************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

  - SYSTEM GROUNDING

    - Service equipment

      - Connect the service equipment ground bus to the electrical system grounding bar; use a grounding electrode conductor as indicated on the Drawings, or not smaller than the grounding electrode conductor required by the NEC and not smaller than 4 AWG.

*********************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

    - Separately Derived Systems:

      - Install system bonding jumper in transformer enclosure, from the neutral point of the transformer to the transformer grounding terminal bar.  Size system bonding jumper as shown on drawings, but not less than the NEC requirement in table 250.102(C)(1).

      - When the system bonding jumper is in the transformer, grounding electrode conductor shall be terminated to transformer grounding bar.

      - First means of disconnect shall have no system bonding jumper installed and shall have separate neutral and ground bars.

  - ENCLOSURE AND EQUIPMENT GROUNDING

    - Provide permanent and effective equipment, enclosure, and raceway bonding in accordance with NEC requirements and as further specified or shown on the Drawings.

    - Provide an equipment ground bar, if one is not already a part of the equipment, in all switchgear, switchboards, panelboards, transformers, motor control centers, starters, and disconnect switch, for grounding the enclosure and for connecting other equipment and raceway grounding and bonding conductors.

Note: Some drawings show a bonding jumper between the grounding bar and the enclosure.  This is for illustration only and is not meant to be installed in the field.

    - Make connections and couplings on metallic conduit systems wrench-tight.

    - Bonding Bushings:

      - Install bonding bushings on metallic conduits entering enclosures through concentric, eccentric or oversize knockouts.

      - Install bonding bushings on metallic conduits that terminate to a metallic enclosure without effective electrical connection such as locknuts or threaded bushings.

Bond conduit bonding bushing lug to the equipment ground bar or ground lug in switchgear, panelboards, transformers, motor control centers, starters, disconnect switches, cabinets, etc.  Size bonding jumpers in accordance with the NEC.

      - If bonding jumpers are part of the effective ground-fault current path that is downstream of overcurrent protection, the bonding jumper is an “equipment bonding jumper” and is sized per table 250.122 in the NEC based on the rating of the overcurrent protection upstream.

      - If bonding jumpers are part of the effective ground-fault current path that is upstream of overcurrent protection, the bonding jumper is a “supply-side bonding jumper” and is sized per table 250.102(C)(1) in the NEC.

    - Provide an insulated equipment grounding conductor for each raceway containing feeder or branch circuits.

      - Install the equipment grounding conductor within the common conduit or raceway with the related phase and neutral conductors and connect to the grounding terminal or grounding bus in each box or cabinet where a splice or termination of the associated conductors is made.

      - Size equipment grounding conductor as shown on the Drawings.

    - In each 15 or 20 ampere branch circuit outlet box and junction box where a splice is made, install a green-colored, washer-head grounding screw with a 12 AWG equipment grounding conductor pigtail and connect it to the equipment grounding conductor of the associated circuit.

    - Connect receptacle grounding terminals to the effective ground-fault current path   using minimum 12 AWG equipment grounding conductor.  Do not use a "self-grounding" receptacle strap as the only equipment grounding path.

*********************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

    - Provide busways with a separate, internal equipment grounding conductor bus bar.  Install separate insulated equipment grounding conductor from the ground bus in the switchgear, switchboard, or distribution panel to the equipment grounding conductor bar terminal on busway.  Size conductor in accordance with the NEC.

*********************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project.

Isolated ground systems shall only be installed with the permission of the LANL Electrical Standards Point of Contact.

*********************************************************************************************************

  - ISOLATED GROUND SYSTEM

    - Install an isolated ground system as shown on the Drawings. In addition to the equipment ground bar, provide a separate, insulated, isolated copper ground bar in panelboards and switchboards supplying isolated ground circuits.

    - Run the isolated grounding conductor together with the phase, neutral, and equipment grounding conductors in isolated ground system feeder and branch circuit conduits.

    - Make the isolated ground conductor the same size as the associated line or phase conductors.

    - At the first isolated ground system overcurrent device or disconnecting means, or where shown on drawings, bond the isolated ground bus to the equipment ground bus.  Make no other isolated ground to equipment ground connections on the load side of the separately derived system disconnect.

    - Connect the isolated ground conductors to the isolated ground bars in switchboards and panelboards and to the isolated ground terminals at receptacles and equipment.

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project. Refer to Section D5020 in Chapter 7 of the LANL Engineering Standards Manual for SRG requirements.

*************************************************************************************************************

  - SIGNAL REFERENCE GRID (SRG)

    - Install an SRG on the concrete subfloor under raised computer flooring as indicated on the Drawings.  Join pre-fabricated grid sections by exothermic welding.  Position copper strip so sharp burrs on edge of strip face down.

    - Bond structure, conduits, water pipes, ducts, etc., entering the computer room to the SRG. Bond to the nearest intersecting point of SRG using 6 AWG grounding conductor.

    - Bond computer equipment to the SRG using low impedance riser (LIR).

      - Do not connect LIR to the SRG strip closest to the outside edges.

      - Cut LIR to the shortest possible length.

      - If length of LIR exceeds 24 inches, use two parallel LIRs.  Make the second LIR 20% to 40% longer than the first and connect to equipment at opposite corners.

    - Bond power distribution units and power distribution panelboards to the SRG using LIR.

    - Bond every sixth raised floor pedestal in each direction to the nearest intersecting point of the SRG using 6 AWG grounding conductor.  Keep conductors as short as possible.

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project. Refer to Section D5020 in Chapter 7 of the LANL Engineering Standards Manual for static electricity grounding and bonding design requirements.

*************************************************************************************************************

Static Electricity Grounding and Bonding

    - Install static electricity grounding and bonding material as indicated on the Drawings.

    - Comply with the NEC and NFPA 77 Recommended Practices on Static Electricity.

    - Install ground bus cable from the [main electrode ground bar or extension] [effectively grounded building structural steel] to the static electricity grounding and bonding locations indicated on the Drawings.

    - Support exposed ground bus cable with cable holders installed at intervals not exceeding 24 inches.

    - Make connections to and between ground bus cable using compression connectors, nuts, bolts, flat washers, and lock washers.  Install compression connectors using tools and compression dies recommended by the connector manufacturer.

    - Install static grounding cable reels at locations indicated on the Drawings; coordinate location with luminaires, equipment, piping, and ductwork.

    - Install pipe clamps and C-clamps to bond pipes, drums, and tanks in the static electricity control areas.

  - FIELD QUALITY CONTROL

    - General: Constructor shall perform on-site quality control inspections.  Inspection shall be visual for workmanship and adherence to requirements before grounding electrode system is covered up by earth or concrete.

    - Notify the LANL Subcontract Technical Representative (STR) ten (10) working days in advance of the expected completion of a grounding system installation.  Inspection can be scheduled in parts or by area depending on the system and construction schedule.

    - Before work is concealed, it must be inspected by the office of the Chief Electrical Inspector to verify and certify that the following grounding installations have been made correctly:

      - The electrical system grounding electrode system.  This includes the bonding of the foundation reinforcing bars, bonding of the structural steel columns, and bonding of other metallic systems and other grounding electrode systems.

      - Ground plates and grounding bars.

      - All other underground grounding installations.

*********************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable to Project.

*********************************************************************************************************

      - Signal reference grid (SRG) before the raised flooring is installed.

END OF SECTION

**************************************************************************************************

Do not delete the following reference information.

**************************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0526 Rev. 3, dated August 24, 2020.