SECTION 26 0548.16

SEISMIC CONTROLS FOR ELECTRICAL SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

This template isn’t applicable to systems/ components that are seismically exempt per ASCE 7 Ch. 13, or to “non-exempt components” that will comply with ASCE 7 (paragraph 13.2.1 in 2010 edition) via Manufacturer certification.

In order to properly edit the template for “non-exempt components,” the following two (2) decisions have to have been made first:

- Who is going to be responsible for preparing Project-specific design and documentation (ref. ASCE 7 paragraph 13.2.1)

- Whether or not the component(s) a Designated Seismic System (DSS).

I) There are two (2) options for preparation of Project-specific design and documentation:

- Engineer of Record (EOR), or

- Construction subcontractor (i.e., Delegated Design).

Once it’s known whether I.A of I.B applies to the Project in question, subsequent author notes can be properly interpreted and the section text edited.

II) DSS: If a component must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5, which makes it a DSS (per ASCE 7 paragraph 13.1.3).  If the DSS requires Special Certification per ASCE 7 paragraph 13.2.2, this Section (26 0548.16) shall reference Section 01 8734, SEISMIC QUALIFICATION OF NONSTRUCTURAL COMPONENTS (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.

Seismic control/ restraint is achieved by devices (e.g., supports and attachments, etc.) that provide restraint against excessive movement during an earthquake (without compromising the effectiveness of vibration isolators, if applicable).  Since these devices are included herein, if a Project Spec includes this Section, only control/ restraint devices that differ from those herein (that are required for use) need be included in the Section pertaining to the component (or added herein if used in multiple Sections).
*************************************************************************************************************

- GENERAL

      - SUMMARY

        - Section Includes:

          - Restraint channel bracings.

          - Restraint cables.

          - Seismic-restraint accessories.

        - Related Requirements:

*************************************************************************************************************

Retain subparagraphs below to cross-reference requirements Subcontractor might expect to find in this Section but are specified in other Sections.

Refer to the “seismic portion” of the author note on page 1 for details associated w/ 1st subparagraph.

- If ASCE 7 paragraph 13.2.1 is going to be complied with via manufacturer certification, and the component isn’t a DSS requiring Special Certification, then delete the 1st subparagraph

- If the component is a DSS requiring Special Certification, retain the 1st subparagraph (regardless of how ASCE 7 paragraph 13.2.1 is going to be complied with).

The last subparagraph is required in order to link this Section (26 0548.16) w/ the reason it’s necessary.  In other words, identify the section number and title associated w/ the component that requires seismic control (and ensure that Section refers to this one).  Add as many similar subparagraphs as applicable.

- *************************************************************************************************************

          - Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements for manufacturer certification for seismic qualification of components, supports, and attachments; and for special certification of Designated Seismic Systems.

          - Section 05 0520, Post-Installed Concrete and Grouted-Masonry Anchors Normal Confidence, for product and installation requirements.

          - Section 09 5100, Acoustical Ceilings, for requirements for seismic restraint of lighting fixtures associated with suspended ceilings.

          - Section 26 0529, Hangers and Supports for Electrical Systems, for commonly used electrical supports and installation requirements.

          - Section 26 5200, Emergency Lighting, for product and installation requirements associated with seismic restraint/ protection.

          - Section 26 [____], [________________________________________], for all requirements associated with the component/ system requiring seismic control.

      - REFERENCES

        - American Society of Civil Engineers (ASCE):

          - ASCE 7 – Minimum Design Loads for Buildings and Other Structures

        - ASTM International:

          - ASTM A492 – Standard Specification for Stainless Steel Rope Wire

          - ASTM A603 –  Standard Specification for Zinc-Coated Steel Structural Wire Rope

        - American Welding Society (AWS)

          - AWS D1.1 – Structural Welding Code – Steel

        - International Code Council (ICC):

          - IBC – International Building Code

          - ES – Evaluation Service

            - ESR – Evaluation Service Report

        - Metal Framing Manufacturers Association (MFMA)

          - MFMA-4 – Metal Framing Standards Publication

        - National Fire Protection Association (NFPA)

          - NFPA 70 – National Electric Code

        - State of California Office of Statewide Health Planning and Development (OSHPD)

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic-restraint component used.

*************************************************************************************************************

Edit the options in the following subparagraph in accordance w/ the applicable independent third-party evaluator/ certifier of the product(s) to be used.  And the same goes for subsequent similar Paragraphs/ subparagraphs herein.

- *************************************************************************************************************

            - Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated by [an ICC-ES ESR] [OSHPD] [______].

            - Annotate to indicate application of each product submitted and compliance with requirements.

        - Welding Procedure Specification (WPS) and Procedure Qualification Record (PQR):

          - Shop:

            - Prior to shop welding, submit WPS and supporting PQR meeting the requirements of AWS D1.1 for the processes and materials that will be used for welding.  See Section 01 4444 Offsite Welding and Joining Requirements.

          - Field:

            - Prior to field welding, submit LANL WPS meeting the requirements of AWS D1.1 for the processes and materials that will be used for welding.  See Section 01 4455 Onsite Welding and Joining Requirements.

- *************************************************************************************************************

- Retain Paragraph below if responsibility for design services have been delegated to (construction) Subcontractor.

- If retaining and Project includes equipment mounted outdoors, retain the portions of subparagraphs pertaining to “wind.”

- If retaining, and Project includes vibration-isolation bases and/or devices, then retain related text in subparagraphs B.2, B.3.b, and/or B.3.c.

- Professional engineer is defined in Section 01 4000 Quality Requirements.

- *************************************************************************************************************

        - Delegated-Design Submittal: For each seismic-restraint device and, as applicable, for each connection type and/ or connection detail associated with providing adequate flexibility.

          - Include design calculations and details for selecting seismic restraints complying with performance requirements, design criteria, and analysis data signed and sealed by the professional engineer, registered in the State of New Mexico, responsible for their preparation.

          - Design Calculations: Calculate static and dynamic loading caused by equipment weight, operation, and seismic [and wind] forces required to select seismic [and wind] restraints [and for designing vibration isolation bases].  [Calculate anticipated differential movement between adjacent structures, or portions of the same structure that may move independently, required to select a type(s) of, and/ or provide a detail(s) for, flexible connection(s).]

            - [Coordinate design calculations with wind load calculations required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.]

*************************************************************************************************************

Retain "Seismic [-and Wind]-Restraint Details" subparagraph below only if seismic design requirements apply but charts on Drawings do not describe seismic restraints in detail. Retaining subparagraph will require Subcontractor to submit seismic-restraint Shop Drawings prepared by a professional engineer. Revise to suit project requirements.

*************************************************************************************************************

          - Seismic[- and Wind]-Restraint Details:

            - Design Analysis: To support selection and arrangement of seismic [ and wind] restraints. Include calculations of combined tensile and shear loads.

            - Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. [Indicate association with vibration isolation devices.

              - Vibration isolators used for component mounting shall comply with the associated “Additional Requirements” in ASCE 7 paragraph 13.6.5.5.]

            - [Coordinate seismic-restraint [and vibration isolation] details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.]

            - Preapproval and Evaluation Documentation: By [an ICC-ES ESR] [OSHPD] [__________], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

          - Details to Provide Adequate Flexibility During a Seismic Event:

            - The portions of the aforementioned “Seismic-Restraint Details” applicable to compliance with the provisions of ASCE 7 Chapter 13 pertaining to “Seismic Relative Displacements” and “differential displacements” shall be provided/ adhered to.

      - INFORMATIONAL SUBMITTALS

************************************************************************************************************

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

- *************************************************************************************************************

        - Coordination Drawings: Show coordination of seismic bracing for electrical components with other systems and equipment in the vicinity, including other supports and seismic restraints. Electrical components include:

          - Control [and monitoring] panels.

          - Generators.

          - Luminaires (not associated with suspended ceilings, or Emergency Lighting).

          - Motor control centers.

          - Panelboards.

          - Photovoltaic system components (not associated with ballasted, roof-mounted systems).

          - Substations.

          - Switchboards.

          - Switchgear.

          - Transformers.

          - Unit substations.

- *************************************************************************************************************

- Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 01 4000, Quality Requirements.

- *************************************************************************************************************

        - Qualification Data: For professional engineer.

- *************************************************************************************************************

- Retain "Welder Performance Qualification Records” Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Control" Article.

- *************************************************************************************************************

        - Welding certificates.

        - Field quality-control reports.

      - QUALITY CONTROL

- ************************************************************************************************************

- Quality Control (QC) is what is contained herein, and is the responsibility of the Subcontractor.

- Quality Assurance (QA, which is required by IBC chapter 17) is contained in the EOR’s Statement of Special Inspections (SSI), and is the responsibility of LANL (i.e., execution of the SSI).  The SSI template is found in ESM Chapter 16, Section IBC-IP, Attachment B.

- ************************************************************************************************************

        - Comply with seismic-restraint requirements in the IBC unless requirements in this Section are more stringent.

************************************************************************************************************

Retain appropriate subparagraphs(s) under “Welder Quals” paragraph if shop and /or field welding is required. If retaining, also retain "Welding Certs" Paragraph in "Informational Submittals" Article.

- ************************************************************************************************************

        - Welding Qualifications:

          - Shop.

            - Prior to shop welding, submit WPQR certification for each welder stating the type of welding and positions qualified for, the code and procedure qualified under, date qualified, and the firm and individual certifying the qualification tests. See Section 01 4444 Offsite Welding and Joining Requirements.

              - If the qualification date of the welding operator is more than 180 days old, the welding operator's qualification certificate must be accompanied by a current certificate by the welder attesting to the fact that he has been engaged in welding since the date of certification, with no break in welding service greater than 6 months.

          - Field.

            - Refer to Section 01 4455, Onsite Welding and Joining Requirements.

        - Seismic-restraint devices shall have horizontal and vertical load testing and analysis. They shall bear preapproval from OSHPD (i.e., “OPA #”), preapproval by ICC-ES (i.e., ESR #), or preapproval by a similar agency, showing maximum seismic-restraint ratings. Ratings based on independent testing are preferred to ratings based on calculations. If preapproved ratings are not available, submittals based on independent testing are preferred. Calculations (including combining shear and tensile loads) that support seismic-restraint designs must be signed and sealed by a professional engineer registered in the State of New Mexico.

        - Comply with NFPA 70.

- PRODUCTS

************************************************************************************************************

Edit the following Article in accordance w/ the same one (i.e., “Seismic Performance Requirements”) in the “component-specific Section (i.e., 26 XXXX),” and indicate that section number and title.

- For “non-critical components (i.e., Component Importance Factor, Ip, = 1.0),” the phrase “position retention” herein is shorthand for the definition of “withstand” therein.

- For DSS (i.e., Ip = 1.5) the phrase “fully operational” herein is the same as that used in the definition of “withstand” therein.

Add on to/ delete Paragraph A and/or B as applicable.

- ************************************************************************************************************

      - SEISMIC PERFORMANCE REQUIREMENTS

        - Per the Article, “Seismic Performance Requirements” in Section 26 [____] [_____________], the design of the seismic restraints shall ensure that position retention of the component/ system is achieved.

        - Per the Article, “Seismic Performance Requirements” in Section 26 [____] [_____________], the design of the seismic restraints shall ensure that position retention of the component/ system is achieved and, to the extent that’s applicable*, that the component is fully operational.

- *Refer to ASCE 7 paragraph 13.6.4, and the portions of paragraph 13.6.5 pertaining to “Ip = 1.5” and “certified” equipment.

- *************************************************************************************************************

- If the “Delegated-Design Submittal” in PART 1 was retained, retain the following Article, and edit its Paragraphs as applicable to Project.

- If retaining Paragraph A, edit options based on project requirements and ESM Chapter 5 Section II, “Section 1609 Wind Loads.”

- If retaining Paragraph B, edit options based on project requirements and ESM Chapter 5 Section II, “Section 1613 Earthquake Loads.” Add to this paragraph as required to capture all of the components requiring restraint.

- *************************************************************************************************************

      - DESIGN CRITERIA

        - Wind Restraint:  Design loads shall be determined in accordance with IBC Section 1609 and the following parameters:

          - Building Risk Category: [I] [II] [III] [IV].

          - Ultimate Design Wind Speed, Vult, miles per hour (mph): [105] [115] [120].

          - Exposure Category: Exposure C.

        - Seismic Restraint:  Design loads shall be determined in accordance with IBC Section 1613 and the following parameters:

          - Building Risk Category: [I] [II] [III] [IV].

          - Site Class: D.

          - Design Spectral Response Acceleration at Short Periods, SDS, gravity (g): [0.75] [____].

          - Design Spectral Response Acceleration at 1.0-Sec. Period, SD1, gravity (g): [0.64] [____].

          - Seismic Design Category: D.

************************************************************************************************************

Regarding the “Ip subparagraph" below, per ASCE 7 paragraphs 13.2.3 & 13.6.6, design and detailing as DSS (i.e., Ip = 1.5) might be required for components that otherwise seem/ appear to be unessential/ noncritical (i.e., Ip = 1.0).

- ************************************************************************************************************

          - Component Importance Factor, Ip: [1.0] [1.5].

************************************************************************************************************

Regarding the “Rp subparagraph" below, per ASCE 7 paragraph 13.1.4, 6.0 is the maximum value that can be used to determine the force in an attachment.  This provision only pertains to components w/ Rp > 6.0.

- ************************************************************************************************************

          - Component Response Modification Factor, Rp: [1.5] [2.0] [2.5] [3.0] [6.0].

          - Component Amplification Factor, ap: [1.0] [2.5]

      - RESTRAINT CHANNEL BRACINGS

        - Description: MFMA-4, shop- or field-fabricated bracing assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end, with other matching components, and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

      - RESTRAINT CABLES

        - Restraint Cables: [ASTM A603] [ASTM A492] steel cables with end connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for restraining cable service; with a minimum of two clamping bolts for cable engagement.

      - SEISMIC-RESTRAINT ACCESSORIES

************************************************************************************************************

Retain "Hanger-Rod Stiffener" paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings. Use with either channel- or cable-type bracing assemblies when required to counter seismic forces. Detail fabrication and indicate locations on Drawings.

- ************************************************************************************************************

        - Hanger-Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

        - Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [rigid channel bracings] [and] [restraint cables].

        - Bushings for Floor-Mounted-Equipment Anchorage: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchors and studs.

        - Bushing Assemblies for Wall-Mounted-Equipment Anchorage: Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

        - Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

      - POST-INSTALLED CONCRETE AND GROUTED-MASONRY ANCHORS

        - Furnish post-installed expansion, adhesive, and undercut concrete and grouted-masonry anchors as indicated on the Drawings and in Section [05 0521, Post Installed Concrete Anchors – High Confidence] [and/or] [05 0520, Post Installed Concrete and Grouted-Masonry Anchors – Normal Confidence].

      - FLEXIBLE CONNECTIONS

        - Permissible products include those that permit rotational and/ or translational movement without degradation of performance.  Examples include universal joints, bellows expansion joints, and flexible metal hose.

- EXECUTION

      - EXAMINATION

        - Examine areas and equipment to receive [vibration isolation and] seismic-control devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for reinforcement and cast-in-place anchors to verify actual locations before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATIONS

        - Multiple Raceways or Cables: Secure raceways and cables to trapeze member with clamps approved for application by [an ICC-ES ESR] [OSHPD] [_____________].

************************************************************************************************************

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual raceways, bus duct, cable trays, and hanger rods for trapeze hangers require hanger-rod stiffeners.

- ************************************************************************************************************

        - Hanger-Rod Stiffeners: Install hanger-rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods caused by seismic forces.

        - Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength will be adequate to carry present and future static and seismic loads within specified loading limits.

        - Equipment:  Each equipment item shall be installed such that it is entirely located and attached on one side only of a building expansion or seismic-control joint.

- *************************************************************************************************************

- In the following paragraph, retain the subparagraph if applicable to project.  If this subparagraph is retained, and Delegated Design isn’t applicable to project (ref. “Action Submittals” in PART 1), the calculations and drawing detail(s) associated w/ ASCE 7 paragraph 13.6.6 must be provided by the EOR.

- *************************************************************************************************************

        - Distribution/ Distributed Systems:  Where raceways (e.g., conduits, cable trays, busways, etc.) cross building expansion or seismic-control joints, pass from one building to another, or pass from one floor/ story of a building to another, or connect to other nonstructural components that aren’t braced/ rigidly mounted, flexible connections shall be installed.

          - [For utility / service lines passing from one building to another, or between portions of the same building that may move independently, flexibility shall be provided per the associated drawing detail(s).]

      - SEISMIC-RESTRAINT DEVICE INSTALLATION

        - Coordinate the location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in Section 03 3001, Reinforced Concrete.

        - Equipment and Hanger Restraints:

          - Install resilient, bolt-isolation washers on equipment anchors where clearance between anchor and adjacent surface exceeds 0.125 inch.

          - Install seismic-restraint devices using methods approved by [an ICC-ES ESR] [OSHPD] [_______] providing required submittals for component.

        - Install cables so they do not bend across edges of adjacent equipment or building structure, and such that they are taught (i.e., without slack) when the component they are to control/ restrain is “at rest.”

        - Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

        - Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

        - Seismic Restraint of Conduit:

          - Conduit offsets, loops, anchors, and guides shall be installed as required to provide specified motion capability and limit motion of adjacent distribution systems.

          - Provide appropriately-sized openings in walls, floors, and ceilings for anticipated seismic movement.  Provide fire seal systems in fire-rated walls where applicable.

        - Seismic Restraint of Electrical Services.

          - Provide appropriately-sized openings in walls, floors, and ceilings for anticipated seismic movement.  Provide fire seal systems in fire-rated walls where applicable.

        - Seismic Restraint of Lighting Fixtures in Buildings:

          - Assembly Mounted on Outlet Box:  A supporting assembly, that is intended to be mounted on an outlet box, shall be designed to accommodate mounting features on 4-inch boxes, plaster rings, and fixture studs.

      - FIELD QUALITY CONTROL

*************************************************************************************************************

- The primary purpose of the Article is to alert the Subcontractor that he/she is responsible for quality control (QC) and that, in addition to QC, the ceiling is subject to the quality assurance (QA) indicated in the Project’s Statement of Special Inspections.
*************************************************************************************************************

        - Inspection Agency: Engage a qualified inspection agency to perform inspections.

        - Perform inspections, with the assistance of a factory-authorized service representative(s) as necessary/ required, during the installation (to include anchorage where applicable) of the systems, equipment, etc. associated with/ affected by this Section (i.e., 26 0548.16) as necessary to ensure that the applicable provisions of ASCE 7 Chapter 13 are met.

        - Prepare an inspection report.

        - Seismic controls will be considered defective if the affected systems, equipment, etc. do not pass the inspections indicated in the Project’s Statement of Special Inspections.

      - ADJUSTING

        - Adjust restraints to permit free movement of equipment within normal mode of operation.

END OF SECTION

******************************************************************

Do not delete the following reference information.

******************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 0548.16 Rev. 0, dated March 30, 2017.