SECTION 26 0553

Identification for electrical systems

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project - and specifiers’ notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality requirements.
*************************************************************************************************************

GENERAL

Section Includes

*************************************************************************************************************
Edit the following articles to match project requirements; delete articles not applicable to Project.

*************************************************************************************************************

Component identification tags

Equipment nameplates

Switch or Receptacle labels

Wire markers

Voltage markers

Warning signs

Arc flash and shock hazard warning labels

Working space markers

One-line diagrams and operating instructions

SUBMITTALS

Submit the following:

Catalog Data: Submit manufacturer’s catalog literature for each product.

Submit electrical identification schedule including list of wording, symbols, letter size, color coding, tag number, location, and function.

*************************************************************************************************************

Include the following paragraph for submission of samples for selection of finish, color, texture, and other properties.

*************************************************************************************************************

Samples:

Submit [two] [________] samples of each type of printed identification products applicable to project.

Submit [two] [________] nameplates illustrating materials and engraving quality.

Manufacturer's Installation Instructions: Submit installation instructions, indicating special procedures and installation requirements.

REGULATORY REQUIREMENTS

Conform to requirements of the National Electrical Code (NEC), NFPA 70E, and 10CFR851.

Conform to applicable requirements of the following ANSI Standards:

Z535.1 Safety Color Code.

Z535.2 Environmental and Facility Safety Signs.

Z535.3 Criteria for Safety Symbols and Labels.

Z535.4 Product Safety Signs and Labels.

Z535.5 Safety Tags and Barricade Tapes (for Temporary Hazards).

Coordination

Coordinate identification names, abbreviations, colors, and other features with requirements in the Subcontract Documents, Shop Drawings, and manufacturer's wiring diagrams with those required by codes, standards, and 29CFR1910.145. Use consistent designations throughout Project.

Verify electrical equipment designations with LANL through the Subcontract Technical Representative.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

************************************************************************************************************

Edit the following article to match project requirements; delete if not applicable to the Project.  Provide a schedule for component identification tags on the Drawings. Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

************************************************************************************************************

  - Component Identification TAGS

Furnish component identification tags as specified below [and scheduled on the Drawings] to identify electrical equipment using the system designation, equipment identification, tech area number, and building number.

Coordinate electrical component identification tag schedule with final equipment identification scheme for project.

Provide component identification tags with black letters on yellow background with 2 inches by 3 inches dimensions.

Provide minimum 48 point size lettering.

Provide tags made of one of the following materials:

Type 1 (Indoor Applications Only):

Laminated plastic adhesive tape with machine printed letters.

Manufacturer: Brother, Seton, Brady.

Type 2:

Two-ply plastic nameplate with letters engraved through yellow surface showing black core.

Provide UV stabilized material for outdoor applications.

Manufacturer: Seton Nameplate Corp.

*************************************************************************************************************

Edit the following article to match project requirements; delete if not applicable to the Project.  Provide a schedule for equipment nameplates on the Drawings. Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

*************************************************************************************************************

  - EQUIPMENT NAMEPLATES

Furnish equipment nameplates as specified below [and scheduled on the Drawings] to indicate the following information:

Category I nameplates:

Supplied by nameplates: circuit directory information including circuit number, equipment identification, location of equipment supplying the item, and the circuit voltage (e.g., 480Y/277V, 480V 3Ø, 208Y/120V, 120/240V).

Supplies nameplates: circuit directory information including circuit number, equipment identification, location of equipment being supplied, and the circuit voltage (e.g. 480Y/277V, 480V 3Ø, 208Y/120V, 120/240V).

Category II nameplates – general or operational information including basic instructions or specific operating procedures.

Category III nameplates – emergency operations information including emergency shutdown procedures.

Coordinate equipment nameplate schedule with equipment numbering scheme provided on the drawings, or by the Subcontract Technical Representative.

Provide nameplates made of one of the following materials:

Type 1 (Indoor Applications Only):

Laminated plastic adhesive tape with machine printed letters.

Manufacturer: Brother, Seton, Brady.

Type 2:

Two-ply plates with letters engraved through surface color showing core color.

Use UV stabilized material for outdoor applications.

Manufacturer: Seton Nameplate Corp.

Provide 10-point-minimum size lettering.

Provide colors as follows:

Category I nameplates: white or black letters on blue background.

Category II nameplates: white letters on black background.

Category III nameplates: white or black letters on red background.

Dimensions shall be as follows:

Category I nameplates: 1 inch by 2 1/2 inch minimum.

Category II nameplates: as required for instructions, 1 inch by 2 1/2 inch minimum.

Category III nameplates: as required for instructions, 1 inch by 2 1/2 inch minimum.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if not applicable to the Project.  Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

*************************************************************************************************************

  - switch AND receptacle LABELS

Furnish a typewritten or machine printed label for each switch and receptacle indicating circuit number, panelboard, and voltage.

Provide labels of the following materials:

Laminated plastic adhesive tape with machine printed letters.

Manufacturer: Brother, Seton, Brady.

Provide black, 10-point-minimum size lettering on a white background.

  - WIRE MARKERS

Provide wire markers for power, control, instrumentation, alarm, and communication circuit wires that indicate the panel and circuit designation

Furnish split sleeve, heat-shrinkable sleeve, or self-laminating adhesive wire markers.

Locate a wire marker on each conductor at each termination and splice point.

Manufacturer: Brady, Panduit, LEM Products, Inc.

  - VOLTAGE MARKERS

Furnish voltage markers, as required, to identify voltages present in equipment

For medium voltage, in addition to the above, furnish voltage markers for pull boxes and raceways.

Provide flexible pressure sensitive vinyl markers with minimum 1 inch X 4 inches orange background and black letters.

Provide voltage markers with lettering indicating all voltages present:

120 or 208Y/120

120, 240, or 120/240

480 or 480Y/277

13.2 kV or 13.8 kV

Fire alarm system: FIRE ALARM

Telephone/data system: TELEPHONE

Manufacturer: Electromark, LEM Products, Inc.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if not applicable to the Project.

*************************************************************************************************************

  - Emergency system Identification

Furnish identification for emergency system components as required below and by NEC Article 700.

note: ThE FOLLOWING PARAGRAPH only applies to emergency systems.  It does not apply to legally required standby or optional standby systems.

Provide flexible pressure sensitive vinyl markers with minimum 1 inch X 4 inches orange background and black letters indicating EMERGENCY SYSTEM.

*************************************************************************************************************
Edit the following article to match project requirements; delete if not applicable to the Project.  Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.
*************************************************************************************************************

  - ARC FLASH and shock Hazard WARNING LABELS

Furnish arc flash and shock hazard warning labels, as indicated in approved construction documents.

Provide warning labels that comply with ANSI Z535.4.  The color in top part of WARNING labels shall be ANSI “safety orange.”  The color in top part of DANGER labels shall be red. Lettering on labels shall be black.

Provide either machine-produced custom labels or manually filled-in pre-printed labels that meet the requirements below.

Label dimensions shall be approximately 4 inches high by 6 inches wide.

Outdoor labels shall be suitable for a high-UV environment.

Machine-produced custom labels:

Use polyester label stock that is NRTL-recognized to UL969, Marking and Labeling Systems, and has a high-adhesion adhesive back.

Use printing ribbon recommended by the label stock manufacturer.

Use a suitable thermal transfer process label-printing machine to generate labels and enter the application-specific information indicated in the installation sub-paragraphs.

Pre-printed labels:

Use labels printed on self-adhesive UV-resistant polyester with pressure-sensitive adhesive back. Provide labels with a clear polyester overlay film to protect manually-entered information.

Use a black, UV-resistant, industrial permanent marker pen to legibly hand letter the application-specific information indicated in the installation sub-paragraphs.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not applicable. Use Arc Flash and Shock Hazard Warning Label Design #1 where the calculated incident energy does not exceed 40 cal/cm2.

*************************************************************************************************************

Use Arc Flash and Shock Hazard Warning Label Design #1 for equipment where the calculated arc flash incident energy does not exceed 40 cal/cm2. See installation sub-paragraphs for an explanation of the application-specific information entries on the label.

Arc Flash and Shock Hazard Warning Label — Design #1

WARNING

Arc Flash and Shock Hazard. Appropriate PPE Required.

## inches Arc Flash Protection Boundary. (Arc flash hazard analysis based on: SWGR-A main circuit breaker set in energy-reducing maintenance mode. ) ##.# cal/sq cm Arc flash incident energy at ## inches working distance ### V Shock Hazard exists when personnel are exposed to energized electrical conductors or circuit parts. ## inches Limited Approach Boundary. ## inches Restricted Approach Boundary

Equipment I.D.: ######-##-####-# Date of Analysis: MM/DD/YYYY . ##,### A Maximum Available Fault Current (RMS symmetrical amperes).

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not applicable.  Use Shock Hazard Warning Label Design #2 for equipment operating at a nominal system voltage less than 240 volts, from a transformer with a rating less than 125 kVA.

*************************************************************************************************************

Use Shock Hazard Warning Label Design #2 for equipment operating at a nominal system voltage less than 240 V and fed by a transformer with a rating less than 125 kVA. See installation sub-paragraphs for an explanation of the information entries on the label.

Arc Flash and Shock Hazard Warning Label — Design #2

WARNING

Shock Hazard only. Shock hazard PPE Required Arc Flash PPE not required

This equipment operates at a nominal system voltage of less than 240 VAC and is fed from a transformer with a rating less than 125 kVA. No arc flash hazard. Arc rated PPE is not required. XX Shock Hazard exists when personnel are exposed to energized electrical conductors or circuit parts. 42 inches Limited Approach Boundary. ## inches or ‘avoid contact’ Restricted Approach Boundary.

*************************************************************************************************************

Edit the following paragraph to match Project requirements; delete if not applicable. Use Arc Flash and Shock Hazard Warning Label Design #3 where the calculated incident energy exceeds 40 cal/cm2.

*************************************************************************************************************

Use Arc Flash and Shock Hazard Warning Label Design #3 for equipment where the calculated arc-flash incident energy is greater than 40 cal/cm2. See installation sub-paragraphs for an explanation of the application-specific information entries on the label.

Arc Flash and Shock Hazard Warning Label — Design #3

DANGER

Lethal Arc Flash and Shock Hazard. Mode 1,2, or 3 Work requires an EEWP

## inches Arc Flash Protection Boundary. ##.# cal/sq cm Arc flash incident energy at ## inches working distance. ### V Shock Hazard when personnel are exposed to energized electrical conductors or circuit parts. ## inches Limited Approach Boundary. ## inches Restricted Approach Boundary.

Equipment I.D.: ######-##-####-# Date of Analysis: MM/DD/YYYY . ##,### A Maximum Available Fault Current (RMS symmetrical amperes).

Manufacturer: Summit Electric Supply, Seton Name Plate Co., Safety Label Solutions, Hazard Communication Systems, Electromark, Brady.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if not applicable to the Project.  Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

*************************************************************************************************************

  - Working Space floor MARKING

Provide black paint and white paint to mark the NEC-required working space on the floor at electrical equipment, if shown on drawings.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if not applicable to the Project.

*************************************************************************************************************

Working Space Labels

Provide labels indicating required working clearance at switchgear, switchboards, panelboards, and other equipment as shown on drawings.

Material:

Use polyester label stock that is NRTL-recognized to UL969, Marking and Labeling Systems, and has a high-adhesion adhesive back.

Use printing ribbon recommended by the label stock manufacturer.

Use a suitable thermal transfer process label-printing machine to generate labels and enter the application-specific information

Outdoor labels shall be suitable for a high-UV environment.

Minimum dimensions: 3-1/2 x 1-1/4 inches.

Use the following label design:

NOTICE

Keep area in front of this electrical equipment clear for #-#/# feet.

Signal word: “NOTICE” in 24-point-minimum white italic letters on safety blue panel.

Word message: 16-point-minimum black or safety blue letters on white background.  The number of feet is given by the following table.

************************************************************************************************************
Edit Table 1 to match Project requirements; delete any that do not apply to Project. Verify voltages in specialized equipment installed as part of the Project.

************************************************************************************************************

Table 1-WSL

| Equipment Hazard | Number of Feet for Word Message |
| --- | --- |
| 120/240V and 208Y/120V | 3 |
| 480V and 480Y/277V with exposed live parts on one side of the working space and no live parts on the other side of the working space | 3-1/2 |
| 480V and 480Y/277V with exposed live parts on both sides of the working space | 4 |
| 4160Y/2400V with exposed live parts on one side of the working space and no live parts on the other side of the working space | 4 |
| 4160Y/2400V with exposed live parts on both sides of the working space | 5 |
| 13,200V with exposed live parts on one side of the working space and no live parts on the other side of the working space | 5 |
| 13,200V with exposed live parts on both sides of the working space | 6 |

Manufacturer: Brother, Seton, Brady

*************************************************************************************************************
Include this article for indoor major pieces of equipment, such as switchgear and switchboards.

*************************************************************************************************************

  - One-Line Diagram CabinetS

Provide aluminum framed bulletin board cabinet(s) to display electrical one-line diagram(s) plus special operating instructions and emergency procedures as shown on Drawings.

Housing: extruded aluminum with manufacturer’s standard outside dimensions of approximately [36" x 48"][36" x 60"][48" x 60"][48" x 72"] x 3” deep.

Doors: two sliding 3/16” tempered glass doors with ground-in finger pulls and flat key tumbler locks.

Back panel: tackable cork.

Finishes: manufacturer’s standard finishes and colors.

Manufacturer: Claridge “Imperial Series”

EXECUTION

*********************************************************************************************************

Delete this article when existing construction is not affected.  Edit to match project requirements.

*********************************************************************************************************

  - EXAMINATION

Examine surfaces to receive identification products for compliance with installation tolerances and other conditions affecting performance of the identification products.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION - General

Where identification is to be applied to surfaces that require finish, install identification after completion of finish work.

Install labels where indicated and at locations for best convenience of viewing without interference with operation and maintenance of equipment.

Coordinate installation of identifying devices with location of access panels and doors.

Where the required labels do not fit on the face of the equipment, labels may be placed on a plate immediately adjacent to or above the equipment.

Install electrical identification products only when ambient temperature and humidity conditions for adhesive are within range recommended by manufacturer.

Clean surface where electrical identification product is to be placed.

Use manufacturer's recommended adhesive for engraved tags and nameplates.

************************************************************************************************************

Edit the following articles to match project requirements; delete any that do not apply to Project.  Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

************************************************************************************************************

Component Identification Tags

Install component identification tag on the front of each piece of electrical equipment as indicated on the Drawings.

Position tags so they can be read from floor or ground.

Equipment Nameplates

Install equipment nameplate or nameplates on the front of each piece of electrical equipment as indicated on the Drawings.

************************************************************************************************************

Edit the following articles to match project requirements; delete any that do not apply to Project.

************************************************************************************************************

Important Equipment: Install a Category III nameplate at the branch circuit breaker(s) that provide(s) AC power to the following equipment per Table 2-IEN.

Table 2-IEN

| Important Equipment Type | Branch Circuit Breaker(s) Nameplate Wording |
| --- | --- |
| Fire alarm control panel | WARNING – AC POWER TO FIRE ALARM CONTROL PANEL – DO NOT TURN OFF WITHOUT AUTHORIZATION |
| Other life safety system components | WARNING – AC POWER TO LIFE SAFETY SYSTEM – DO NOT TURN OFF WITHOUT AUTHORIZATION |
| Other safety systems | WARNING – AC POWER TO SAFETY SYSTEM – DO NOT TURN OFF WITHOUT AUTHORIZATION |
| Security system components | WARNING – AC POWER TO SECURITY SYSTEM – DO NOT TURN OFF WITHOUT AUTHORIZATION |

Position nameplates so they can be read from floor or ground.

switch or receptacle Labels

Install label on outside of device cover for each receptacle and light switch.

Wire Markers

Install wire markers on power, control and communication conductors at each termination or splice point

Voltage Markers

Install voltage markers at the following locations and position markers so they can be read from floor or ground:

************************************************************************************************************

Edit the following articles to match project requirements; delete any that do not apply to Project.

************************************************************************************************************

Front and rear of each medium-voltage switchgear assembly.

Front and rear of each free-standing low- voltage switchgear or switchboard section.

Front of each transformer, switchgear, switchboard, panelboard, industrial control panel, starter, VFD, motor control center, enclosed circuit breaker, safety switch, and cabinets, including those furnished with mechanical equipment.

Cover of each pull box containing medium-voltage conductors.

Raceways containing medium-voltage conductors.  Space markers not more than 20 feet on center.

************************************************************************************************************

Edit the following article to match project requirements; delete if not applicable to Project. Note: A system is only “Emergency” if it is defined as such by the Authority Having Jurisdiction.  In this case, it must meet the requirements of NEC Article 700.  Other systems are either “Legally Required Standby” per NEC Article 701 or “Optional Standby” per NEC Article 702.

************************************************************************************************************

Emergency System Identification

Install identification for emergency system markers at the following locations and position markers so they can be read from floor or ground:

Front of each emergency system generator.

Front and rear of each free-standing emergency system switchgear or switchboard section.

Front of each low-voltage transformer, panelboard, industrial control panel, motor control center, enclosed circuit breaker, safety switch, and motor controller enclosure, including those furnished with mechanical equipment.

Cover of each pull box and junction box containing emergency system conductors.

Each emergency system conduit longer than 6 feet; space markers not more than 20 feet on center.

The front or cover plate of each receptacle supplied from the emergency system.

Arc Flash and shock hazard Warning Labels

Install arc-flash and shock-hazard warning labels at all locations, as shown on the Drawings.

Working Space Floor Markers

Install floor marking paint on the floor at the locations as shown on Drawings.

Dimensions of working space area shall be as follows:

Width: the greater of the width of the equipment or 30 inches.

Depth:  The same number of feet as required by the Working Space label wording in Table 1-WSL in PART 2 above.

Thoroughly prepare floor surface to receive paint.

Paint the NEC-required working space area with alternating 3 to 6 inch wide black and white diagonal stripes.

************************************************************************************************************

Edit the following articles to match project requirements; delete if not applicable to the Project.  Use working space labels only where it is impractical to mark the NEC-required working space on the floor (e.g., carpeted areas). Refer to LANL ESM Chapter 7 Section D5000 Part 7.0.

************************************************************************************************************

Working Space Labels

Install working space labels on switchgear, switchboards, panelboards, and where shown on drawings

Position labels so they can be read from floor or ground.

One-Line Diagram Cabinet(s)

Install one-line diagram cabinet(s) in the locations shown on drawings

************************************************************************************************************

Edit the following articles to match project requirements; delete any that do not apply to Project.

************************************************************************************************************

END OF SECTION

**********************************************************************************************************

Do not delete the following reference information.

**********************************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0553 Rev. 3, dated February 2, 2017.