SECTION 26 0700

INDUCTION Motors – 500hp and smaller

*******************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic:  If the motor isn’t exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this Section to be Project-specific, refer to Sections 26 0548.16, Seismic Controls for Electrical Systems, and 01 8734, Seismic Qualification of Nonstructural Components (IBC), as applicable.

*******************************************************************************************************

GENERAL

Section Includes

Section includes single- and three-phase induction motors rated 500 horsepower and smaller and 600 volts and less for application on equipment provided under other sections, and motors furnished loose to Project.

Section does not address motors intended for used in hazardous locations as defined in the National Electrical Code, or as required by DOE-STD-1212, Explosives Safety.

Section does not address sealed (hermetic-type) motor-compressor parts.

Section does not address special-purpose motors such as for submersible pumps.

*************************************************************************************************************

Seismic: If the motor is exempt from seismic design then delete both of the following subparagraphs.

- Otherwise, see the seismic-portion of the previous author note.

*************************************************************************************************************

  - RELATED SECTIONS

    - Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements.

    - Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

Quality Assurance

Comply with the National Electrical Code (NEC) for installation requirements

Motors shall be listed and labeled by a Nationally Recognized Testing Laboratory (NRTL)

UL 1004-1, Standard for Rotating Electrical Machines - General Requirements

UL 1004-2, Standard for Impedance Protected Motors

UL 1004-3, Standard for Thermally Protected Motors

UL 1004-5, Standard for Fire Pump Motors

UL 1004-8, Standard for Inverter Duty Motors

SUBMITTALS

Submit the following in accordance with project submittal procedures.

Action Submittals

Catalog Data: Submit catalog data for each motor furnished loose. Indicate nameplate data, standard compliance, electrical ratings and characteristics, and physical dimensions, weights, mechanical performance data, and support points.

Calculations: Motor selection calculations including brake horsepower of the load, ambient temperature range at the motor location, and characteristics of moving air stream (if any) at the motor location.

*************************************************************************************************************

Edit the following sections to meet job requirements.  Delete para. 4 if test reports are not necessary.  Delete para. 6 if field inspections and tests are not warranted.

*************************************************************************************************************

Certification: Submit certification that motors meet specified performance, efficiency, and selection requirements.

Test Reports: Submit procedures and results for factory testing.

Installation instructions including handling, storage, setting, mechanical connections, lubrication, wiring, and testing.

Records of field inspections and tests for each motor.

Closeout Submittals

Operation and maintenance data:

        - Operation data including instructions for safe operating procedures.

        - Maintenance data including assembly drawings, bearing data with replacement sizes, and lubrication instructions.

SERVICE CONDITIONS

    - Motors shall perform satisfactorily in the following service conditions:

      - Elevation: 7,500 feet above sea level.

      - Maximum ambient temperature: 104 degrees F.

      - Minimum ambient temperature: -20 degrees F.

*************************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*************************************************************************************************************

      - Maximum solar heat gain: 110 W/sq. ft.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1—Standard Practices for Good Workmanship in Electrical Construction (ANSI), and NECA 230—Standard for Selecting, Installing, and Maintaining Electric Motors and Motor Controllers (ANSI).

Upon delivery of motors to site, inspect thoroughly for damage.

Store, protect and handle motors following manufacturer’s instructions.  Provide slings and spreader bars as required.  Lift only with lugs provided. Do not lift motors using shaft as an attachment point.

Protect products from weather and moisture by covering with plastic or canvas and by maintaining heating within enclosure.

For extended outdoor storage, remove motors from equipment and store separately.

PRODUCTS

*************************************************************************************************************

For motors that are not exempt from seismic, if Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted, follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************

Seismic: Delete article 2.2 if motors are exempt from seismic design.

Otherwise retain the section and edit its content based on the following:

- 1st paragraph is for motors that do not have to operate/ function post-seismic-event.

- 2nd paragraph is for motors that must operate/ function after a seismic event (i.e., a Designated Seismic System, or DSS).

- If paragraph applies, the “E” drawings for the motors shall also state that the motors are Designated Seismic Systems

If paragraph applies, edit it in accordance with content of 26 0548.16 and/or 01 8734.

*************************************************************************************************************

  - SEismic Performance requirements

    - The motors shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

    - The motors are Designated Seismic Systems and, as such, shall remain in place and be fully operational following the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

  - MANUFACTURERS

Baldor

Emerson Motors

GE Motors

Siemens

TECO-Westinghouse

  - GENERAL CONSTRUCTION AND REQUIREMENTS

Motors less than ¼ HP, for general applications, may be equipment manufacturer's standard product and need not conform to these specifications, unless otherwise required.

Provide NRTL-listed motors with electrical and mechanical performance in accordance with NEMA MG-1, Motors and Generators, unless specified otherwise in this Section.

********************************************************************************************************

Edit the following article to match project requirements.

********************************************************************************************************

Enclosure

For NEMA frame motors, provide motors that conform to IEEE 841.  In the event that any part of this specification is in conflict with IEEE 841, IEEE 841 shall prevail.

For non-NEMA frame motors, provide type as shown on drawings

Provide 240 volt space heaters in motors, if indicated on the Drawings.

Rating

Motors shall be rated for continuous-duty, unless otherwise specified

De-rate motors for operation at 7500 feet altitude in accordance with NEMA MG-1.  Do not use motor service factor to compensate for altitude.  Refer to motor selection table below.

Nameplates:

Each motor shall have a stainless steel nameplate indicating information required by the NEC and NEMA MG-1.

Additional nameplate information may be required by other sections in this specification

Attach nameplates to motor frame with stainless steel fasteners.

Wiring Terminations:

Terminal lugs shall match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in a terminal box sized to the NEC, and threaded for conduit.

For fractional horsepower motors where connection is made directly, provide conduit connection in end frame.

There shall be a screw or lug inside terminal cover or terminal box for connection to an Equipment Grounding Conductor.

Motors shall meet NEMA MG-1 noise level standards.

  - SINGLE PHASE POWER – SPLIT PHASE MOTORS

Use single-phase power, split phase motors where shown on approved construction documents.

Split phase motors shall have the following characteristics:

Starting Torque: Less than 150 percent of full load torque.

Breakdown Torque: Approximately 200 percent of full load torque.

Insulation: Class A (60 deg C temperature rise) or better.

Service Factor: Minimum of 1.35 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

  - SINGLE PHASE POWER – PERMANENT-SPLIT CAPACITOR MOTORS

Use single-phase power, permanent split capacitor motors where shown on approved construction documents.

Permanent split capacitor motors shall have the following characteristics:

Starting Torque: Exceeding 1/4 of full load torque.

Multiple Speed: Through tapped windings.

Insulation: Class A (60 deg C temperature rise) or better.

Service Factor: 1.0

Bearings: Pre-lubricated ball or sleeve bearings.

Integral Protection: Automatic reset overload protector.

  - SINGLE PHASE POWER – CAPACITOR-START MOTORS

Use single-phase power, capacitor-start motors where shown on approved construction documents.

Capacitor-start motors shall have the following characteristics:

Starting Torque: 3 times full load torque.

Pull-up Torque: Up to 350 percent of full load torque.

Breakdown Torque: Approximately 250 percent of full load torque.

Motors: Capacitor in series with starting winding. Provide capacitor-start/ capacitor-run motors with 2 capacitors in parallel with run capacitor remaining in circuit at operating speeds.

Insulation: Class A (60 deg C temperature rise) or better.

Service Factor: Minimum of 1.25 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

  - THREE PHASE POWER – SQUIRREL CAGE MOTORS

Use 3-phase power, squirrel-cage, induction motors for applications where shown on approved construction documents.

*************************************************************************************************************

Edit the following article to match project requirements. NEMA design B motors will be used for most centrifugal fan and centrifugal pump applications. Special applications such as positive displacement pumps may require motors with higher starting torque than NEMA Design B.

Delete Section C if tests are not required.

*************************************************************************************************************

3-phase power, squirrel-cage motors shall have the following characteristics:

Starting Torque:  NEMA Design B characteristics.

Locked Rotor Current: NEMA Design B characteristics.

Power Output, Locked Rotor Torque, Breakdown or Pull-Out Torque: NEMA Design B characteristics.

Design, Construction, Testing, and Performance: Conform to NEMA MG 1 for Design B motors.

Insulation System: NEMA Class F or better.

Service Factor: 1.15 minimum.

Test motors in accordance with NEMA MG-1 and IEEE 112, IEEE Standard Test Procedure for Polyphase Induction Motors and Generators.  Each motor shall receive a routine commercial test to verify freedom from electrical or mechanical defects.  Provide prototype test reports for each rating.

Motors shall be NEMA Standard T-Frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

Motors shall have grease lubricated anti-friction ball bearings, with housings equipped with provision for re-lubrication,

The bearings shall have a rated L-10 fatigue life per ANSI/ABMA 9 - Load Ratings and Fatigue Life for Ball Bearings of 150,000 hours for direct-coupled applications and 50,000 hours for belted applications minimum. Belted rating shall be based on radial loads and pulley sizes called out in NEMA MG1. The calculation will be determined from the pulley centerline being at the end of the motor shaft.

Bearing cavities and greasing passages shall be thoroughly cleaned of all debris before lubricating. Motors shall be lubricated at the factory with Exxon Mobil Polyrex™ EM grease, or equal.

Stamp ANSI/ABMA bearing identification number on motor nameplate.

For belted applications, provide an adjustable sliding base; for applications above 10 horsepower, sliding base shall have 2 adjusting bolts.

General purpose, single-speed motors shall be NEMA PremiumTM labeled motors or motors with full-load nominal efficiency not less than that tabulated below when tested in accordance with IEEE Std. 112, subclause 6.4, Method B.

| NOMINAL FULL-LOAD EFFICIENCY |
| --- |
| MOTOR HP | NUMBER OF POLES / SYNCHRONOUS SPEED, RPM |
|  | ODP MOTORS | TEFC MOTORS |
|  | 2 3600 | 4 1800 | 6 1200 | 2 3600 | 4 1800 | 6 1200 |
| 1 | 77.0 | 85.5 | 82.5 | 77.0 | 85.5 | 82.5 |
| 1.5 | 84.0 | 86.5 | 86.5 | 84.0 | 86.5 | 87.5 |
| 2 | 85.5 | 86.5 | 87.5 | 85.5 | 86.5 | 88.5 |
| 3 | 85.5 | 89.5 | 88.5 | 86.5 | 89.5 | 89.5 |
| 5 | 86.5 | 89.5 | 89.5 | 88.5 | 89.5 | 89.5 |
| 7.5 | 88.5 | 91.0 | 90.2 | 89.5 | 91.7 | 91.0 |
| 10 | 89.5 | 91.7 | 91.7 | 90.2 | 91.7 | 91.0 |
| 15 | 90.2 | 93.0 | 91.7 | 91.0 | 92.4 | 91.7 |
| 20 | 91.0 | 93.0 | 92.4 | 91.0 | 93.0 | 91.7 |
| 25 | 91.7 | 93.6 | 93.0 | 91.7 | 93.6 | 93.0 |
| 30 | 91.7 | 94.1 | 93.6 | 91.7 | 93.6 | 93.0 |
| 40 | 92.4 | 94.1 | 94.1 | 92.4 | 94.1 | 94.1 |
| 50 | 93.0 | 94.5 | 94.1 | 93.0 | 94.5 | 94.1 |
| 60 | 93.6 | 95.0 | 94.5 | 93.6 | 95.0 | 94.5 |
| 75 | 93.6 | 95.0 | 94.5 | 93.6 | 95.4 | 94.5 |
| 100 | 93.6 | 95.4 | 95.0 | 94.1 | 95.4 | 95.0 |
| 125 | 94.1 | 95.4 | 95.0 | 95.0 | 95.4 | 95.0 |
| 150 | 94.1 | 95.8 | 95.4 | 95.0 | 95.8 | 95.8 |
| 200 | 95.0 | 95.8 | 95.4 | 95.4 | 96.2 | 95.8 |
| 250 | 95.0 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 300 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 350 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 400 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 95.8 |
| 450 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |
| 500 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |

Do not select motors to operate continuously above rated load in the service factor area.

De-rate motors for operation at 7500 ft. altitude in accordance with the following table, taking into consideration the ambient temperature of the motor environment. Select motor based on 104 degrees F ambient temperature, unless motor is in a moving air stream when operating.

| MAXIMUM MOTOR SHAFT LOADe (bhp) |
| --- |
| Motor Nameplate (hp) | Ambient Temperaturea, b, c (deg F) |
|  | 81.1 | 85 | 90 | 95 | 100 | 104d |
| 1 | 1.00 | 0.98 | 0.95 | 0.92 | 0.89 | 0.87 |
| 1.5 | 1.50 | 1.47 | 1.43 | 1.38 | 1.34 | 1.31 |
| 2 | 2.00 | 1.96 | 1.90 | 1.85 | 1.79 | 1.75 |
| 3 | 3.00 | 2.93 | 2.85 | 2.77 | 2.68 | 2.62 |
| 5 | 5.00 | 4.89 | 4.75 | 4.61 | 4.47 | 4.36 |
| 7.5 | 7.50 | 7.34 | 7.13 | 6.92 | 6.71 | 6.55 |
| 10 | 10.0 | 9.78 | 9.51 | 9.23 | 8.95 | 8.73 |
| 15 | 15.0 | 14.7 | 14.3 | 13.8 | 13.4 | 13.1 |
| 20 | 20.0 | 19.6 | 19.0 | 18.5 | 17.9 | 17.5 |
| 25 | 25.0 | 24.5 | 23.8 | 23.1 | 22.4 | 21.8 |
| 30 | 30.0 | 29.3 | 28.5 | 27.7 | 26.8 | 26.2 |
| 40 | 40.0 | 39.1 | 38.0 | 36.9 | 35.8 | 34.9 |
| 50 | 50.0 | 48.9 | 47.5 | 46.1 | 44.7 | 43.6 |
| 60 | 60.0 | 58.7 | 57.0 | 55.4 | 53.7 | 52.4 |
| 75 | 75.0 | 73.4 | 71.3 | 69.2 | 67.1 | 65.5 |
| 100 | 100 | 97.8 | 95.1 | 92.3 | 89.5 | 87.3 |
| 125 | 125 | 122 | 119 | 115 | 112 | 109 |
| 150 | 150 | 147 | 143 | 138 | 134 | 131 |
| 200 | 200 | 196 | 190 | 185 | 179 | 175 |
| 250 | 250 | 245 | 238 | 231 | 224 | 218 |
| 300 | 300 | 293 | 285 | 277 | 268 | 262 |
| 350 | 350 | 342 | 333 | 323 | 313 | 305 |
| 400 | 400 | 391 | 380 | 369 | 358 | 349 |
| 450 | 450 | 440 | 428 | 415 | 403 | 393 |
| 500 | 500 | 489 | 475 | 461 | 447 | 436 |
| Notes: |  |  |  |  |  |  |
| a. | Select motor based on 104 degrees F ambient temperature unless motor is in a moving air stream when operating. |
| b. | Document selection of an ambient temperature lower than 90 degrees F. |
| c. | Do not extrapolate to ambient temperatures below 81.1 or above 104 degrees F. If the ambient temperature is outside the 81.1 °F to 104 °F range, refer to NEMA MG 1 and/or the motor manufacturer for guidance. |
| d. | If ambient temperature exceeds 104 degrees F, select motor with greater nameplate hp rating in accordance with NEMA MG 1. |
| e. | Motor selection criteria developed from temperature rise considerations in NEMA MG 1, clauses 12.43, 12.51, and 14.4. |

*************************************************************************************************************

Edit the following para to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if no motors are controlled by part-winding starters.

*************************************************************************************************************

Where indicated on Drawings, provide motors suitable for use with part winding starting systems to reduce locked rotor current to approximately 60 percent of full winding locked rotor current while providing approximately 50 percent of full winding locked rotor torque.

*************************************************************************************************************

Edit the following para to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if there are no 2-speed motors.

*************************************************************************************************************

Where indicated on Drawings, provide motors suitable for use in a single winding, variable torque connection for 2 speed fan and centrifugal pump applications.

*************************************************************************************************************

Edit the following para to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if no motors are on adjustable frequency controllers.

*************************************************************************************************************

Where indicated on Drawings, provide motors suitable for use with adjustable frequency controllers as follows:

Provide motors that comply with Part 31 of NEMA MG-1 for use with pulse width modulation (PWM) adjustable frequency AC controllers.

Provide motors that comply with Part 30 or 31 of NEMA MG-1 for use with six step adjustable frequency controllers.

*************************************************************************************************************

Edit the following para to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if not used. Only critical motors warrant winding thermistors.

*************************************************************************************************************

Where indicated on approved construction documents, provide three positive thermal coefficient (PTC) thermistors imbedded in motor windings (one per phase) and solid state control relay for wiring into motor starter.

EXECUTION

*************************************************************************************************************

For motors that are not exempt from seismic, if Project Spec includes 26 0548.16, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

- EXISTING WORK

********************************************************************************************************

Delete this section when existing construction is not affected.

********************************************************************************************************

Maintain access to existing motors and other installations remaining active and requiring access. Modify installation or provide access panel.

If part of the project scope, clean and repair existing motors that are to remain or are to be reinstalled.

- EXAMINATION

    - Examine surfaces to receive motors for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

- INSTALLATION

    - Install motors and accessories in accordance with manufacturer's instructions and NECA 230; have manufacturer’s installation instructions available at the construction site.

Remove any slushing compound on shaft or other parts using a petroleum-type solvent.

Remove shaft shipping braces after motor is placed in its final location.

***************************************************************************************************************

The following paras, D through F, are only for when the electrical subcontractor is responsible for the finished installation.  In most cases, it is the responsibility of the mechanical discipline to install the coupling.

****************************************************************************************************

Install shaft coupling or sheave in accordance with manufacturer’s instructions.  Do not modify motor shaft to accommodate coupling or sheave.

Align the motor shaft with the load shaft. Meet the most stringent of the motor manufacturer’s requirements for shaft alignment, the driven equipment manufacturer’s requirements for shaft alignment, or the following requirements for shaft alignment. The minimum acceptable criteria for motor installation and shaft alignment for motors 10 hp and larger are as follows:

Load and motor casing distortion (soft foot): Not more than 0.002 inch (0.0508 mm) at each foot. Use stainless steel pre-stamped shims as required in bringing soft foot within acceptable limits.

Load and motor shaft runout: Not more than 0.001 inch.  If load shaft exceeds criteria contact the LANL Subcontract Technical Representative (STR). If motor shaft runout exceeds criteria, replace the motor.

Alignment tolerances for coupled shafts with short couplings:

| Speed, rpm | SHAFT OFFSET At center, inch (mm) | ANGULARITY/GAP Inch/10 inches (mm/254 mm) |
| --- | --- | --- |
| 600 | 0.005 (0.1270) | 0.010 (0.2540) |
| 900 | 0.003 (0.0762) | 0.007 (0.1778) |
| 1200 | 0.0025 (0.0635) | 0.005 (0.1270) |
| 1800 | 0.002 (0.0508) | 0.003 (0.0762) |
| 3600 | 0.001 (0.0254) | 0.002 (0.0508) |
| 7200 | 0.0005 (0.0127) | 0.001 (0.0254) |

Alignment tolerances for coupled shafts having couplings with spacers:

| Speed, rpm | SHAFT OFFSET Per inch (25.4 mm) of spacer length |
| --- | --- |
| 600 | 0.0018 (0.0457) |
| 900 | 0.0012 (0.0305) |
| 1200 | 0.0009 (0.0229) |
| 1800 | 0.0006 (0.0152) |
| 3600 | 0.0003 (0.0076) |
| 7200 | 0.00015 (0.0038) |

For belt-driven loads, use string or straight edge alignment of pulley grooves to minimize offset, angle, and twist so belts are not distorted. Verify roundness of pulleys; replace pulleys with total indicator runout exceeding 0.005 inch. Set belt tension as low as possible.

Verify that line voltage and phases agree with motor nameplate.

********************************************************************************************************

Edit the following article to match the current LANL standard specification numbers.

********************************************************************************************************

Connections to motor: Use motor lead splicing kits to insulate and seal connections to leads. Make electrical connections to motors using materials and methods specified in Sections 26 0519, Low Voltage Electrical Power Conductors and Cables and 26 0533, Raceways and Boxes for Electrical Systems. Use flexible conduits for connection.

- FIELD Quality Control

    - Perform the following inspections for all field installed motors:

Verify that motor nameplate data agrees with Drawings and Specifications.

Inspect physical and mechanical condition of motor.

Verify that motor is properly anchored.

Verify that motor is lubricated in accordance with manufacturer’s instructions.

Perform and document the following inspections and tests for all field installed motors that are indicated on the approved construction documents to be driving critical loads:

Witness the torqueing of accessible bolted electrical connections.

Check electrical connections for high resistance using a low-resistance ohmmeter; investigate any values that deviate from similar connections by more than 50 percent.

Perform insulation-resistance tests in accordance with ANSI/IEEE Standard 43; investigate if stator phase-to-phase resistance values deviate by more than 10 percent.

Before energizing motor with driven equipment, verify proper alignment of motor shaft with load shaft.

Verify proper rotation direction as required by the load.

Maintain and submit records of inspections and tests for each motor.

*************************************************************************************************************

Edit the following para to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*************************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813, Electrical Acceptance Testing.

************************************************************************************************************

Edit the following article to match project requirements.  Balance the benefits of start-up services against the cost of the motor and the importance of the load it drives.  Delete the following section if the cost of the manufacturer’s start-up service is not warranted.  Generally, only motors that drive critical loads will require start-up services.

*************************************************************************************************************

- manufacturer’s Start-up Services

    - For motors driving critical loads, provide services of a factory-trained manufacturer’s service representative to verify proper installation and start-up of equipment.

    - Submit certification that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

- project Record Documents

    - Submit the following in accordance with Section 01 7839, Project Record Documents:

Report of field tests showing compliance with and field quality control specified in PART 3 of this specification section.

*************************************************************************************************************

Edit the following section to match project requirements; delete if not needed.  See instructions for MANUFACTURER’S START-UP SERVICE article of this Section.

*************************************************************************************************************

Start-up report from motor manufacturer’s start-up service to certify that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

END OF SECTION

***********************************************************

Do not delete the following reference information:

***********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 0700, Rev. 3, dated June 13, 2017.