SECTION 26 2419

MOTOR-CONTROL CENTERS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic Design:  This template can only be properly edited for job-specific seismic requirements once the following three (3) decisions have been made:

- Whether the switchboard is exempt from ASCE 7 Ch. 13.

- How to comply with ASCE 7 paragraph 13.2.1.

- Whether the motor control center must operate after a seismic event.  (i.e., it is a Designated Seismic System (DSS)).

Note:  In some cases, equipment is not in the scope of ASCE 7, particularly if it is outside a building, not in the path of egress, and does not have to remain in place or function after a seismic event.  This will have to be determined by the responsible structural engineer.

I) If the motor control center is not in the scope of ASCE 7, or if it is exempt from ASCE 7 per paragraph 13.1.4, then the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

II) There are two (2) options for complying with ASCE 7 paragraph 13.2.1:

- Project-specific design and documentation, prepared by:

  - the Engineer of Record (EOR)

  - the construction subcontractor (i.e., Delegated Design)

- Manufacturer certification

If the latter option applies then this Section (26 2413) shall reference Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.

III) DSS: If a motor control center must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that MCCs are “active,” it is a DSS that requires Special Certification.  If this applies then, regardless of the previous decision (i.e., II), this section shall reference Section 01 8734, SEISMIC QUALIFICATION OF NONSTRUCTURAL COMPONENTS (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.  
Guidance:  A motor control center must be fed from a Designated Seismic System in order for the motor control center to be a Designated Seismic System.  The only Designated Seismic Systems at LANL are from generators and, for small systems, UPSs.  Facility power is not a Designated Seismic System because the LANL utility is not a Designated Seismic System.

If II.A applies, and will be accomplished via Delegated Design, then this Section shall reference Section 26 0548.16, Seismic Controls for Electrical Systems, and a project-specific version of 26 0548.16 shall be created and included in the Project Spec.  The seismic design criteria will be included therein.

Finally, another reason to include Sect. 26 0548.16 in a Project Spec is to specify seismic control/ restraint.  Section 26 0548.16 is not applicable if either:
- the motor control center is not subject to seismic design or is exempt 
- the manufacturer has certified that the MCC is seismically qualified

*************************************************************************************************************

GENERAL

  - SECTION INCLUDES

- Arc-resistant motor-control center (MCC) rated 600 volts and less.

*************************************************************************************************************

Retain Article below to cross-reference requirements Subcontractor might expect to find in this Section but are specified in other Sections.  Refer to the “seismic portion” of the author note on page 1 for details.

- If the MCC is exempt then delete both paragraphs.

- If ASCE 7 paragraph 13.2.1 is going to be complied with via manufacturer certification, and the motor control center doesn’t have to operate after a seismic event, then retain only the 1st paragraph.

- If ASCE 7 paragraph 13.2.1 is going to be complied with via project-specific design and documentation, and the motor control center doesn’t have to operate after a seismic event, then retain only the 2nd paragraph, and edit bracketed text based on whether II.A or II.B applies:

  - If II.A applies, delete bracketed text.

- For all other circumstances, retain both paragraphs, and edit the bracketed text in the 2nd as applicable.

*************************************************************************************************************

  - RELATED SECTIONS

- Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements

- Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

  - DEFINITIONS

- Arc-resistant: Designed to withstand the effects of an internal arcing fault and to direct the internally released energy away from personnel performing normal operating duties in close proximity to the equipment, while the equipment is operating under normal conditions, with all covers in place.

- Normal operating duties: Operations such as opening or closing switching devices, connecting and disconnecting withdrawable parts, reading of panel mounted measuring instruments and monitoring equipment.

- Operations that are not considered normal:  removing or replacing active components (e.g., fuses or any other removable primary component) and activities required to carry out maintenance work when the covers are open.

  - SUBMITTALS

- Action Submittals:  Provide the following per Project submittal procedures:

  - Catalog Data: Submit manufacturer’s descriptive literature describing each MCC. Include data substantiating that materials comply with specified requirements including a full description of the arc-resistant design features.

  - Shop Drawings: Submit shop drawings for each MCC including dimensioned plans and elevations and component lists. Show ratings, including short time and short circuit ratings, and horizontal and vertical bus ampacities. Include: front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrance locations.

  - Wiring Diagrams: Submit interconnecting wiring diagrams pertinent to the class and type specified for the MCC. Submit a schematic diagram of each type of controller unit supplied.

*************************************************************************************************************

Delete paragraph 4 only if MCC is exempt from seismic.  If retained, edit paragraph in accordance with editing done in Article 1.2 and the project-specific decisions referred to in the author note on pp. 1 (e.g., whether the MCC is a DSS, whether the project spec includes Sect. 26 0548.16, whether the project-specific design is prepared by the engineer of record or is delegated).  *************************************************************************************************************

  - Additional Information for Seismic:

  - Certification: Submit certified test report of IEEE Std C37.20.7 tests. Indicate the test conditions used, including the voltage, arc current and arc duration, whether a plenum was used and the number of structures tested simultaneously.

  - Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified below in “QUALITY ASSURANCE”.  Include instructions for storage, handling, protection, examination, installation, and starting of Product, including equipment anchoring requirements to meet the seismic conditions specified below in “SERVICE CONDITIONS”.

    - Include dimensioned plans and elevations that identify the weight, and the locations of the horizontal and vertical centers or gravity.

    - Indicate field anchorage or mounting provisions to hold the equipment in place and resist forces derived from the criteria specified in [section 01 8734] [section 26 0548.16].

    - Identify anchors and other mounting devices.

    - Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions.

- Closeout Submittals  Provide the following per requirements of Section 01 7700 and Project submittal procedures:

      - Operation and Maintenance Instructions:

        - Submit complete operation and maintenance instructions including step-by-step inspection, and maintenance procedures.

        - Include the manufacturer’s name, equipment model number, service manual, parts list, and brief description of equipment and its basic operational features.

      - Test and Inspection Records: Submit records of inspections, tests, and adjustments performed under FIELD QUALITY CONTROL.

  - QUALITY ASSURANCE

- MCC shall be NRTL listed and labeled to the current edition of UL 845 – UL Standard for Safety for Motor Control Centers for the application, installation condition, and the environment in which installed.

- MCC of the same design shall have been tested to IEEE Std C37.20.7- IEEE Guide for Testing Metal-Enclosed Switchgear Rated Up to 38 kV for Internal Arcing Faults, for Accessibility Type 2, and assessed as meeting the five internal  performance criteria after an arcing fault has occurred:

      - Doors and covers do not open.

      - No parts are ejected from the equipment.

      - The arc does not burn any holes in the exterior of the tested structure.

      - Cotton indicators (150 g/m2), which represent typical industrial work suits, do not ignite.

      - The connections that are part of the effective ground-fault current path remain effective.

- Comply with the National Electrical Code (NEC) for installation requirements.

  - COORDINATION

- Coordinate the features of each motor controller with the ratings and characteristics of the supply circuit, the motor, the required control sequence, the duty cycle of the motor, drive, load, the pilot device, and control circuit affecting controller functions.  Furnish controllers that are horsepower-rated to suit the motor controlled.

  - DELIVERY, STORAGE, AND HANDLING

- Receive, handle, and store MCC according to NECA 402 – Recommended Practice for Installing and Maintaining Motor Control Centers and NEMA ICS 2.3 – Instructions for Handling, Installation, Operation, and Maintenance of Motor Control Centers.

  - SERVICE CONDITIONS

- MCC shall perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

- Operating elevation of 7500 feet above sea level.

- Operating ambient temperature extremes of 32 to 104 degrees F.

- Operating relative humidity: 0 to 80 percent, without condensation.

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

- Maximum solar heat gain: 110 W/sq ft.

  - EXTRA MATERIALS

- Furnish six spares of each size and type fuse required.

- Furnish one spray can of touch-up paint that matches finish for each MCC.

  - FIELD MEASUREMENTS

- Verify field measurements against manufacturer’s shop drawings prior to fabrication.

PRODUCTS

*************************************************************************************************************

For MCCs that are subject to seismic design, if Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).

*************************************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

- Alternate products may be accepted; follow Section 01 2500 - Substitution Procedures.

*************************************************************************************************************

Delete the following section if the MCC is not subject to seismic design.

If retaining, edit the Article in accordance with related edits made in PART 1.

If the MCC is a Designated Seismic System, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/ indicated.).

*************************************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

    - The MCC shall withstand the effects of earthquake motions as represented by the [design basis earthquake in Section 01 8734] [seismic hazard indicated on the drawings] [the forces derived from the criteria specified in Section 26 0548.16].

- The term “withstand” means “the MCC will remain in place without separation of any parts when subjected to the seismic [forces derived from the specified criteria] [hazard indicated on the drawings].”

    - DSS: the MCC is a designated seismic system and, as such, it shall withstand the effects of earthquake motions as represented by the design basis earthquake in section 01 8734.

- The term “withstand” means “the MCC will remain in place without separation of any parts when subjected to the seismic forces derived from the specified criteria, and it will be fully operational after the design basis earthquake.”

GENERAL

- Furnish arc-resistant MCC as indicated on the Drawings that complies with UL 845 and NEMA ICS 18 – Standard for Motor Control Centers and is assessed as arc-resistant in accordance with IEEE Std C37.20.7.

*************************************************************************************************************

Edit the following article to match Project requirements; typically use Class I, Type B. Consider a schedule of MCCs on the Drawings if different requirements exist for different MCCs or controllers within an MCC.

*************************************************************************************************************

- MCC shall have wiring classification [Class I, Type A] [Class I, Type B] [Class I, Type C] [Class II, Type B] [Class II, Type C], as defined in NEMA ICS 2 [and scheduled on the Drawings].

*************************************************************************************************************

Edit the following article to match Project requirements; typically use Type 1A for indoor installations.

*************************************************************************************************************

- MCC shall have NEMA [Type 1 (general purpose)] [Type 1A (gasketed general purpose)] [Type 12 (industrial duty)] [Type 3R non-walk-in (rainproof)][Type 3R walk-in with 48” minimum aisle, interior lighting, door at each end, automatic ventilation system, sloped roof, and anti-skid floor] enclosure as defined in NEMA 250—Enclosures for Electrical Equipment, [as scheduled on the Drawings] except as otherwise indicated.

- MCC sections and components shall have UL 508 short circuit current withstand or interrupting ratings equal to or greater than the available fault current, in RMS symmetrical amperes, available at the MCC line terminals.

- Manufacturers:

  - Allen-Bradley, “CENTERLINE 2100”

  - Eaton, “Freedom 2100 Series”

  - Siemens “TIASTAR”

STRUCTURE

- MCC structure shall consist of vertical sections that are bolted together to form a rigid, self-supporting, free-standing assembly and are designed to permit future additions or rearrangement of control units.

- Design enclosure to be rodent proof with maximum 1/4" diameter unprotected openings.

- Each MCC shipping section shall have removable lifting angles. Mount each shipping section on steel channel sills.

- Vertical sections shall be a nominal height of 90 inches and width of 20 inches. The depth of all sections shall be 15 to 16 inches nominal.

- Each section shall have dead-front and dead-back construction. Rear access shall not be necessary for inspection or maintenance. The structure arrangement shall be for front only mounting of units.

- Each vertical section shall have a conduit entrance area on the top. This opening shall be covered with a bolted flat plate which may be removed and drilled. Provide the bottom of each structure with a rectangular area for termination of conduit.

- Each vertical section shall have a top and a bottom horizontal wireway, aligned with adjacent sections, to form wireways extending the entire length of the MCC. End vertical sections shall have cover plates which can be easily removed to allow addition of future vertical sections.

- Furnish each vertical section with a vertical wireway extending the full height of the structure and connecting to the top and bottom wireways. The vertical wireway shall have its own separate hinged door. Provide wire tie retainers in vertical wireway.

- Doors shall be formed of 16 gauge steel or heavier, with all edges flanged 5/8 inches deep minimum. Doors shall be mounted on adjustable and removable pin type concealed hinges and so arranged that unit doors may be removed without disturbing unit doors above or below.

- Isolate all power bussing and splice connections from the unit compartments and from the vertical and horizontal wireways.

- Barriers in the structure and units shall prevent the contact of any energized bus or terminal by a fish tape inserted through the conduit or wireway areas.

FINISH

- Paint enclosure and unit parts using an electro-deposition process. Interior and exterior surfaces as well as bolted joints shall have a complete finish coat on and between them. The paint process shall consist of cleaning, rinsing, phosphating, pre-paint rinses, painting, post paint rinses, a bake cure, and cool down.

- Paint exterior surfaces with medium light gray acrylic enamel. Paint the unit interior surfaces white for greater internal visibility.

- Furnish all unpainted parts with corrosion-resistant plating or material.

BUS BARS AND BRACING

- Main horizontal bus shall extend the entire length of the MCC. Bus shall be fabricated from tin-plated copper with ratings as shown on the Drawings.

- The vertical bus in each section shall be tin-plated copper with a current capacity of not less than 300 amps, and at least 10% of the rating of the main overcurrent protection. The bus support system shall be high dielectric strength, low moisture absorbing, and high-impact material.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

- Bus assembly shall be braced withstand the mechanical stress caused by fault currents of [42,000][65,000][100,000] sym. RMS amperes [as scheduled on the Drawings].

- A continuous copper ground bus, with a minimum current rating of 300 amperes, shall be located in the bottom of the structure, with cable lugs at each end of the line-up. A copper vertical equipment grounding conductor bus shall make contact with the plug-in units before the bus stabs engage the vertical bus.

- Bolted connections at each bus joint shall be front accessible for servicing with a torque wrench. Indicate the location of all splices with a label located on the inside of the vertical wireway door.

ISOLATION AND INSULATION

- Horizontal bus access covers and vertical bus covers shall isolate the energized buses to guard against the hazard of accidental contact.

- Cutouts shall be located in the vertical isolation barriers for stab connections to the vertical bus. A shutter mechanism shall close the cutouts when a plug-in unit is removed. Provide the vertical bus with phase isolation barriers.

- Isolate all units from one another, above and below, by unit support pans or steel barriers which remain in place when the units are withdrawn.

- Isolate incoming line compartments from horizontal and vertical wireways by steel barriers.

- Units shall have a side barrier to provide isolation from the vertical wireway.

UNITS

- Furnish combination motor-starter units, Size 1 through Size 5, as well as other electrical assemblies including feeder units through 225 amps, with appropriately rated stab assemblies for plug-in type construction. Starter units Size 6 and larger shall be bolt-in construction.

- Support and guide each plug-in unit so that unit arrangement is easily accomplished. After insertion, each plug-in unit shall be positively held in place.

- Each plug-in unit (bucket) shall have an equipment grounding conductor stab that makes connection to the vertical equipment grounding conductor bus before the power stabs engage.

- Each plug-in unit (bucket) shall have a mechanism for the stabs to engage to, and disengage from, the vertical bus after the bucket has been fully inserted and locked in place.

- An operator mechanism mounted on the unit shall provide the means for operating the disconnect. This operator shall extend through an opening in the unit door and shall clearly indicate whether the disconnect is 'ON', 'OFF', or 'TRIPPED'. This indication shall function whether the compartment door is open or closed.

- With the disconnect in the 'ON' position, a mechanical interlock shall prevent opening of the unit door. This interlock shall be provided with a defeater so that authorized personnel may gain access to the compartment without interrupting service. This interlock shall also prevent unintentional closing of the disconnect when the compartment door is open, a second mechanical interlock shall prevent any possibility of removing or re-inserting the plug-in unit while the disconnect is in the 'ON' position.

- The operator mechanism design shall provide for padlocking the disconnect in the 'OFF' position.

- The operator mechanism shall be so designed as to allow easy access to the magnetic trip settings on circuit breakers and motor circuit protectors.

- A remote operator shall be provided for each type of plug-in unit that is shipped with the motor control center.

- Each unit shall have a removable door mounted on removable pin type hinges which allow the door to swing open at least 110 degrees. Doors shall be removable from any location in the center without disturbing any other doors. The unit door shall be fastened to the stationary structure so that it can be closed to cover the unit space when the insert has been removed. The unit doors shall be held closed with 1/4-turn, pawl-type latches designed to resist forces during fault conditions.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

INCOMING MAIN AND FEEDER UNITS

- Furnish incoming main and feeder units as indicated on the Drawings.

- Overcurrent devices shall be 600 volt, molded case, thermal magnetic circuit breakers that conform to UL 489– Molded Case Circuit Breakers.

- The interrupting capacity of the circuit breakers shall equal or exceed the maximum available fault current at the MCC.

- Furnish surge protective devices as scheduled on the drawings and per Section 26 4300 Surge Protective Devices.

CIRCUIT BREAKER-TYPE NON-REVERSING STARTER UNITS

- Furnish starter units containing combination magnetic motor controllers with motor circuit protector disconnects or thermal-magnetic circuit breakers as indicated on the Drawings.

- Motor circuit protector shall conform to UL 845 and UL 489 - Molded Case Circuit Breakers, with an integral instantaneous magnetic trip in each pole.

  - Trip units shall coordinate with the actual locked-rotor current of the connected motor and the controller overload relays.

  - Furnish motor circuit protectors that are factory assembled with the controller, interlocked with unit cover or door, and arranged to disconnect the controller.

  - The short circuit rating of the motor circuit protector and starter combination shall equal or exceed the maximum available fault current at the MCC.

  - Furnish motor circuit protectors rated 600 volts when used on 480 volt systems.

- Controllers shall be AC general purpose Class A magnetic, full-voltage, non-reversing controllers for induction motors rated in horsepower and conforming to the requirements of NEMA ICS 2 – Industrial Control Devices, Controllers, and Assemblies.

  - Coil shall be of the encapsulated type, 120 volts, 60 Hz.

  - Controllers shall be the sizes and number of poles as indicated on the Drawings.

  - Contacts shall be totally enclosed, double-break, silver-cadmium-oxide power contacts. Contact inspection and replacement small be possible without disturbing line or load wiring.

  - Contactor shall be suitable for at least the number of operations indicated in the NEMA AC-3 utilization category load-life profile for the contactor size.

*************************************************************************************************************

Edit the following article to match Project requirements. Delete if auxiliary contacts are not required

*************************************************************************************************************

- Each controller shall have [one][two] sets of NEMA ICS 2 field convertible auxiliary contacts in addition to the seal-in contact [as scheduled on the Drawings].

- Controllers for motors rated up to 100 full-load amperes shall have solid-state overload units with the following characteristics:

*************************************************************************************************************

Edit the following article to match Project requirements. Class 20 tripping is suitable for most applications.

*************************************************************************************************************

  - NEMA Class [10][20][30] tripping characteristics [as scheduled on the Drawings].

  - Field-selectable motor-full-load current.

  - Ambient temperature insensitive.

  - Phase loss protection.

  - Manual reset after time delay.

  - Integral current transformers.

*************************************************************************************************************

Edit the following articles to match Project requirements; delete if no motors on Project are rated from 100 to 300 full-load amperes. Refer to Section D5020 in the LANL Engineering Standards Manual for overload protection for motors rated over 300 full-load amperes.

*************************************************************************************************************

- Controllers for motors rated from 100 to 300 full-load amperes shall have solid-state overload units with the following characteristics:

*************************************************************************************************************

Edit the following article to match Project requirements; some motor/load combinations require a Class 10 (fast trip) or Class 30 (slow trip) start time characteristic instead of the standard Class 20. Consider a schedule of enclosed controllers on the Drawings if different requirements exist for different controllers.

*************************************************************************************************************

  - NEMA Class [10] [20] [30] tripping characteristics [as scheduled on the Drawings].

  - Field selectable/adjustable overload trip current.

  - Phase unbalance and phase loss protection.

  - Manual or electric reset after time delay.

  - Current sensing using external current transformers with 5 ampere secondary.

*************************************************************************************************************

Edit the following article to match Project requirements. Delete control devices that are not required, but do not delete all control devices.

*************************************************************************************************************

- Controllers shall have heavy duty, 22 mm or 30 mm, metal operator, oil tight pilot devices as listed below with NEMA ICS 2, Form Z, A600 rated contacts.

*************************************************************************************************************

Edit the following article to match Project requirements. Use a rotary type selector switch on equipment that is required to re-start automatically after a power interruption (e.g. most HVAC equipment).

*************************************************************************************************************

  - Selector Switches:  Rotary type [as scheduled on the Drawings]

      - Use ON-OFF-AUTO selector switch if controller is connected to an automatic control system, or may be in the future.

      - Use ON-OFF selector switch if controller is not connected to an automatic control system.

*************************************************************************************************************

Edit the following article to match Project requirements. Use push button controls on equipment that is required to remain OFF after a power interruption (e.g. equipment requiring operator assisted startup or having safety issues during startup).

*************************************************************************************************************

  - Push buttons: [as scheduled on the Drawings]

      - Flush, momentary START and STOP pushbuttons.

      - Unless indicated otherwise on the Drawings, START-STOP pushbuttons are not required if controller is connected to an automatic control system.

*************************************************************************************************************

Edit d to match Project requirements. Delete if not required

*************************************************************************************************************

      - Furnish mushroom head, maintained action, turn-to-release or pull-to-release EMERGENCY STOP pushbutton as indicated on the Drawings.

  - Use push-to-test LED type indicating lights as follows:

      - Red: RUNNING pilot light.

      - Green: STOPPED pilot light.

      - Additional pilot lights as indicated on the Drawings.

  - Push-buttons, pilot lights and selector switches shall have legend plates.

- Each motor overload unit shall have an externally operable manual reset operator.

*************************************************************************************************************

Edit the following article to match Project requirements. Some special applications use 24V controls. Some applications may warrant specifying additional future control power transformer capacity.

*************************************************************************************************************

- Each motor-starter unit shall have a control power transformer with 120 volt secondary and sufficient capacity to operate starter coil and all connected pilot, indicating and control devices, plus [20 percent][100 percent] spare capacity [as scheduled on the Drawings]. Primary and secondary circuits of transformer shall be fused. Bond un-fused leg of secondary to enclosure.  Use fuse-blown-indicating fuses mounted in fuse blocks.

- Adhere to accepted industry standards of neatness and bending radius for wiring of controller units. Use MTW (AWM) wire for control and power wiring. Install wrap-around wire markers at both ends on all control wiring.

- Pull-apart control terminal blocks shall be mounted on the side or near the bottom of each unit to permit clear and easy access to the terminals. Terminal blocks shall facilitate disconnection and removal of the unit without damage to wiring. Terminal blocks shall be rated IP20, finger safe.

- Controller shall have auxiliary control relay(s) as indicated in the drawings or as required by sequence of operation. Relays shall be heavy-duty general purpose type, having 115 volt 60 Hertz operating coils.

IDENTIFICATION

- Each unit shall have an identification nameplate label, indicating either a catalog number or serial number description.

- Each vertical section shall have a stamped metallic identification nameplate, indicating serial number, bus rating and vertical section reference numbering. The nameplate shall be externally mounted near the center of the vertical wireway door of each section.

- Attach nameplates using sheet metal screws or approved alternate method.

EXECUTION

************************************************************************************************************

For MCCs that aren’t exempt from seismic, if Project Spec includes 26 0548.16, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

- Maintain access to each existing MCC that is to remain active.

EXAMINATION

- Examine spaces and surfaces to receive MCCs for compliance with installation tolerances and other conditions affecting performance of the product.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

- General:  Install each MCC where indicated on the Drawings in accordance with NECA 402 – Recommended Practice for Installing and Maintaining Motor Control Centers, NEMA ICS 2.3 – Instructions for the Handling, Installation, Operation, and Maintenance of MCCs, and with the manufacturer's written installation instructions. Manufacturer’s installation instructions shall be available at the construction site.

- Provide a minimum of 1/2 inch space between the back of MCC and a wall; provide a minimum of 6-inch space for damp locations.

- Ensure MCC doors, while open, do not block egress paths

- Install each MCC on a reinforced concrete housekeeping pad, minimum 5” thick, or as shown on drawings. Refer to Section 26 0548.16 – Seismic Controls for Electrical Systems for materials and installation requirements.

- Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from MCC units and components.

- Ground and bond MCC as required in Section 26 0526 – Grounding and Bonding for Electrical Systems and as shown on drawings.

- Install conduits as required in Section 26 0533 – Raceways and Boxes for Electrical Systems.

  - Terminate conduits in the MCC section containing the corresponding device.

  - Install plugged couplings set flush with the top of the concrete pad. After MCC is set in place, extend conduits to 1-1/4 inch above the pad and terminate with insulated grounding bushings.

- Install conductors as required in Section 26 0519 – Low Voltage Electrical Power Conductors and Cables.

- Train conductors neatly in groups; bundle and secure as recommended by manufacturer to withstand fault current.

- Tighten electrical connectors and terminals, including bus bar and grounding connections, according to the manufacturer’s published torque-tightening values.

- Set overload relays and motor circuit protectors in motor controllers to match installed motor characteristics.

*********************************************************************************************

Delete the following paragraph if the MCC is not subject to seismic design

*********************************************************************************************

- Comply with requirements for seismic control devices and mounting and anchoring requirements specified in section 26 0548.16 Seismic Controls for Electrical Systems

IDENTIFICATION

- Identify MCC and install warning signs and arc-flash warning labels as required in Section 26 0553 – Identification for Electrical Systems.

- Provide Category I nameplate for each starter unit or overcurrent protective device. Refer to Section 26 0553.

- At indoor locations, mark floor in front of MCC to show NEC required working clearances, according to Section 26 0553.

- Provide neatly typed label inside each motor-starter enclosure door identifying motor served, nameplate horsepower, full load amperes, code letter, service factor, and voltage/phase rating.

- Post one-line diagrams data and operating instructions in accordance with Section 26 0553.

FIELD QUALITY CONTROL

- Clean, inspect, test, adjust, and energize MCCs in accordance with the manufacturer’s instructions

      - Inspect each MCC for physical damage, proper alignment, and proper anchorage.

      - Witness the torquing of all bus bar splices

      - Verify that the proper overloads are installed and set according to the motor characteristics.

      - Verify that the proper motor circuit protectors or thermal magnetic circuit breakers are installed and set for the motor full-load-current from NEC (Table 430.250).

      - Verify proper operational response to control devices.

      - Keep records of inspections, tests, and adjustments; submit them to the LANL STR.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

Delete 3.6 if Manufacturer’s field service is not necessary

*****************************************************************************************************

- Coordinate inspections and tests with those required by Section 26 0813 – Electrical Acceptance Testing.

- After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

MANUFACTURER'S FIELD SERVICE:

- Provide the services of a factory trained representative from the MCC manufacturer to inspect and certify the installation and to oversee energizing and testing.

- Manufacturer’s representative shall certify in writing that each MCC has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 2419 Rev. 5, dated August 31, 2020.