SECTION 28 0528

PATHWAYS FOR ELECTRONIC SECURITY

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical/Security POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections. 
*************************************************************************************************************

*************************************************************************************************************

Edit this specification to match project requirements. Selection of an Argus system or a “conventional” system will be made by the LANL Security Systems Group depending upon the security posture of the facility. An Argus system uses the AFP, BAT, and FTB enclosures; a “conventional” system uses the LFP enclosure.

*************************************************************************************************************

GENERAL

Section Includes

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Electronic Physical Security System (PSS) rough-in that originates in [Argus Field panels (AFPs)] [Laboratory Field Panel(s) (LFPs)] located in the entrance telecommunications room and extends to LANL-furnished Automated Access Control System (AACS) and Interior Intrusion Detection System (IIDS) components indicated on the Drawings.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Automated Access Control System (AACS) includes:

Door access control systems with badge readers, biometric units, and door hardware (strikes and latches) with key overrides.

Turnstile access control systems with badge readers and/or biometric units. Turnstile egress may be accomplished with pushbutton or badge reader.

Interior Intrusion Detection System (IIDS) includes:

Volumetric, perimeter, and/or point contact detectors.

Door sensor switches.

LANL Furnished Materials for SUBContractor INstallation (GFE)

*************************************************************************************************************

Edit the following article to match project requirements. An Argus system uses the AFP, BAT, and FTB enclosures; “conventional” system uses the LFP enclosure.

*************************************************************************************************************

[Laboratory Field Panel (LFP) enclosures.] [Argus Field Panel (AFP) enclosures, Field Termination Boxes (FTB), and Battery Boxes (BAT).]

Specialty PSS boxes.

Copper for data and control of PSS field devices.

LANL Furnished and Installed Equipment

LANL will furnish and install the PSS field devices (badge readers, biometric units, volumetric sensors, door sensor switches, power supplies, and control equipment after beneficial occupancy.

LANL PERFORMED WORK

LANL will make final wiring connections to PSS field devices and control equipment after beneficial occupancy.

SUBMITTALS

Submit the following in accordance with Section 01 3300,  Submittal Procedures:

Test Reports: Provide inspection and test report for each PSS power, signaling, and control cable.

As-Built Drawings: Provide as-built drawings showing installed PSS raceways, boxes, and cables.

Quality Assurance

Conform to requirements of the National Electrical Code (NEC).

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) as suitable for purposes specified and shown.

COORDINATION

Coordinate installation of PSS rough-in (pathways and cables) with the LANL Security Systems Group.

Coordinate the layout of PSS equipment in the telecommunications rooms with both the LANL Telecommunications Group and the LANL Security Systems Group. Verify that adequate space exists for equipment.

Complete telecommunications rooms to allow not less than 5 working days for the LANL Security Systems Group to install LFP enclosures (s) before scheduled start of PSS installation. Coordinate schedule with the LANL Project Leader.

Coordinate electrical requirements for electric strikes/latches with the LANL Security Systems Group. Refer to Electric Door Hardware paragraph in this Section.

Coordinate required quantities of PSS cables and delivery schedule with the LANL Security Systems Group.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products and materials according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500 Substitution Procedures.

  - Raceways and Boxes

Use intermediate metal conduit (IMC) and fittings for all PSS raceways.

Terminate conduits on boxes and enclosures using threaded hubs or locknuts and insulated bushings.

Provide 4-11/16 square, 2-1/8 inch deep outlet boxes for PSS field devices (e.g. badge readers, biometric units, security terminal boxes, and volumetric detector units). Provide mud rings that match the thickness of the wallboard and the mounting requirements of the PSS field device. Provide support to prevent movement of the box.

LANL will furnish as government-furnished equipment (GFE) the following specialty boxes and enclosures for installation by the Subcontractor:

10” x 10” x 4” hinged cover, flush-mounting junction boxes.

6” x 6” x 4” hinged cover, surface-mounting junction boxes.

*************************************************************************************************************

Edit the following article to match project requirements. An Argus system uses the AFP, BAT, and FTB enclosures; “conventional” system uses the LFP enclosure.

*************************************************************************************************************

[60” x 60” x 12” LFP enclosure(s) with 12” high floor stands.][24” x 24” x 8” AFP enclosure(s), 24” x 24” x 8” FTB enclosure(s) and 20” x 20” x 8” BAT enclosure for wall-mounting.]

4” x 4” x 4” access/secure and pushbutton boxes.

Mounting brackets for badge reader and biometric units.

Refer to Section 26 0533 Raceways and Boxes for Electrical Systems for additional material requirements.

  - PSS WIREWAYS

Provide 8” x 8” x 72” feed-through NEMA Type 12 wireway(s) with all closure plates, gaskets, fittings and hangers required for a complete installation.

Manufacturer: Hoffman F-88W36 (2 required), F-88WP (2 required), and F-88WG (3 required) for each 8” x 8” x 72” wireway.

Electric Door Hardware

Furnish electric door hardware (strikes, panic bars, latches) with key override for each access-controlled door or set of doors as indicated on the Drawings.

Provide 24-volt dc door strikes and panic bars that operate on 3 amperes or less, are easily serviceable, and are electrically compatible with the LANL-furnished PSS, functionally compatible with each access-controlled door, and with finish compatible with the other door hardware.

Refer to Section 08 7100 Door Hardware for material requirements.

  - PSS Cables

LANL will furnish the PSS cables as GFE for installation by the Subcontractor. The following information is provided for determining conduit sizes and estimating installation labor:

25 pair cable, 24 AWG twisted pairs with overall shield, NEC Type CMG, 0.5 inch nominal outside diameter (O.D.).

15/C cable 22 AWG with overall shield, NEC Type CMG, 0.35 inch nominal O.D.

Cat 5e cable, four 24 AWG twisted pairs, NEC Type CM, 0.25 inch nominal O.D.

Flat 8 cable, 26 AWG, UL VW-1 rated, 0.4 inch nominal width.

2/C 18 AWG stranded cable, NEC Type CMG, 0.2 inch nominal O.D.

Coordinate cable lengths and delivery schedule with the LANL Security Systems Group.

EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Remove abandoned PSS cables.

Remove abandoned raceways and boxes when PSS cables servicing boxes are abandoned or removed. Install blank cover for abandoned boxes not removed.

Maintain access to existing PSS connections remaining active and requiring access. Modify installation or provide access panels.

EXAMINATION

Verify interior of the building has been protected from weather.

Verify that installation of telecommunications rooms is complete.

Examine raceways and building finishes for compliance with installation tolerances and other conditions affecting performance of the PSS. Do not proceed with installation until unsatisfactory conditions have been corrected.

Raceway and Box Installation - General

Install a complete raceway and box system for PSS.

Select conduit sizes based on the following factors:

Less than 50 ft between pulling points and only one bend: not more than 40 percent conduit fill.

More than 50 ft between pulling points or two 90-degree bends: not more than 31 percent conduit fill.

Minimum conduit size: 1-inch unless indicated otherwise.

Install PSS conduits and boxes as follows:

Not more than 100 ft of conduit between pull points.

No more than 180 degrees of conduit bends between pull points.

Install a pull box at each reverse bend.

Make PSS conduit bends as follows:

For conduits 2-inches and smaller, make inside radius of bends not less than 6 times the internal diameter of the conduit.

For conduits larger than 2-inches, make inside radius of bends not less than 10 times the internal diameter of the conduit.

Install conduits concealed in walls and above ceilings to the extent practicable.

Refer to Section 26 0533 Raceways and Boxes for Electrical Systems for additional installation requirements.

PSS Service  Installation

Install PSS service entrance conduits; refer to Section 33 7119, Electrical Underground Ductbanks and Manholes.

*************************************************************************************************************

Select between and edit the following two articles to match project requirements. Selection is dependent upon whether an Argus or a “conventional” system will be installed. An Argus system uses the AFP, BAT, and FTB enclosures; a “conventional” system uses the LFP enclosure. Coordinate with the LANL Security Systems Group.

*************************************************************************************************************

LFP Enclosure Installation

Install GFE LFP enclosure(s) in the entrance telecommunications room and/or other locations indicated on the Drawings.

Coordinate final LFP location in the telecommunications room with the LANL Telecommunications Group and the LANL Security Systems Group.

Provide a dedicated space that is 6 ft wide, 8 ft high, and 14 inches deep for each LFP.

Install two double-duplex 20-ampere, 120-volt receptacle outlets in each LFP.

      - Locate outlet boxes centered on lower inside right side of each LFP enclosure. Place the lower outlet box centered 10 inches above the bottom of the LFP enclosure; connect upper outlet box to lower box with a chase nipple.

Connect each double-duplex receptacle outlet to an individual dedicated 20-ampere branch circuit.

Install an 8” x 8” x 72” feed-through NEMA Type 12 wireway with bottom 8 ft above the floor centered above each LFP. Mount with hinged edge down.

Install two 3-inch conduits from each LFP up to the wireway

Connect conduits to the lower rear corners of the LFP; locate one at the left side and one at the right side of the LFP using LL and LR type conduit bodies

Locate centers of conduit openings approximately 3 inches from the bottom and 3 inches from the back of the LFP enclosure.

Install a 1-inch conduit from the wireway to a point above the telephone terminal blocks. Coordinate location with the LANL Telecommunications Group.]

AFP, FTB, and BAT Enclosures Installation

Install GFE AFP, FTB, and BAT enclosures in the entrance telecommunications room and/or other locations indicated on the Drawings.

      - Locate AFP enclosure(s) with top approximately 7’-0” above finished floor.

      - Locate FTB enclosure(s) with top approximately 4’-10” above finished floor and aligned with the AFP enclosure above.

      - Locate BAT enclosure with top approximately 22” above finished floor and centered on the wireway above

      - Coordinate final AFP, FTB, and BAT enclosure quantities and locations in the telecommunications room with the LANL Telecommunications Group and the LANL Security Systems Group.

Provide a dedicated space that is 7 ft wide, 9 ft high, and 14 inches deep for each AFP, FTB, and BAT installation.

Install a double-duplex 20-ampere, 120-volt receptacle outlets in each BAT enclosure.

      - Locate outlet box centered on lower inside right side of each BAT enclosure.

Connect double-duplex receptacle outlet to an individual dedicated 20-ampere branch circuit.

Install an 8” x 8” x 72” feed-through NEMA Type 12 wireway with center 9’-0” above the floor above the AFP enclosures(s). Mount with hinged edge down.

Install an 8” x 8” x 72” feed-through NEMA Type 12 wireway with bottom 24 inches above the floor below the FTB enclosure(s) and above the BAT enclosure. Mount with hinged edge down.

Interconnect the AFP, FTB, and BAT enclosures and the wireways as follows:

Install two 3” conduits from each AFP enclosure to the FTB enclosure below.

Install two 3” conduits from each FTB enclosure to the wireway below.

Install two 3” conduits from the upper wireway to the lower wireway. Locate conduits near the left and right ends of the wireway.

Install two 1” conduits from each BAT enclosure up to the lower wireway.

Install a 1-inch conduit from the wireway to a point above the telephone terminal blocks. Coordinate location with the LANL Telecommunications Group.]

AACS and IIDS Junction Box Installation

Install two GFE 10” X 10” X 4” flush-mounted junction boxes above door frame and below the suspended ceiling on the higher security side of each VTR access controlled door.

*************************************************************************************************************

Edit the following article to match project requirements. An Argus system uses the FTB enclosures; “conventional” system uses the LFP enclosure.

*************************************************************************************************************

The box on the left will be the AACS junction box and the box on the right will be the IIDS junction box. These boxes will provide the interface between the PSS field devices and the [LFP][FTB].

Install IIDS junction boxes at additional locations as indicated on the Drawings or as required to serve PSS volumetric detectors.

Install a dedicated IIDS junction box for each group of 10 PSS volumetric detectors or as indicated by the LANL Security Systems Group’s design.

Refer to the volumetric detector outlet installation paragraph of this Section.

Mount boxes so the cover opens with the hinge to the left.

Connect the IIDS junction box(es) to the AACS junction box with a 1-1/4 inch nipple or conduit

Install a properly-sized home-run conduit from each AACS junction box to the wireway in the telecommunications room; refer to Raceway and Box Installation – General paragraph of this Section for conduit sizing requirements.

Make conduit connections to the top, bottom, and/or sides, but not to the back of AACS or IIDS junction boxes.

Badge Reader and Biometric Unit Outlet Installation

Install two flush mounted 4-11/16 square, 2-1/8 inch deep outlet boxes on the lower security side of each access-controlled door as indicated on the Drawings.

For a single-leaf door locate outlet boxes on the strike side of the door with centers 39 inches above the floor and approximately 16 inches and 32 inches from the doorframe.

For a double-leaf door locate the outlet boxes on the right side of the door with centers 39 inches above the floor and approximately 16 inches and 32 inches from the doorframe.

Provide each box with a two-device mud ring that match the thickness of the wallboard.

Provide supports securely attached to the wall studs to prevent movement of the boxes.

At each location provide a minimum 24 inch x 24 inch clear and flat surface centered on the outlet boxes suitable for mounting a LANL badge reader bracket.

Install a 3/4-inch conduit connecting the two boxes.

Install a 1-inch conduit from the right-hand outlet box to the AACS junction box.

At exterior doors install a 3/4-inch conduit from the right-hand outlet box to the AACS junction box.

Door Sensor Switch (STB) outlet installation

Install one flush mounted 4-11/16 square, 2-1/8 inch deep STB outlet box on the higher security of each access-controlled door as indicated on the Drawings.

For a single-leaf door locate the outlet box above the strike side of the door with center 6 inches above the doorframe.

For a double-leaf door locate the outlet box centered 6 inches above the doorframe.

Provide each box with a two-device mud ring that match the thickness of the wallboard.

Install a 3/4-inch conduit from the STB outlet box to the IIDS junction box.

Access/secure switch Outlet installation

Install one flush mounted 4-11/16 square, 2-1/8 inch deep access/secure switch outlet box on the higher security of each access-controlled door as indicated on the Drawings.

For a single-leaf door locate the outlet box on the strike side of the door with center 44 inches above the finished floor and approximately 16 inches from the doorframe.

For a double-leaf door locate the outlet box on the right side of the door with center 44 inches above the finished floor and approximately 16 inches from the doorframe.

Provide each box with a single-device mud ring that match the thickness of the wallboard.

Install a 3/4-inch conduit from the outlet box to the IIDS junction box.

Electric Hardware installation

Install electric door hardware at each access controlled door as indicated on the Drawings and in accordance with the installation requirements Section 08 7100 Door Hardware.

Install a 3/4-inch conduit from the doorframe to the AACS junction box.

Coordinate rough-in with the requirements of the particular hardware installed on each door. Typical rough-in locations are as follows:

Door strike integral to door frame: rough-in conduit to strike side of door frame.

Panic bar or latch on door leaf: rough-in conduit to hinge side of door frame.

volumetric detector outlet installation

Coordinate the quantity and locations of volumetric detectors with the LANL Security Systems Group.

For estimating purposes use a quantity of not less than one detector per 100 sq ft of protected area.

Furnishings, ceiling height, room geometry, and equipment in the protected space may necessitate a greater density of detectors.

Install flush mounted 4-11/16 square, 2-1/8 inch deep outlet boxes for volumetric detectors as indicated on the Drawings or as required by the Security Systems Group.

For spaces with ceilings not more than 9 ft above finished floor, locate the outlet boxes with centers 8 ft above the finished floor.

For spaces with ceilings more than 9 ft above finished floor, install two outlet boxes at each location.

Center the lower outlet box 8 ft above the finished floor and the upper outlet box 8-inches above the lower outlet box or as required by the Security Systems Group

Install a 3/4-inch conduit connecting the two boxes.

Provide each box with a two-device mud ring that match the thickness of the wallboard.

Install a dedicated 1-inch conduit loop from the IIDS junction box to serve no more than 5 outlet boxes.

Connect no more than 10 volumetric detectors outlet boxes to an IIDS junction box.

Refer to the AACS and IIDS Junction Box Installation paragraph of this Section.

*************************************************************************************************************

Edit the following article to match project requirements. System selection is dependent upon the security posture of the facility. Coordinate with the LANL Security Systems Group. An Argus system uses the AFP, BAT, and FTB enclosures; “conventional” system uses the LFP enclosure.

*************************************************************************************************************

PSS Cable Installation

Install GFE PSS cables after painting and similar activities that could damage cables have been completed.

Clean foreign matter from interior of boxes and conduits before installing PSS cables.

At the [LFP] [FTP] enclosure(s) use the left 3-inch conduit for all 25-pair cables; use the right 3-inch conduit for all 15/C and CAT 5e cables. Leave 10 ft of slack in each cable in the [LFP] [FTP] enclosure.

Leave 3 ft of slack in each cable at the PSS field device outlet boxes.

Install cables in accordance with the following schedules. Where a cable is indicated to “loop through” a junction box on its way to a field device, provide a slack loop of the cable around the inside perimeter of the junction box.

| Cable Routing Requirements - General |
| --- |
| From | To | Cable Type (GFE) |
| [LFP] [FTP] Enclosure | Each IIDS junction box (loop through AACS Junction Box) | One 25-pair cable |
| [LFP] [FTP] Enclosure | Biometric Unit outlet box (loop through AACS Junction Box) | One 15/C cable One CAT 5e cable One 2/C 18AWG cable (exterior locations only) |
| IIDS Junction Box | Each Biometric Unit outlet box (loop through AACS Junction Box) | One Flat 8 cable |
| IIDS Junction Box | Each STB outlet box | Single leaf door: One Flat 8 cable Double leaf door: Two Flat 8 cables |
| IIDS Junction Box | Each Access/Secure outlet box | One Flat 8 cable |
| IIDS Junction Box | Each Volumetric Detector outlet box | One Flat 8 cable |
| AACS Junction Box | Door hardware | One 2/C 18AWG cable |

| Cable Routing Requirements – Turnstiles |
| --- |
| From | To | Cable Type (GFE) |
| [LFP] [FTP] Enclosure | Biometric Unit outlet box (loop through AACS Junction Box and loop through turnstile top channel) | One 15/C cable One CAT 5e cable |
| IIDS Junction Box | Each Biometric Unit outlet box (loop through AACS Junction Box) | One Flat 8 cable |
| IIDS Junction Box | Each Pushbutton outlet box | One Flat 8 cable |
| Turnstile channel | Each Pushbutton outlet box | One 2/C 18AWG cable |
| IIDS Junction Box | Each turnstile channel | One Flat 8 cable |

Uniquely identify each cable at both ends using a numbering scheme that complies with instructions from the LANL Security Systems Group; use a tag or an indelible marker

The LANL Security Systems Group will install PSS equipment and field devices and will terminate all PSS cables.

GROUNDING

Ground PSS raceways and boxes following Section 26 0526 Grounding and Bonding for Electrical Systems using the raceway system as the equipment grounding conductor.

FIELD QUALITY CONTROL

Test power, PSS cables for continuity, shorts, and unintentional grounds.

Verify proper labeling of cables.

Submit test and inspection report.

END OF SECTION

*************************************************************************************************************

Do not delete the following reference information.

*************************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 28 0528 Rev. 1, dated July 22, 2008.