SECTION 33 7311

PAD-MOUNTED TRANSFORMER ROUGH-IN

************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file at https://engstandards.lanl.gov

Rev. 4 Summary of changes Options for the grounding electrode expanded to reflect NESC requirements. Clarified inspection responsibility. Reduced requirement for grounding electrode conductor from 4/0 to 4 AWG. Other minor changes.

In addition to a pad for the transformer, containment for transformer oil may be required by ESM Chapter 7, Section G4010 (e.g., part 19) for environmental or fire protection reasons. Detail such containment structures on the Drawings.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

***********************************************************************************************************

GENERAL

SECTION INCLUDES

Furnish and install rough-in for pad-mounted utility transformer including the following:

Reinforced concrete transformer pad.

Underground ductbank for medium-voltage cables.

Underground secondary service.

Grounding provisions.

*************************************************************************************************************

Edit the following paragraph to match project requirements; delete if containment is not required. Refer to ESM Chapter 7, Section G4010 (e.g., part 19)  for containment requirements. Detail containment structures on the Drawings.

*************************************************************************************************************

Transformer oil containment provisions.

LANL-PERFORMED WORK

LANL Utilities & Infrastructure (U&I) will furnish, install, and test the pad-mounted transformer and associated medium-voltage cables.

SUBMITTALS

None

QUALITY ASSURANCE

Comply with the requirements of IEEE C2, National Electrical Safety Code.

SEQUENCING AND SCHEDULING

Coordinate rough-in for pad-mounted transformer with LANL (U&I) through the LANL Subcontract Technical Representative (STR).

After transformer pad is formed, and conduits, reinforcing bars, and grounding electrode are installed, but before concrete is placed, schedule an inspection through the LANL STR.

Contact the LANL STR to schedule an inspection of the secondary service conductor installation.

PRODUCTS

  - PAD-MOUNTED TRANSFORMER (GFE)

LANL (U&I) will furnish a compartment type, self-cooled, tamperproof, and weatherproof pad-mounted transformer that will comply with the following ANSI/IEEE standards:

ANSI/IEEE C57.12.22, American National Standard for Transformers—Pad-Mounted, Compartmental-Type, Self-Cooled Three-Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34500 GrdY/19920 Volts and Below; Low Voltage, 480 Volts and Below.

ANSI C57.12.00, IEEE Standard for Standard General Requirements for Liquid Immersed Distribution, Power, and Regulating Transformers.

EXECUTION

  - EXAMINATION

Examine surfaces and conditions, with Installer present, for compliance with installation tolerances and other conditions affecting rough-in for pad-mounted transformer.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - Conduit and duct INSTALLATION

Terminate medium-voltage ducts in the primary compartment area of the transformer pad. Refer to Section 33 7119, Electrical Underground Ducts and Manholes for material and installation requirements.

Terminate low-voltage conduits in the secondary compartment of the transformer. Refer to Section 26 0526, Raceways and Boxes for Electrical Systems.

Terminate each primary and secondary conduit with a bell end fitting set 2 inches above the top of the concrete pad.

  - CONCRETE PAD Installation

Prepare level, compacted pad site per Section 31 2000, Earth Moving. Compact to 95% per ASTM D 1557.

*************************************************************************************************************

Edit the following article to match project requirements. Use and finalize LANL Standard Detail ST-G4010-38 (all sheets) as Project-specific transformer pad construction dimensions and installation details on the Drawings.

Spill containment: Refer to ESM Chapter 7, Section G4010 (parts 10.4 and 18.0) for requirements. Detail such structures on the Drawings or delete structures if not required.

*************************************************************************************************************

Install reinforced concrete pad [and spill containment structure] for pad-mounted transformer as shown on the Drawings. Refer to Section 03 3001, Reinforced Concrete for materials and installation requirements.

Form concrete transformer pad using framing lumber with form release compounds.

Use a Section 03 3001 pre-approved design mix for exterior, 4000 psi minimum concrete.

Wood float finish top of pad to be level within 1/4” in 5 ft and to have no depressions.

Chamfer top edges and corners.

Cure concrete not less than seven days before installing equipment.

*************************************************************************************************************

Edit the following article to match project requirements; delete if equipment protection is not required. Refer to ESM Chapter 7, Standard Detail ST-G4010-39. Locate and detail equipment protection barriers on the Drawings.

*************************************************************************************************************

Install equipment protection barrier pipes around the transformer pad as indicated on the Drawings.

  - Grounding

[Install a 10-ft driven ground rod, or other grounding electrode, below the secondary compartment area of the transformer pad per NESC Rule 094. Provide 4 AWG ground conductor to connect grounding electrode to transformer ground pad in the secondary compartment.]

[Install a concrete-encased grounding electrode in the transformer pad per NESC Rule 095.  Provide 4 AWG ground conductor to connect grounding electrode to transformer ground pad in the secondary compartment.]

Terminate medium-voltage duct bank ground cable in primary compartment area of the transformer pad. Provide compression ground lug to connect duct bank ground cable to transformer ground pad in the primary compartment.

Refer to Section 26 0526, Grounding and Bonding for Electrical Systems for material and installation requirements.

  - Field Quality Control

Field inspections to be performed by LANL U&I

After transformer pad is formed, and conduits, reinforcing bars, and ground rod are installed, but before concrete is placed, schedule an inspection through the LANL STR.

Allow 3 working days in schedule for LANL inspection.

Correct deficiencies noted before placing concrete.

  - Transformer INSTALLATION

LANL (U&I) will install the pad-mounted transformer on the concrete pad.

The transformer will be anchored to the pad with post-installed concrete anchors per Section 03 1534 and the Drawings.

Ground cables will be connected to the ground pads in the primary and secondary compartments.

LANL (U&I) will install, test, and terminate the medium-voltage cables in the primary compartment.

Install the secondary service conductors from the building service equipment to the pad-mounted transformer secondary compartment.

Connect secondary service conductors to the low voltage lugs in the secondary compartment.

Use materials and installation methods specified in Section 26 0519, Low Voltage Electrical Power Conductors and Cables.

Identify secondary service conductors per Section 26 0553, Identification for Electrical Systems.

Contact the LANL STR to schedule a NEC compliance inspection of the secondary service conductor installation.

END OF SECTION

**********************************************************

Do not delete the following reference information.

**********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 33 7311 Rev. 4, dated July 14, 2022.