SECTION 33 7711

PAD-MOUNTED SWITCH ROUGH-IN

************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

For the purposes of this Section, a “pad-mounted switch” consists of a single self-supporting enclosure containing up to four medium-voltage interrupter switches. Refer to ESM Chapter 7, Section G4010, Part 7.0 for additional information.

***********************************************************************************************************

GENERAL

SECTION INCLUDES

Furnish and install rough-in for pad-mounted medium-voltage switch including the following:

*************************************************************************************************************

Edit the following article to match project requirements; pad mounted medium-voltage switch will be installed on either a manhole or on a concrete pad adjacent to an existing manhole.

*************************************************************************************************************

[Concrete pad.] [Manhole.]

Underground ductbank for medium-voltage cables.

Grounding provisions.

LANL WORK

LANL Utilities & Infrastructure will furnish, install, and test the pad mounted medium-voltage switch and associated medium voltage cables.

At electrical manholes containing energized electrical cables, LANL Utilities & Infrastructure make penetrations into the manholes and will install the last 5 ft of duct into the manhole using materials furnished by the construction subcontractor.

SUBMITTALS

Construction Submittals: None

QUALITY ASSURANCE

Comply with the National Electrical Code and IEEE C2 National Electrical Safety Code.

SEQUENCING AND SCHEDULING

    - Coordinate rough-in for medium-voltage pad-mounted switch with LANL Utilities & Infrastructure through the LANL Subcontract Technical Representative (STR).

*************************************************************************************************************

Edit the following article to match project requirements; pad mounted medium-voltage switch will be installed on either a manhole or on a concrete pad adjacent to an existing manhole. Delete article if switch will be installed on a manhole.

*************************************************************************************************************

    - After pad is formed, and conduits, reinforcing bars, and ground cables are installed, but before concrete is placed, schedule an inspection through the LANL STR.

PRODUCTS

  - PAD-MOUNTED medium-voltage Switch (GFE)

LANL Utilities & Infrastructure will furnish tamperproof and weatherproof pad-mounted medium-voltage switch that will comply with IEEE C37.74, IEEE Standard Requirements for Subsurface, Vault, and Pad-Mounted Load-Interrupter Switchgear and Fused Load-Interrupter Switchgear for Alternating Current Systems Up to 38 kV.

EXECUTION

  - EXAMINATION

    - Examine surfaces and conditions, with Installer present, for compliance with installation tolerances and other conditions affecting rough-in for pad-mounted medium-voltage switch.  Do not proceed with installation until unsatisfactory conditions have been corrected.

*************************************************************************************************************

Edit the following articles to match Project requirements. Pad-mounted switch unit will either be mounted on top of an electrical distribution manhole (standard for new construction) or on a concrete pad adjacent to an existing electrical distribution manhole. If switch will be mounted on a manhole, retain clause 3.2 and delete clause 3.3.  If switch will be mounted on a concrete pad, delete clause 3.2 and retain clause 3.3.

*************************************************************************************************************

  - Manhole

    - Provide manhole with top section designed for mounting [one][two] medium voltage pad mounted switch units as shown on the Drawings.

    - Refer to Section 33 7119, Electrical Underground Ducts and Manholes.

  - CONCRETE PAD Installation

    - Prepare level, compacted pad site per Section 31 2000, Earth Moving. Compact to 95% per ASTM D1557.

*************************************************************************************************************

Project-specific switch pad construction dimensions and details must be included in the Drawings. Use Drawing ST-G4010-38 as guidance for concrete pad dimensions reinforcing, and other details.

*************************************************************************************************************

    - Install reinforced concrete pad for pad-mounted switch as shown on the Drawings Refer to Section 03 3001, Reinforced Concrete for materials and installation requirements.

Form concrete pad using framing lumber with form release compounds.

Use a Section 03 3001 pre-approved design mix for exterior, 4000 psi concrete.

Wood float finish top of pad to be level within 1/4” in 5 ft and to have no depressions.

Chamfer top edges and corners.

Cure concrete not less than seven days before installing equipment.

*************************************************************************************************************

Edit the following article to match project requirements; delete if equipment protection is not required. Refer to ESM Chapter 7, Drawing ST-G4010-39. Locate and detail equipment protection barriers on the Drawings.

*************************************************************************************************************

Install equipment protection barrier pipes around the medium-voltage switch pad as indicated on the Drawings.

  - duct INSTALLATION

    - Terminate medium-voltage ducts in the switch compartment areas of the medium-voltage switch pad as indicated on the Drawings.

    - Install 6-inch concrete-encased duct from below each switch compartment at the switch pad to within 5 ft of existing manhole. LANL Utilities & Infrastructure will extend ducts into existing manhole. Furnish all ductbank materials required for this work.

    - Refer to Section 33 7119, Electrical Underground Ducts and Manholes for materials and installation requirements.

    - Terminate each duct with a bell end fitting set 2 inches above the top of the concrete pad.

  - Grounding

    - Install 4/0 AWG grounding cable from each switch compartment area to ground cable ring in the existing electrical manhole or to the duct bank ground cable.

    - Terminate medium-voltage duct bank ground cables in switch compartment area of the medium-voltage switch pad. Provide compression ground lug to connect ground cable to medium-voltage switch ground pad in the switch compartment.

    - Refer to Section 26 0526, Grounding and Bonding for Electrical Systems for material and installation requirements.

*************************************************************************************************************

Edit the following article to match project requirements; pad mounted medium-voltage switch will be installed on either a manhole or on a concrete pad adjacent to an existing manhole. Delete article if switch will be installed on a manhole.

*************************************************************************************************************

  - Field Quality Control

    - After switch pad is formed, conduits are installed, reinforcing bars are installed, but before concrete is placed, schedule an inspection through the LANL STR.

    - Allow 3 working days in schedule for LANL inspection.

    - Correct deficiencies noted before placing concrete.

  - medium-voltage switch INSTALLATION

    - LANL Utilities & Infrastructure will install the pad-mounted medium-voltage switch on the concrete pad.

The switch will be anchored to the pad with post-installed concrete anchors.

Ground cables will be connected to the ground pads in switch compartments and to the ground ring in the electrical manhole or to the duct bank ground cable.

    - LANL Utilities & Infrastructure will install, test, and terminate the medium-voltage cables.

END OF SECTION

************************************************************************************

Do not delete the following reference information.

************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 7711 Rev. 2, dated September 1, 2009.