SECTION 01 4631

Welding of ASME B31 Piping

******************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file at https://engstandards.lanl.gov

Rev. 1 Summary of Changes Section name updated, clarified intent being weld thickness specificity, added option to move content to Drawings or Div 02-48 (wherein submittals are to be sent), updated code editions and other references.

This is not a typical LANL master.  It is verbiage and examples of welded-joint design/fab final design (e.g., thicknesses) that the Design Agency must convey to the Constructor/fabricator.  Conveying this can be accomplished in several ways:

Option 1:  Including (distributing out) the applicable material into each Div 02-48 Section that involves this work (in which case delete ALL references to this Section in Spec Book).

Option 2:  Including applicable material herein on the Drawings. (in which case delete ALL references to this Section in Spec Book).

Option 3:  Include this Section in the Specification while making clear that the submittals discussed here are always sent in per the affected Div 02-48 Section (Option 3 is the last and least desirable option).

This document captures LANL’s B31 welding requirements once (rather than in multiple sections) for LANL’s convenience in maintaining the requirements.  It is provided as an aid to the Design Agency for providing a complete, code-compliant design that LANL can review and accept during the design phase.  Delegation and deferment of said design requires LANL Project Engineer and Pressure Safety SME prior approval.

This section addresses both welding and joining of B31 piping and tubing.  As such, it potentially affects (but is not limited to) the following related LANL Masters:

22 1500, Compressed Air Systems (nominally B31.9),

23 2113, Hydronic Piping (B31.9),

23 2215, Steam and Condensate Heating Piping and Specialties (nominally B31.9)

23 2300, Refrigerant Piping (B31.5), and

40 0504, Process Piping (B31.3).

Sections 01 4444 and 01 4455 which primarily address welder and procedure qualification (offsite and onsite, respectively) are complementary to this section (and to non-B31 welding sections) and should continue to be included where welding is involved.

The designer is encouraged to review the DOE Handbook DOE-HDBK-1132, Design Considerations, and the LANL Engineering Standards Manual Chapters 13 and 17.

This template material must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This section material must also be edited to delete requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.

Please contact the pressure safety POC/CPSO with suggestions for improvements.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 01, General requirements.

This section was developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements might be necessary if increased confidence in procurement or execution is desired, and independent review is necessary.  See ESM Chapter 1 Section Z10 specifications and quality sections.

This template material was developed to meet the requirements for ASME B31.9-2020, B31.1-2020, B31.5-2019, and ASME B31.3-2020.  The type of fluid service must be specified to ensure the correct process is used for the application.  Application of this template to a different fluid service or edition of these ASME code editions will require a detailed review of the code and ESM Chapter 17.   In addition, LANL utilizes a risk-based approach related to personnel injury (FS1, FS2, and FS3) described by ESM Ch. 17 that is used herein.

******************************************************************************************************************

Part 1   GENERAL

  - Section Includes

#### Detailed requirements for welding/brazing of ASME B31-series piping and tubing as required by the design.

  - Design Requirements

**********************************************************************************************************

Only the standards most widely or uniquely used at LANL applications are listed below; add others that are relevant to the design, where this will be helpful to users.

**********************************************************************************************************

The code of record is:

- ASME B31.1–[2020 or state year], Power Piping

  - Fluid:  Steam Condensate

  - Design Pressure:  15 psig

  - Design Temperature:  100 F [normal] 70 F [low]; 150 F [high]

- ASME B31.3–[2020 or state year], Process Piping

- [Fluid], [Fluid Service Category; D, Normal, M, High Pressure, High Purity, High Temperature, Cyclic Service]

- Design Pressure:  165 psig

- Design Temperature:  70 F [normal] 0 F [low]; 100 F [high]

- ASME B31.5–[2019] or state year], Refrigerant Piping and Heat Transfer Components

- Refrigerant:  R410a (501.2.4 Minimum Design Pressure)

- Design Pressure High Side:  430 psig (104 F)

- Design Pressure Low Side:  250 psig (80 F)

- ASME B31.9–[2020 or state year], Building Services Piping

- Fluid:  [Compressed Air] [also list others]

- Design Pressure:  150 psig

- Design Temperature:  70 F [normal] 0 F [low]; 100 F [high]

******************************************************************************************************************

In the listing below, designer must eliminate standards that are not applicable to the project and add standards that are applicable to the project. Then, designer must either (1) specify each B31.1, B31.3, B31.5, or B31.9-listed materials’ national standard edition for each remaining standard listed or (2) determine latest is equivalent.  Then modify to either (1) implement the first option—and also list the edition year after each standard number (e.g., ASTM F493-04)—or (2) implement the second option.

******************************************************************************************************************

  - References

[All national standards invoked herein shall be taken to be the edition in effect for the code of record listed above in 1.2 and shown below, unless noted otherwise] [All national standards invoked below and herein shall be taken to be the latest edition].

- ASME (American Society of Mechanical Engineers) (use latest edition)

      - ASME B16.9, Factory-Made Wrought Buttwelding Fittings

      - ASME B16.11, Forged Fittings, Socket-Welding and Threaded

      - ASME B36.10M, Welded and Seamless Wrought Steel Pipe

      - ASME BPV Code, Section V, Nondestructive Examination

- ASTM International

      - ASTM D2564, Solvent Cements for PVC Plastic Piping Systems

      - ASTM D2855, Standard Practice for the Two-Step (Primer and Solvent Cement) Method of Joining Poly (Vinyl Chloride) or Chlorinated Poly (Vinyl Chloride) (CPVC) Pipe and Piping Components with Tapered Sockets

      - ASTM F714, Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Outside Diameter

- AWS (American Welding Society) [note: these AWS material specifications have been qualified per ASME Section IX as required by ASME B31.3 328.3.1]

      - AWS A2.4-2012, Standard Symbols for Welding, Brazing, and Nondestructive Examination (not listed)

      - AWS A5.1/A5.1M, Specification for Carbon Steel Electrodes for Shielded Metal Arc Welding

      - AWS A5.4/A5.4M, Specification for Stainless Steel Electrodes for Shielded Metal Arc Welding

      - AWS A5.8M/A5.8, Specification for Filler Metals for Brazing and Braze Welding

      - AWS A5.18/A5.18M-2005, Specification for Carbon Steel Electrodes and Rods for Gas Shielded Arc Welding

      - AWS A5.31, Specification for Fluxes for Brazing and Braze Welding

      - AWS D1.1/D1.1M, Structural Steel Welding Code

- MSS

      - MSS SP-97, Integrally Reinforced Forged Branch Outlet Fittings — Socket Welding, Threaded, and Buttwelding Ends.

### ACTION Submittals

NOTE:  The following information shall be submitted for all relevant components TO THE DIV 02-48 SECTION TO WHICH THEY APPLY:

    - For all relevant components:

      - Design Data: An item may be considered unlisted due to its component type or its material of construction.  Submittal evaluation from design agency professional that such items shall adhere to “a” and “b” below, respectively.

        - Items that are unlisted due to component type shall be in accordance with ASME B31.3 Section 302.2.3.

        - Items that are unlisted due to material of construction shall be in accordance with ASME B31.3 Section 323.1.2.

      - Product Data: Include the Manufacturer’s name, model number, parts list, and brief description of equipment and its basic operational features.

      - Installation and Operation & Maintenance Manual(s).

    - Prior to receiving materials submit the Material Control Procedure described at 1.3.

    - Before fabrication, submit NDE (non-destructive examination) procedures that will be used for fabrication and examination of the piping, and pressure-leak testing and cleaning procedures.

    - Provide all submittals required by Section 01 4115, Pressure Safety Submittals, for the as-constructed configuration.

### Quality Assurance

- Material Control Procedure (ESM Ch. 17 FS1 and FS2 systems only)

      - Work shall be performed in accordance with a LANL-approved Material Control Procedure.  This procedure shall describe the control methods and documentation used to handle and monitor the use of controlled materials (piping component, fasteners, and welding filler rod and other components).

      - The procedure shall follow manufacturer’s requirements for storage and handling.

      - The procedure shall also address procurement controls, segregation of materials, and traceability of materials from receipt at the shop through processing and final assembly.

      - An example procedure is LANL’s ESM Ch 13 GWS 1-03 which describes how LANL does this, available at.

- Inspection and Testing

      - The Supplier shall perform inspection and testing to verify the conformance to the specified requirements defined in PART 2 of this Section, as well as any Supplier requirements as defined as part of the Supplier’s QA/QC program.

      - The Supplier shall provide an Inspection and Test Plan indicating all testing and inspection functions to be performed, including hold points during fabrication and assembly, as well as during the factory acceptance testing (FAT).

      - All inspection and testing functions shall be performed by qualified personnel using qualified procedures in accordance with specified requirements.

      - Hold points are required during the fabrication process to allow inspection, verification, or approval by LANL before the Supplier does further work.  Hold points shall be identified on the Inspection and Test Plan, with provisions for LANL review and acceptance.  LANL may waive Hold Points at their discretion.

      - Inspection Records: The Supplier shall appropriately record, submit and maintain records documenting the inspection and/or test then submit the completed Inspection Record as part of the QA Document Package. The status of all planned and executed inspection and testing activities shall be logged and traceable to ensure that the required inspection and testing have been performed, and any items that have failed inspection or testing are not inadvertently installed or implemented.

- Qualifications

      - Installer Qualifications

        - Certify that all personnel have passed relevant qualification tests per ASME B31.3 for joining processes involved and that certification is current.

          - Metallic Pipe:  Welders and braziers shall be qualified in accordance with ASME BPVC Section IX.

          - Bonding of plastics:  Bonder and bonding operators shall be qualified per ASME B31.3, Section A328.2.

          - Steel Support Welding:  Qualify processes and operators to AWS D1.1/D1.1M.

        - Welding/Brazing procedures shall be qualified according to ASME BPVC Section IX.

          - Welding and joining requirements shall be in accordance with Sections 01 4444 (offsite welding) and/or 01 4455 (onsite welding) when included.

        - Bonding procedures for plastic piping shall be in accordance with Sections 01 4444 and 01 4455 and qualified according to ASME B31.3 Section A328.

      - Qualification of Examination Personnel

- Certified Welding Inspectors (CWI) shall be in accordance with 01 4444 and/or 01 4455.

- Personnel performing other examination shall be certified in accordance with contractor’s written practice.  Personnel performing nondestructive examination to the requirements of B31.3 shall be qualified and certified for the method to be utilized following a procedure as described in the ASME BPV Code, Section V, and Article 1, T-120 (e) or (f).

- Certifications of examination personnel shall be maintained for Inspector’s review.

- Examination records including examiner’s qualifications and procedures shall be retained for at least 5 years per ASME B31.3, Section 346.3.

Owner’s Inspector shall be qualified in accordance with ASME B31.3 Section 340 and LANL’s Engineering Services – Facility Engineering (ES-FE) LANL will act for DOE to designate Owner’s Inspectors or Designee.

Manufacturer Qualifications

        - Must have a minimum of 5 years of experience in B31 construction.

        - Must have maintenance service based within 200 miles radius of installation.

Part 2	PRODUCTS

******************************************************************************************************************

This section must be updated to reflect the assembly processes for the system.  The welding design must address the following criteria:

1. Weld procedure specifications (WPS)

2. List of welding materials, to include filler materials and gases

3. Heat treatment requirements

4. Method of welding, brazing, solvent welding, thermal fusion, etc. (GTAW, SMAW, oxyacetylene, etc.)

5. Cleaning methods

6. Contain engineering design calculations or other approved ASME method that establishes the structural integrity of the design.

******************************************************************************************************************

Note:  Non-LANL WPSs may be used with LANL approval.

  - FILLER MATERIALS

    - Stainless Pipe Welding Filler

      - LANL WPS 1000-0213-8

      - Process:  SMAW

      - Filler Metal:  E316L-15,-16,-17

      - Joints:  2 (Fillet Weld aka Socket Weld)

    - Stainless Steel Pipe Welding Filler

      - LANL WPS 2010-0212-8

      - Process:  GTAW

      - Filler Metal:  ER316L

      - Joints: 1, 2, 3 (pipe Groove Weld) and Fillet Welds

    - Carbon Steel Pipe Welding Filler

      - LANL WPS 1000-0201-1

      - Process:  SMAW

      - Filler Metal:  E6010 and E7018

      - Joints:  1, 2, 3, and 5 (pipe Groove Weld) and 5 (Fillet Weld aka Socket Weld)

    - Carbon Steel Pipe Welding Filler

      - LANL WPS 2010-0002-1

      - Process:  GTAW

      - Filler Metal:  ER70S-2,-3

      - Joints:  6, 7 (pipe Grove Welds) and Fillet Welds

    - Copper Braze Filler

      - LANL BPS 6000-107-F103

      - Process:  Torch Brazing (neutral)

      - Filler Metal:  BCuP-5

      - Flux:  N/A

    - PVC/CPVC Bonding

      - LANL WPS 10000-PVC/CPVC

      - Process:  Bonding

      - Solvent:  ASTM D2564

      - Joint:  Socket

    - HDPE Welding

      - LANL WPS 7100-xxxx-HDPE

      - Process:  Thermal Fusion

      - Filler Metal:  Autogenous

      - Joint:  Electrofusion Socket Coupling

    - Carbon Steel Structural Welding Filler

      - LANL WPS 1000-0201-1

      - Process:  SMAW

      - Filler Metal:  E6010 and E7018

      - Joints:  1, 2, 3, and 5 (pipe Groove Weld) and 5 (Fillet Weld aka Socket Weld)

2.2	PIPING/TUBING/FITTINGS

    - See 22 1500, Compressed Air Systems (B31.9)

    - See 23 2113, Hydronic Piping (B31.9)

    - See 23 2300, Refrigerant Piping (B31.5)

    - See 40 0504, Process Piping (B31.3)

PART 3  EXECUTION

- PREPARATION

******************************************************************************************************************

Designer note:  Review ESM Chapter 17 ADMIN-2 Design, Documentation, and Records (or successor document Section PS-SP), for information on cleaning.

******************************************************************************************************************

    - Pre-Weld Cleaning

      - Subcontractor shall be responsible for the cleanliness and integrity of the system.

      - Weld joints shall be clean of shall be free of loose scale, sand, dirt, paint, metal chips, filings, flux, slag, weld spatter, mill scale, rust, grease, oil, waxes, or other contaminants that are easily seen with the unaided eye.

      - Consult manufacturer’s recommendation for the use of acids and cleaning agents to prevent damage. Cleaning agents used with stainless steel systems shall contain no more than 50 ppm halide content.

      - Ensure safeguards are taken to protect personnel from hazards of cleaning, which may include but not be limited to flying particulates, corrosive chemicals, and harmful vapors.

      - A suitable chemical and/or mechanical cleaning method shall be used, if necessary, to clean all surfaces to be fabricated.

- FABRICATION

******************************************************************************************************************

Designer notes

- Designer shall provide weld dimensions for all the piping welds.

- Branch connections must meet the area replacement requirements of ASME B31.3 304.3.3 Reinforcement of Welded Branch Connections.

- Extruded outlet headers must meet the area replacement requirements of ASME B31.3 304.3.4 Reinforcement of Extruded Outlet Headers, and the acceptable details for branch attachment welds Fig 328.5.4D.

- Integrally Reinforced Branch Connection welding must be defined see Figure 328.5.4F.

- Slip-on flanges shall be positioned so that the end of the pipe is recessed from the flange face by approximately 1/16 inch before welding (the distance required by ASME B31.3 Fig. 328.5.2B).

- Socket welds shall be positioned so the end of the pipe is recessed from the socket by approximately 1/16 inch before welding.

- Weld symbols on drawings for design must be specified in accordance with AWS A2.4.

- Where appendices are N/A, delete them and reference to them below.

******************************************************************************************************************

    - Weld Sizes for branch connection are shown in Appendix A.

    - Weld Sizes for fillet welding socket and slip-on flanges are shown in Appendix B.

    - All piping shall be fabricated in accordance with the provided [Construction] Drawings.

    - Welded Joints

      - No welding shall be performed until the Welding Procedure Specification (WPS), Procedure Qualification Records (PQR), and Welder Qualification Test Records (WQTR) have been approved by LANL.

      - Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

      - Weld/braze joints shall be prepared in accordance with the appropriate WPS.

      - Unless noted otherwise on the isometric drawing, field fit-up welds shall include 6 inches of pipe beyond the length required.

******************************************************************************************************************

Designer Note: Evaluate the manufacturer’s information for the HDPE welding process and include those specific items required to perform the welding.

******************************************************************************************************************

    - High Density Polyethylene (HDPE) Butt Fusion Joints

      - Polyethylene piping shall be fabricated and assembled in accordance with this specification and the Manufacturer’s recommendations.

      - Polyethylene pipe shall not be threaded, cemented or solvent welded.

      - Polyethylene piping shall be joined by the thermal butt fusion method with equipment from the approved Manufacturer.

      - HDPE heat fused external and internal beads shall not be removed.

      - Branch connections to the main shall be made with saddle fittings or tees. HDPE saddle fittings shall be saddle-fused to the main pipe.

      - Tools and other devices used to hold or apply forces to the pipe shall be such that the pipe surface is not scored or deeply scratched.

      - A data logger shall be used to record time, pressure, and temperature for all heat fusion welds made for HDPE pipe joints and fittings.

      - Sections of pipe having been discovered with cuts or gouges resulting in wall thicknesses less than the applicable minimum values shown in material specification [ASTM F714 Table 7, or other] shall be cut out and removed. The undamaged portions of the pipe shall be rejoined using the proper heat fusion joining method.

      - Use of Spacers

        - Uniformity of the jacket annulus shall be maintained. Spacers shall be used in accordance with the following requirements:

          - Maximum distance between spacer groups or spacers and jacket end termination shall be 2.1 meters (7 feet) for core NPS 2 and smaller.

          - Maximum distance between spacer groups or spacers and jacket end termination shall be 3.1 meters (10 feet) for core NPS 3 and greater.

          - Spacers or jacket end termination shall be placed within 1.2 meters (4 feet) of the tangent point of elbows or center point of concentric fittings.

          - At least one spacer group or jacket end termination shall be provided for each straight run of pipe.

          - Spacers shall be considered in the flexibility analysis.

          - All annulus spacers (inserted during assembly or pre-assembled by the pipe manufacturer) shall be orientated to facilitate drainage of liquid in the annulus; this means the open portions of the spacers are to be inserted on the bottom of the pipe.

******************************************************************************************************************

Designer Note:  When double-wall pipe is welded concurrently, a sensitive leak test of the internal pipe is required in accordance with ASME B31 Code Case 180.  Work must be planned to facilitate the sensitive leak test.

******************************************************************************************************************

      - End termination fittings shall be used to seal the annular space between the carrier and containment pipes at both ends. These termination fitting will also provide the transition to single wall piping.

- EXAMINATION, TESTING, AND INSPECTION

    - Special Instructions

      - When connecting to existing piping, leak test final tie-in joints per ESM Chapter 17 Section EXIST - Legacy System Requirements, (3.0) (becoming Section PS-SP) of LANL Engineering Standards Manual STD-342-100.

    - For the purposes of this section, the Subcontractor (constructor) is responsible for all tasks identified as examination and testing.  CWI activities are considered examination.  Owner’s Inspector activities are considered inspection.

    - Examination

      - Both the extent of examination and acceptance criteria shall be in accordance with ASME [B31.3, B31.5, B31.9] (for example paragraph 341 Examination and/or, for non-metallic systems, Section A341 as applicable.).

        - For normal fluid service each welder’s and welding operator’s work shall be represented in the 5% sampling.

        - When pneumatic testing is planned 100% of all threaded, bolted, and other mechanical joints shall be examined during assembly.

******************************************************************************************************************

Designer Note:  The postweld heat treatment in accordance with 331 Heat Treatment must be defined for the application.

******************************************************************************************************************

      - Pipe examinations shall be performed after fabrication [, after required heat treatment], and before leak testing.

      - External and accessible internal surfaces shall be examined to be free of rust, scale, weld flux, weld slag, splatter, and paint.

      - Any items rejected because of defects shall be repaired, replaced, and examined in accordance with this specification and ASME B31.3.

      - Methods of examination shall be in accordance with ASME B31.3 Section 344.

      - Acceptance Criteria for Welds is in ASME B31.3 Table 341.3.2, Acceptance Criteria for Welds–Visual and Radiographic Examination.

      - In process examination of welds [may, may not] replace radiographic [or, and] ultrasonic volumetric analysis for [all, specify welds] welding in accordance with ASEME B31.3 344.7 In-Process Examination.

    - Inspection

      - Owner’s Inspector shall have access to any and all design, fabrication, manufacture, fabrication, heat treatment, assembly, erection, examination, testing , records, documentation or other project information or activities to verify that all required examinations and testing have been completed and to inspect the piping to the extent necessary to be satisfied that it conforms to all applicable examination requirements of the Code and of the engineering design and to perform the role defined in ASME B31.3.

      - Owner’s Inspector is the final authority on acceptance of the project, examination, or test.

END OF MAIN SECTION [; APPENDICES FOLLOW]

***********************************************************

Do not delete the following reference information:

***********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 01 4631 Rev. 1, dated June 2, 2022.

**********************************************************************************************************

The following examples are not valid unless the designer evaluation has been performed per 304.3 Branch Connections

**********************************************************************************************************

***************************************************************************************************************

The following examples are not valid unless using an integrally reinforced branch connection MSS SP-97 fittings.  The following example is not meant to be all inclusive, but to provide basis of the design and guidance to the Designer that will be modifying this specification section.

***************************************************************************************************************

Integrally Reinforced Branch Connection MSS SP-97 Fittings

Integrally Reinforced Branch Connection MSS SP-97 Fittings

| Branch Pipe IPS | Identification/Schedule | Branch Pipe Nominal (1) Thickness (Tbar b) | 0.7 x (Tbar b) | Fillet weld throat thickness (tc) | Maximum Run IPS |
| --- | --- | --- | --- | --- | --- |
| ½ | STD | 0.190 | 0.0763 | 0.0763 | 2 |
| ½ | Extra Strong | 0.147 | 0.1029 | 0.1029 | 2 |
| ½ | Schedule 160 | 0.188 | 0.1316 | 0.1316 | 2 |
| 2 | STD | 0.154 | 0.1078 | 0.1078 | 8 |
| 2 | Extra Strong | 0.218 | 0.1526 | 0.1526 | 8 |
| 2 | Schedule 160 | 0.344 | 0.2408 | 0.2408 | 8 |
| 2 | Extra Extra Strong | 0.436 | 0.3052 | 0.25 | 8 |

- Thickness from ASME B36.10M–2004, Welded and Seamless Wrought Steel Pipe

Notes

      - Branch size must not exceed NPS 2 (DN-50)

      - Branch size does not exceed one fourth (1/4; 0.25) the nominal size of the run

      - Minimum wall thickness of the coupling shall not be less than that of the unthreaded branch pipe

      - Coupling or half coupling minimum Class 3000 per ASME B16.11

      - Coupling shall be full penetration groove weld with fillet weld cap

Cover fillet weld shall provide a smooth transition to the run pipe with an equal leg fillet at the longitudinal section to an equal leg fillet, unequal (oblique) leg fillet

ASME B31.1, B31.3, B31.5, and B31.9 Slip-On Flange Weld Size Determination Method

(Minimum weld dimensions for double-welded, slip-on, socket-weld flange attachment welds)

Reference:

ASME B31.1 Figure 127.4.4 (B) (a)

ASME B31.3 Figure 328.5.2 B (1)

ASME B31.5 Figure 527.3.3-2 (first figure)

ASME B31.9 Figure 927.4.3-2

Material:  ASTM A312/A312M-2011, TP304L, UNS S30403

Flange:  Class 150 ASME B16.5

Pipe Size:  1 inch pipe thicknesses per ASME B36.10 (example used for illustration)

| One Inch Pipe |
| --- |
| Nominal Wall Thickness (inch) | Schedule | Standard |
| 0.065 | 5 |  |
| 0.109 | 10 |  |
| 0.114 | 30 |  |
| 0.133 | 40 | Standard |
| 0.179 | 80 | XS |
| 0.25 | 160 |  |
| 0.358 |  | XXS |

ASME B16.5 Class 150 Dimensions from Table II-8

Thickness of straight neck (thub) = (X –B)/2 = (1.94-1.36)/2 = 0.29 inches

Length of stub end (lstub) = Y - tf = 0.62-0.5 = 0.12 inch

Adjustment for neck thickness for 7o taper

Tan(7°) = opposite/adjacent = thinning of neck/length of stub end

Thinning of neck = length of stub end x Tan(7°) = 0.12 Tan(7°) = 0.0147

Thickness of taper neck = thub – thinning of neck = 0.29 – 0.0147 = 0.2753 inches

Comparing the thicknesses of the pipe, the slip on neck thickness, and the code required minimums from the figures gives the following minimum weld sizes for weld 1 and weld 2.

Apply criteria for B31.3 or other Code of Record

Weld 1 = less of T bar (nominal pipe thickness) or ¼ inch

Weld 2 = lesser of ¼ T bar (nominal pipe thickness) or hub thickness (straight or tapered)

Note that for ML-1 or ML-2 applications these simple calculations should be checked per the calculation procedure AP-341-605.

| B31.3 One-inch Pipe Front and Back Fillet Weld Sizes, Class 150 Slip-On Flange (Equal Leg Fillet Weld) all sizes in inches |
| --- |
| Nominal Wall Thickness (inch) | Schedule | Standard | B31.3 T-bar | B31.3 1/4 Weld | B31.3 Minimum Weld 1 | 1.4 x T bar | Class 150 Straight Hub Thickness | Class 150 Tapered Hub Thickness | B31.3 Straight Hub Minimum Weld 2 | B31.3 Tapered Hub Minimum Weld 2 |
| 0.065 | 5 |  | 0.065 | 1/4 | 0.065 | 0.091 | 0.29 | 0.273 | 0.091 | 0.091 |
| 0.109 | 10 |  | 0.109 | 1/4 | 0.109 | 0.153 | 0.29 | 0.273 | 0.153 | 0.153 |
| 0.114 | 30 |  | 0.114 | 1/4 | 0.114 | 0.16 | 0.29 | 0.273 | 0.16 | 0.16 |
| 0.133 | 40 | Standard | 0.133 | 1/4 | 0.133 | 0.186 | 0.29 | 0.273 | 0.186 | 0.186 |
| 0.179 | 80 | XS | 0.179 | 1/4 | 0.179 | 0.251 | 0.29 | 0.273 | 0.251 | 0.251 |
| 0.25 | 160 |  | 0.25 | 1/4 | 0.25 | 0.35 | 0.29 | 0.273 | 0.29 | 0.273 |
| 0.358 |  | XXS | 0.358 | 1/4 | 0.25 | 0.501 | 0.29 | 0.273 | 0.29 | 0.273 |

Note that for ML-1 or ML-2 applications these simple calculations should be checked by (e.g., by calculation procedure AP-341-605).