SECTION 03 3053

MISCELLANEOUS CAST-IN-PLACE CONCRETE

*************************************************************************************************************LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

*************************************************************************************************************

NOTE: This specification may be adjusted to cover separate curbs and gutters or combination curbs and gutters.  This guide specification will not be used for integral or monolithic curbs of concrete pavement.

*************************************************************************************************************

SECTION INCLUDES

Concrete sidewalks, drive pads, and median pavement.

Concrete curb and gutters.

Concrete for fence posts

Concrete thrust blocks on utility lines

Concrete foundations or bases for manholes

ACTION SUBMITTALS

Submit the following:

Material certifications documenting compliance with the New Mexico Department of Transportation (NMDOT) Standard Specifications for Highway and Bridge Construction (SSHBC) including any Supplemental or Interim Specifications (i.e., latest specs).  Exclude NMDOT Division 100, General Provisions, and any other references to METHOD OF MEASUREMENT, to BASIS OF PAYMENT, and for pay factor determination.  Guidance:  Document(s) at 
http://www.dot.state.nm.us/content/nmdot/en/Standards.html

Design mix of each class of concrete, unless LANL pre-approved mix design is used.

Laboratory test reports for design mix for concrete, unless pre-approved mix design is used.

Batch tickets.

Test Reports of Concrete Field Testing (except per 3.4.E)

RELATED SECTIONS

Section 31 2000 - Earth Moving

Section 03 3001 - Reinforced Concrete

QUALITY ASSURANCE

Perform work, materials and construction requirements, in accordance with the NMDOT SSHBC, Section 608, Sidewalks, Drive Pads, and Concrete Median Pavement and NMDOT SSHBC Section 609, Curb and Gutter.

Furnish and place concrete in conformance to the NMDOT Supplemental SSHBC Section 510.

JOB CONDITIONS

Do not place concrete when base surface temperature is less than 40 degrees F.

Perform concrete washout, trucks and mixers, in a designated and controlled area to prevent the runoff of washout material and the co-mingling of unset concrete with storm water.  Properly dispose of all hardened concrete.

PRODUCTS

  - MATERIALS

Provide materials and construction requirements for forms, concrete, joints, and required accessories conforming to NMDOT SSHBC Section 608, Sidewalks, Drive Pads, and Concrete Median Pavement and NMDOT SSHBC Section 609, Curb and Gutter.

ACCESSORIES

Joint Fillers shall be preformed and conform to the requirements of AASHTO M33 or M153.

  - CONCRETE MATERIALS

    - Cement: ASTM C 150, Type I or Type II.

    - Fine and Coarse Aggregates: Conform to ASTM C 33.

    - Water: Potable water that is clean and not detrimental to concrete.

    - Fly Ash: Conform to ASTM C 618, type F.

  - ADMIXTURES

    - Air Entrainment: Conform to ASTM C260.

    - Chemical: Conform to ASTM C494.

  - CONCRETE MIX

    - Standard Mix Design

      - The standard mix design for LANL shall contain a minimum of 20% by weight of total cementitious material Type F fly ash conforming to ASTM C 618 for mitigating the deleterious effects of alkali-silica reaction in concrete that is common with the siliceous nature of aggregates found in Northern New Mexico.  (The pre-approved LATM mixes meet this standard mix design).

    - Provide concrete meeting the following criteria:

      - Exterior Concrete Exposed to Freezing and Thawing:

        - Minimum compressive strength, f ’ c : [4,000 psi @ 28 days].

        - Maximum nominal aggregate size: [0.75 in.]

        - Maximum water / cement ratio: [0.45]

        - Slump: [4 inch]

        - Air content: [6] percent.

      - Exterior Concrete to be Pumped, Exposed to Freezing and Thawing:

        - Minimum compressive strength, f ’ c : [4,000 psi @ 28 days].

        - Maximum nominal aggregate size: [0.75 in.]

        - Maximum water / cement ratio: [0.38].

        - Slump: [6 inch] at discharge of truck.

        - Slump: [3 to 7 ½ inch] at pump discharge.

        - Air content: [6] percent.

      - Interior and Below Grade -- Fill Concrete, Thrust Blocks, Anchors, Cradles, and Encasement, with Minimum Two Feet of Cover (not Exposed to Freezing and Thawing):

        - Compressive strength, f ’ c : [3,000 psi at 28 days].

        - Maximum nominal aggregate size: [0.75 inch].

        - Maximum water/cement ratio: [0.44].

        - Slump: [4 inch.]

        - Air content: [3] percent.

Pre-approved LATM Design Mixes (Ref: AMEC Project No. 4-519-003279).  These mix designs can be used as long as material properties remain constant (LANL will verify this periodically).

- LATM Mix No. 19 -- Exterior, 4,000 psi concrete, 4" slump, 5% air +1.5% tolerance (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) , minimum 20% fly ash (proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras 	656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water	295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz #67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer:  Mb poly heed 997    	 41 oz(1)

Air Entraining Agent: MB Micro Air,    	8.2 oz(2)

- LATM Mix No. 44 -- Exterior, 4,000 psi concrete to be pumped, 6" slump, 5% air +1.5% tolerance (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete), minimum 20% fly ash (proportions per CY) :

Type I-II Cement: Gcc Rio Grande, Tijeras	 656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water	 295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz #67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer, Mb poly heed 997	 57.4 oz(1)

Air Entraining Agent: MB Micro Air,	   8.2 oz(2)

- LATM Mix No. 20 – Interior and below grade, 3,000 psi concrete, 4" slump, 3% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), minimum 20% fly ash (Proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 417 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 104 lbs

Water	 268 lbs

Washed Concrete Sand:  El Guique Quarry	           1378 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	           1765 lbs

Water Reducer, Mb poly heed 997	20.8 oz(3)

Air Entraining Agent: MB Micro Air,	 2.6 oz(4)

Note (1): Temperature and slump variation may require adjustment in dosage within the range of 24.6 fl oz / cy to 57.4 fl oz / cy

Note (2): Temperature and slump variation may require adjustment in dosage within the range of 1.025 fl oz / cy to 12.3 fl oz / cy

Note (3): Temperature and slump variation may require adjustment in dosage within the range of 15.6 fl oz / cy to 36.5 fl oz / cy

Note (4):  Temperature and slump variation may require adjustment in dosage within the range of 0.65 fl oz / cy to 7.8 fl oz / cy

- LATM Mix Class A -- Exterior, 3,000 psi concrete, 3.5" +/-1” slump, design 6.5% air +1.5% tolerance (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) , 28.2% fly ash by wt. of cement (Proportions per CY):

Type I-II Cement: GCC Rio Grande, Tijeras 	440 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 124 lbs

Water	263 lbs

Washed Concrete Sand:  El Guique Quarry	1176 lbs

Sz #67 Coarse Aggregate: El Guique Quarry	1764 lbs

Water Reducer:  Mb Polyheed 997    	 50.8 oz

Air Entraining Agent: MB Micro Air,    	9.0 oz

- LATM Mix Class AA -- Exterior, 4,000 psi concrete, 3.5" +/-1” slump, design 6.5% air +1.5% tolerance (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete), 28.2% fly ash by wt. of cement (Proportions per CY) :

Type I-II Cement: GCC Rio Grande, Tijeras	 560 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 158 lbs

Water	 280 lbs

Washed Concrete Sand:  El Guique Quarry	 990 lbs

Sz #67 Coarse Aggregate: El Guique Quarry	1759 lbs

Water Reducer, Mb Polyheed 997	 64.6 oz

Air Entraining Agent: MB Micro Air,	   18.7 oz

- LATM Mix Class F – Exterior (Slip Form), 3,000 psi concrete, 1.5" +/-1” slump, design 6.5% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 33.4% fly ash by wt. of cement (Proportions per CY):

Type I-II Cement: GCC Rio Grande, Tijeras	 461 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 154 lbs

Water	 258 lbs

Washed Concrete Sand:  El Guique Quarry	           1100 lbs

Sz #67 Coarse Aggregate: El Guique Quarry	           1795 lbs

Water Reducer, Mb Polyheed 997	65.2 oz

Air Entraining Agent: MB Micro Air,	 24.6 oz

EXECUTION

  - INSPECTION

Verify compacted, treated base is ready to support concrete and imposed loads.

Verify grades and elevations of base are correct.

Verify forms are set to the required grade and alignment and extend to the required depth.

PLACING CONCRETE

Notify the LANL Subcontract Technical Representative (STR) a minimum of 48 hours prior to commencement of concreting operations.

Ensure that reinforcement, inserts, embedded parts, fence posts, formed joint fillers, joint devices, and formwork are not disturbed during concrete placement.

Concrete shall be placed in the forms in one layer.  The concrete shall be consolidated with an approved vibrator, and the surface shall be finished to grade with a strike off.

Install joint fillers, primer and sealant in accordance with manufacturer’s instructions.

Install joint devices in accordance with manufacturer’s instructions.

Place concrete continuously between predetermined expansion, control, and construction joints.

Concrete Finishing

The surface shall be finished true to grade and section with a wood float or darby to a smooth and uniformly fine granular or sandy texture free of waves, irregularities, or tool marks.  Sidewalks shall receive a scored surface produced by brooming with a fiber-bristle brush in a direction transverse to that of the traffic, followed by edging.

All slab and sidewalk edges, including those at formed joints, shall be finished with an edger having a radius of 1/4 inch.

Finished concrete slab surfaces shall be free from irregularities.  Check and ensure that the slab has the proper crown, slope, and/or grade.  Trueness shall not vary more than 1/4 inch from the testing edge of a 10-foot straightedge.

Finished concrete sidewalks and curb and gutters shall be free from irregularities.  Check and ensure that the sidewalks, curb and gutters, and medians have the proper crown, slope, and/or grade.  Do not allow the surface of concrete sidewalks, curb and gutters, and medians to deviate more than 1/4 inch (in any direction), if tested with a ten (10) foot straightedge.

Slope top of concrete fence post bases to provide positive drainage.

Finish thrust blocks to the extent where surface voids are eliminated.

CurING AND PROTECTION

Immediately after placement, protect concrete from premature drying, excessively hot or cold temperatures and mechanical injury.

Use all applicable practice and recommendations:  for hot weather concrete application, from ACI 305.1; for cold weather concrete applications from ACI 306.1; for curing from ACI 308.1.

FIELD QUALITY CONTROL

Provide a certified testing agency to perform field testing in accordance with ACI 301.

Testing agencies performing testing services on concrete materials shall meet the requirements of ASTM C 1077.  Test agency must be approved by LANL Building Official; listing of pre-approved agencies is here http://engstandards.lanl.gov/ESM_Chapters.shtml#esm16

Field testing of concrete shall be performed by an ACI Certified Concrete Field Testing Technician – Grade I.

Notify the LANL STR 48 hours in advance of field testing to allow for witnessing of testing.

The testing agency shall perform the following tests and collect strength cylinders on one batch in every 50 cu. yards of concrete placed or once a day when less than 50 cu. yards is placed.

Record temperature of concrete in accordance with ASTM C 1064.

Perform slump test in accordance with ASTM C 143.

Perform air content test in accordance with ASTM C 231, pressure method.

Take 4 concrete strength test cylinders in accordance with ASTM C 31.

The testing agency shall test the strength test cylinders in accordance with ASTM C 39 at 7 days and 28 days.

Concrete to be used for nonstructural purposes that comprises a total quantity of less than 2 cu. yds. (i.e., per project) does not require field testing provided the concrete is mixed per manufacturer’s instructions or approved mix design parameters as reflected by the mix ticket.  For the purposes of this testing exclusion, "nonstructural" will be taken to mean concrete on or below the ground surface that will not adversely affect life safety and does not require a structural design.  Examples of such concrete that meet this definition of nonstructural include sidewalks, curbs and gutters, thrust blocks, valve boxes and test box collars, post and pole anchorage when 8 feet in height or less, and manhole collars in non-vehicle-traffic-bearing areas.

DEFECTIVE CONCRETE

Defective concrete is concrete not conforming to strength requirements, not being free from excessive cracking, discoloration, form marks, tool marks, honeycombs, embedded debris, or otherwise non-consistent with the overall appearances of the work.

Do not accept or place defective concrete that is not in conformance with acceptance criteria.  Return the fresh concrete to the supplier.

Replace defective concrete not meeting appearance criteria, at Subcontractor’s expense.  The STR may allow repair of defective concrete at Subcontractor’s expense.

Replace concrete not in conformance with details, tolerances, and other construction requirements at Subcontractor’s expense.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 03 3053 Rev.8, dated June 29, 2015.