SECTION 05 0520
POST-INSTALLED CONCRETE AND GROUTED-MASONRY ANCHORS—
NORMAL CONFIDENCE
*************************************************************************************************************

LANL MASTER SPECIFICATION

This section supersedes LMS 03 1534.  It includes field installation and inspection requirements for normal-confidence post-installed (PI) anchors.  These inspection requirements are not to be confused with the Special Inspections required by associated ICC-ES reports (ESRs), which should appear in a project’s Statement of Special Inspections.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Structural POC.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This section was developed for ML-3 and ML-4 projects.  For ML-3 applications, additional requirements may be added if additional confidence is desired.  Section 05 0521, which is intended for ML-1 and ML-2 installations, has examples of possible changes that can be made to increase confidence, or it may be used as the starting point when the utmost confidence is desired.  At a minimum, for ML-3 applications, it is recommended that testing be mandated in this section to provide added assurance as opposed to increased rigor on procurement.1

This section is not required for anchors meeting the definition of “Seismically Exempt Anchors”2 contained in ESM Chapter 5 Section II Appendix A; however, seismically exempt anchors must (1) still comply with the portions of Appendix A that aren’t related to design for seismic forces, (2) be identified as such on the construction drawings and, if applicable (3) indicate the respective evaluation report and that its limitations for use in only uncracked concrete and in SDCs A and B isn’t applicable.  See author’s note in the PART-1 Article, Definitions, for further explanation.

ESM Chapter 5 Section I includes a crosswalk that helps technical personnel transition from PC categories to RC categories used herein.

1	In accordance with ACI 355.2 paragraph R13.3.4, for ML-3 and/or RC-IV applications using adhesive anchors, regardless of whether or not testing is mandated herein (i.e., ‘quality control’), it is recommended that testing be mandated in the Statement of Special Inspections (i.e., ‘quality assurance;’ ref. ESM Ch. 16, IBC-IP, Att. B*).

* As indicated in Attachment B/SSI template, per their respective ESRs, certain adhesive anchors REQUIRE this ‘QA testing’ in certain applications.

2	The term “non-structural anchors” was used in these documents prior to Nov 2014 editions.

*************************************************************************************************************

PART 1 GENERAL

# SECTION INCLUDES

- The technical requirements for purchasing post-installed (PI) concrete anchors for Management Level [ML-3 and] ML-4 and Risk Category (RC)-1 through RC-IV structures, systems, and components (SSC). This specification applies to expansion, adhesive, undercut, and screw.

- The technical requirements for field installation, inspection and testing of PI anchors (including anchor systems consisting of steel reinforcing bars/dowels and grout) in concrete and grouted masonry for Management Level (ML) 3 and 4, and RC-I – RC-IV SSCs. The inspection requirements of this section do not apply to Seismically Exempt Anchors (LANL definition).

- Does not cover cast-in-place anchors, design of PI anchorage, or purchase of tools or equipment required for installation or testing.

# RELATED SECTIONS

- 01 4000 Quality Requirements.

- [03 6000 Grouting:  All requirements (e.g., submittals, quality control, products, installation, etc.) for grout used as indicated in PART 3 herein.]

- [04 2220 Reinforced Unit Masonry:  Installation requirements for repointing as indicated in PART 3 herein.]

- [05 0521 Post-Installed Concrete Anchors—High Confidence.]

- [05 1000 Structural Metal Framing:  Baseplates, bearing plates, leveling plates.]

# DEFINITIONS

- Definitions of anchors per ACI 355.2 (as amended by ICC-ES AC 193) and ACI 355.4 (as amended by ICC-ES AC 308) apply, and all notations are identical to those used in those documents and in ACI 318 Chapter 17.  Where additional terms or notations are used, their definitions are included in this section.

- Attachment/Baseplate/Fixture:  The component/element, in-between the exposed anchor nut and the surface of the concrete/masonry, that is to be anchored (via execution of this section), which is represented herein by the word, “fixture.”

- Evaluation Report (ER):  Document prepared by an internationally-recognized, independent, third-party evaluation agency that attests to the compliance of a given product with the International Building Code (IBC).  Examples of such reports include ICC-ES Evaluation Service Report (ESR), and IAPMO Uniform Evaluation Service (UES) Report.

- LANL STR: LANL Subcontract Technical Representative.

- Reinforcing Steel:  Rebar.

****************************************************************************************************

If the Project includes Seismically Exempt Anchors, they must be identified as such by the Engineer of Record (EOR) on the construction drawings.  If the Project does not include Seismically Exempt Anchors then delete bracketed text.

Furthermore, per CIR-16-002, PI Concrete Anchors, Seismically Exempt (planned for incorporation into ESM Ch 5 Section II), PI-anchor products limited by independent, 3rd-party evaluation reports to use in uncracked concrete in Seismic Design Categories (SDCs) A and B only (e.g., Hilti KB3 in ICC-ES ESR-2302, etc.) may be used at LANL (which is SDC D) for anchorage of seismically-exempt nonstructural components (defined by ESM Ch 5/ASCE 7 Ch. 13).  In order for a project to take advantage of this, in addition to identifying the anchor(s) as being seismically exempt on the drawings, the EOR shall also indicate the respective evaluation report and that its limitations for use in only uncracked concrete and in SDCs A and B isn’t applicable.

Prior to concluding an anchor is seismically exempt, ensure LANL ESM Chapter 5, Sect. II, Appendix A, “Consequential Damage” para. has been considered (e.g., interactions, 2-over-1).

***************************************************************************************************

- Seismically Exempt Anchors are defined in Engineering Standards Manual (ESM) Chapter 5, Section II, Appendix A.  They are used to anchor nonstructural components that meet one of several “exemptions” provided in the definition.  The nonstructural component(s) and the associated exemption(s) that these anchors are used for in this Project are as indicated below.  These anchors must comply with applicable provisions of Appendix A (i.e., requirements that aren’t related to design for seismic loads), to include design and installation in accordance with the respective ER unless modified by LANL; and their use must not conflict with the Conditions of Use in such reports.

The Seismically Exempt Anchors in this Project are used to anchor ______.  [This] [These] nonstructural component[s] meet[s] the following exemption[s]:

        - ___________

        - ___________

        - ___________]

**********************************************************************************************************

If Project includes an anchorage system consisting of grout and concrete reinforcing steel (i.e., rebar/dowel) then the EOR must ensure completion of the following:

- Design calculations for the anchorage system(s) in accordance with applicable portion of ACI 318.

- Specification of the elements of anchorage system(s) consistent with design calcs:

    - 03 6000 Grouting, used (i.e., edit template and include in Project Spec) and its strength stated.

    - The rebar specified by editing Anchoring-Products paragraph (below).  If the rebar will be welded to (after installation), see ACI 318, para. 3.5.2.

- The requirements for the installation of the anchorage system are included herein in the PART-3 Article, Installation of Grouted Anchors.

*************************************************************************************************************

# REFERENCES

| ACI 355.2 | Qualification of Post-Installed Mechanical Anchors in Concrete |
| --- | --- |
| ACI 355.4 | Qualification of Post-Installed Adhesive Anchors in Concrete (ACI 355.4) and Commentary |
| ACI 318 | Building Code Requirements for Structural Concrete and Commentary |
| ASTM A 36 | Standard Specification for Carbon Steel |
| ASTM A 193 | Standard Specification for Alloy-Steel Bolting Materials for High-Temperature or High Pressure Service and Other Special Purpose Applications |
| ASTM A 615 | Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement |
| ASTM C 90 | Standard Specification for Loadbearing Concrete Masonry Units |
| ASTM E 3121 | Standard Test Methods for Field Testing of Anchors in Concrete or Masonry |
| ASTM F 436 | Standard Specification for Hardened Steel Washers |
| IBC | International Building Code |

Other ICC Documents

| ICC-ES Reports ICC ESR-1056 ICC ESR-1385 ICC ESR-1396 | International Code Council Evaluation Services Reports (ESRs) Simpson Strong-Tie Titen HD Screw Anchors Hilti Kwik Bolt 3 Masonry Anchors Simpson Strong-Tie Wedge-All Anchors |
| --- | --- |
| ICC ESR-1545 | Hilti HSL-3 Carbon Steel Heavy Duty Expansion Anchors for Cracked and Uncracked Concrete |
| ICC ESR-1546 ICC ESR-1678 ICC ESR-1702 | Hilti HDA Carbon Steel and Stainless Steel Metric Undercut Anchors in Concrete Wedge-Bolt+ Screw Anchors in Masonry (Dewalt / Powers) Mitek / USP CIA-GEL 7000 Epoxy Anchor System |
| ICC ESR-1917 | Hilti Kwik Bolt TZ Carbon and Stainless Steel Anchors in Cracked and Uncracked Concrete |
| ICC ESR-2502 | Power-Stud+ SD2 Carbon Steel Anchors, Power-Stud+ SD4 Stainless Steel Anchors and Power-Stud+ SD6 Stainless Steel Anchors in Cracked and Uncracked Concrete (Dewalt / Powers) |
| ICC ESR-2818 | Power-Stud+ SD1 Expansion Anchors in Masonry (Dewalt / Powers) |
| ICC ESR-2966 | Power-Stud+ SD1 Expansion Anchors for Cracked and Uncracked Concrete (Dewalt / Powers) |
| ICC ESR-3187 ICC ESR-3027 ICC ESR-3814 ICC ESR-4143 | Hilti HIT-HY 200 Adhesive Anchors and Post Installed Reinforcing Bar Connections in Concrete Hilti Kwik HUS-EZ (KH-EZ), Kwik HUS-EZ P (KH-EZ P), Kwik HUS-EZ E (KH-EZ E), and Kwik HUS-EZ I (KH-EZ I) Carbon Steel Screw Anchors for Use in Cracked and Uncracked Concrete Hilti HIT-RE 500 V3 Adhesive Anchors and Post Installed Reinforcing Bar Connections in Concrete Hilti HIT-HY 270 Adhesive Anchor System International Code Council ES Acceptance Criteria |
| ICC-ES AC 01 ICC-ES AC 58 ICC-ES AC 106 ICC-ES AC 193 | Acceptance Criteria for Expansion Anchors in Masonry Elements Acceptance Criteria for Adhesive Anchors in Masonry Elements Acceptance Criteria for Predrilled Fasteners (Screw Anchors) in Masonry Acceptance Criteria for Mechanical Anchors in Concrete Elements |
| ICC-ES AC 308 | Acceptance Criteria for Post-installed Adhesive Anchors in Concrete Elements |

# ACTION SUBMITTALS

- Verification Documents

The following verification documentation shall be submitted by the supplier for any anchors not in Tables 1 and 2, Examples of Approved Concrete Anchors and Examples of Approved Grouted-Masonry Anchors, respectively:

  - Submit the ER for each product.

  - Submit technical documentation of the product, including, but not limited to: anchor design strength in shear and tension, minimum spacing and edge distances, anchor dimensions, materials and coatings used, installation instructions, and all required design parameters.

  - For adhesive anchors, also submit information on adhesives, including, but not limited to: characteristic bond stress, elevated temperature versus load capacity effects (80–350(F), fire resistance, radiation effects, sunlight exposure effects, adverse chemical reactions, storage instructions, missing system, injection systems, mixing rations, gel time, setting time, shelf life, and hole drilling and cleanliness requirements.

  - For adhesive anchors, also submit information as applicable on anchor element (e.g., threaded rod, deformed reinforcing bar, etc.), including geometry, shape, material properties, and any special requirements.

  - Submit shipping, handling, and packaging procedures as described in the related PART 1 article below.

  - Submit cleaning and coating documentation for review.

  - Submit quality assurance program to meet requirements of the related PART 1 article below.

  - Certificates of Compliance certifying that the anchors meet the requirements of this specification.

# QUALITY ASSURANCE

- All material shall be procured as commercial material. The same quality assurance requirements shall be passed down to any lower tier Subcontractor.

- The installation (and associated design) shall be in full compliance with the “Installation” and “Conditions of Use” sections of applicable ER.  Any departures must be acknowledged per the variance process of ESM Chapter 1 Section Z10.

- The inspection, testing, and documentation requirements for same contained herein are the responsibility of the Subcontractor installing PI anchors (i.e., versus the PI-anchor inspection requirements contained in a project’s Statement of Special Inspections, which is the responsibility of the LANL Special Inspector).

- To reduce delays and potentially redundant LANL inspection effort, notify LANL Inspectors at least 24 hours prior to any Subcontractor installation, inspection, or testing activities associated with Special Inspection and treat such tasks as hold/witness points.

## PACKAGING, SHIPPING, HANDLING, AND STORAGE

- Establish and maintain controls for material handling and storage during fabrication and preparation for shipment to prevent damage and deterioration.

- Prior to packaging an item, remove dirt, oil residue, water, metal chips, or other contamination.

- If nuts, washers, sleeves and anchors are packaged and shipped unassembled, any components that are damaged during handling, shipping and storage, or that don’t fit properly (upon assembly during anchor installation), shall be replaced at no cost to LANL.

- Anchors of different types and/or different sizes shall be packaged separately.

PART 2 	PRODUCTS

## Anchor types including nuts and washers: expansion, adhesive, screw, and undercut.

*************************************************************************************************************

The products tabulated below are NOT the only ones that are allowed to be used at LANL.  Any product that complies with ESM Chapter 5 Section II can be used.

Conversely, the use of a tabulated product does NOT, in and of itself, ensure compliance with ESM Chapter 5 Section II.

Here are examples of typical items for which an ESR must be initially screened when considering a particular anchor product for use on a Project:

- IBC edition applicable to Project Code of Record must be included in Evaluation Scope (Section 1.0).

- Intended use of product must be consistent with Uses (Sect. 2.0).

  - Amongst other things, this includes use in cracked/uncracked concrete, or masonry.

    - At the time of writing, there are no products that can be used in cracked masonry.

- Product must not be precluded from use in either resistance to seismic loads, or in SDC D, in Conditions of Use (Sect. 5.0).

- If product is to be used outdoors, such must not be precluded by Conditions of Use.

Here is one (1) additional ‘initial-screening’ item that applies only to grouted-masonry anchors:

- Evidence Submitted (Section 6.0) must indicate one of ICC-ES AC01, AC58, or AC106.

Once the initial screening is completed, here are examples of items to be alert for that can cause problems during Title II and/or III:

- Some ESRs indicate that a ductile anchorage design cannot be achieved with some portions of a product (e.g., the smallest diameter of a particular screw anchor, the smallest diameter of anchor element of a particular adhesive anchor, etc.).  If such a product is selected for use, the EOR must ensure that the design/analysis complies with the provisions for non-ductile anchorage design.   .

- Some adhesive-anchor ESRs allow more than one type of drill to be used (for creating anchor hole) during installation (i.e., hammer drill vs core dill), and the type of drill selected for use affects the bond strength that the anchor can achieve.  Thus, EOR must select the drill type, design/analyze the anchor based on the applicable bond strength (for the drill type selected), and then indicate the drill type on the Project Record Documents.

- IBC Sect. 2204, Connections, includes an anchor provision that says, “…the protrusion of the threaded ends through the connected material shall fully engage the threads of the nuts…”  If the EOR doesn’t ensure that the product designed and specified is available in a length adequate to satisfy this provision then the Project could experience delays during construction.

*************************************************************************************************************

*************************************************************************************************************

In rad and cleanroom areas, consider using the Hilti HIT-HY 200 adhesive-anchor product since it can be installed without blowing dust from the hole that, in turn, must be vacuumed.  PART-3 Article PREPARATION indicates a product that collects dust.

*************************************************************************************************************

*************************************************************************************************************
Edit Table 1 and/or 2 in accordance with Project’s structural design and drawings.  If deleting either, also edit 1.5.A submittals reference to same.
*************************************************************************************************************

Table 1

Examples of Approved Concrete-Anchors

| Anchor Type | Manufacturer | Product Name | Evaluation Report |
| --- | --- | --- | --- |
| Expansion: |  |  |  |
| Drop-in | not allowed | n/a | n/a |
| Heavy-Duty Sleeve | Hilti | HSL-3 | ESR-1545 |
| Wedge | Hilti | Kwik Bolt TZ | ESR-1917 |
| Wedge | Powers | Power-Stud+ SD2 Carbon Steel Anchors, and SD4 and SD6 Stainless Steel Anchors | ESR-2502 |
| Wedge | Powers | Power-Stud+ SD1 | ESR-2818 |
| Adhesive | Hilti | HIT-RE 500 V3 | ESR-3814 |
| Adhesive | Hilti | HIT-HY 200 | ESR-3187 |
| Screw | Hilti | Kwik HUS-EZ | ESR-3027 |
| Undercut | Hilti | HDA1 | ESR-1546 |
| Undercut | Powers | Atomic+ | ESR-3067 |

1  Hilti HDA designed/installed per Section 05 0521 for ML-1/2 and NDC-3 may not be used in lower NPH Design/Risk-Category installations (e.g., this section) without the permission of the LANL STR.

Table 2

Examples of Approved Grouted-Masonry Anchors

| Anchor Type | Manufacturer | Product Name | Evaluation Report |
| --- | --- | --- | --- |
| Expansion: |  |  |  |
| Drop-in | not allowed | n/a | n/a |
| Wedge | Hilti | Kwik Bolt (KB) 3 | ESR-1385 |
| Wedge | Simpson | Wedge-All | ESR-1396 |
| Wedge | Powers | Power-Stud +SD1 | ESR-2966 |
| Adhesive | USP | CIA-GEL 7000 | ESR-1702 |
| Adhesive | Hilti | HIT-HY 270 | ESR-4143 |
| Screw | Simpson | Titen HD | ESR-1056 |
| Screw | Powers | Wedge-Bolt+ | ESR-1678 |

- anchorING products

- Mechanical anchors: undercut, expansion (heavy-duty sleeve, and wedge), and screw anchors.

- Adhesive anchor systems.

- All material shall be commercial material.

- Anchors shall have a current ER that contains recommended design capacities.

  - Load tests used in the ERs for concrete anchors shall be performed in accordance with ICC AC 193 for mechanical anchors; and AC 308 for adhesive anchors.

  - Load tests used in the ERs for grouted-masonry anchors shall be performed in accordance with ICC AC 01 for mechanical anchors; AC 58 for adhesive anchors; and AC 106 for screw anchors.

- Provide carbon steel or stainless steel anchors as specified. Submit documentation of materials used.

- Outdoor anchors, or those used in a moist environment, shall be of a material, or possess a protective coating, compliant with the associated Condition of Use in the respective ER.

- Anchor head shall be stamped, or otherwise permanently marked, with the total anchor length of a length code that can be related to the total anchor length.

- Anchor head, nut, or washer shall not be marked with a letter “Q” or be marked with the color blue. If the letter “Q” is contained in the length code, those anchors shall be excluded from use.

- [Rebar/dowel:  ASTM A 615, grade 60 deformed bars.]

## TEST AND INSPECTIONS

- The anchor supplier is responsible for performing inspections, as necessary to ensure compliance with all material and documentation requirements identified in this Specification. Documentations of inspections will be available to LANL if requested.

- LANL representative shall have the option of inspecting anchors for finish, workmanship, and dimensional tolerances before any shipment is made.

- Materials that are not properly marked, have poor workmanship, are corroded, have defective threads, or are improperly documented shall be rejected.

## ACCESSORIES

  - In rad and cleanroom areas, for both concrete and grouted masonry, the creation of dust from hole cleaning/blow-out (during anchor installation) is normally prohibited.  If such is the case, and a “non-dust-creating anchor (e.g., Hilti Safe-Set used with HIT-HY 200, etc.)” isn’t specified/indicated for use, and a dust-collection/vacuum device isn’t available, a dust-collector/vacuum shall be purchased*.

*NOTE:  Hilti Item No. 362323, dust-collection hood, is a vacuum attachment.

PART 3    EXECUTION

# INSTALLERS

- Implement and document a training and/or qualification program for installers. Installers shall be trained on, and made fully familiar with, the manufacturer’s printed installation instructions (MPII) *, additions from the associated ESR(s), and additional requirements as noted herein (follow most stringent in the event of a conflict).

* NOTE:  The applicable MPII is that which is specific to the anchor type and designation.  MPII for a given type of anchor type can vary from one designation to another (e.g., Hilti HDA pre-set vs. HDA through-set, etc.).

# GENERAL

*************************************************************************************************************

Since the design and performance of PI anchorage is dependent upon the (1) concrete type (i.e., normal- vs. light-weight), (2) compressive strength (i.e., f’c) and (3) thickness, these properties/data are included in the Special Inspections section of the ESRs for these products, as well as appended Table A1.  Given this, and the fact the installer and inspector might not know these properties (particularly for projects on/in existing structures), the EOR must indicate them on the construction drawings for every location in which an anchor is to be installed.  In the event that none of these properties change from one anchorage location to another, the EOR need only indicate the ‘concrete properties associated with PI anchors’ once on the drawings. Document the source/bases for these data in the anchorage calculation.

This applies to grouted-masonry anchors also (e.g., masonry unit type, grout and mortar compressive strengths, masonry thickness, etc.).  See appended Table A2 and the respective ESR for details on performance-affecting attributes that must be specified/indicated.  Table items that are blank (__) shall be filled in per the respective ESR.

*************************************************************************************************************

- The installation of anchors shall be restricted to the applications and installations indicated. Construction aids are exempt from this requirement.

- The effective embedment depth (hef); and the minimum values of spacing, and edge distance shall be as indicated.

*************************************************************************************************************

The EOR must ensure that the product designed and specified is available in a length adequate to satisfy the following IBC (Ch. 22) “nut-thread-engagement provision.”  Otherwise the project will likely experience delays and/or additional costs.

*************************************************************************************************************

- The nut thread engagement for an anchor stud shall be such that the threads are flush with, or project beyond, the outside face of the nut when completely installed.

- Nuts and washers for anchors that are lost or damaged during installation shall be replaced with respective manufacturer’s specified component or equivalent as pre-approved by the LANL STR.

- Concrete anchors shall not be installed in new, “28-day-mix concrete” until it has cured for at least seven (7) days, and shall not be loaded until the concrete has attained its minimum specified design strength.

***********************************************************************************************************

Retain following para. only if project includes adhesive anchors either of the following apply:

1.  	Design uses minimum characteristic bond stress(es) from ACI 318 Table 17.4.5.2, or,

2.   	Design uses a characteristic bond stress(es) from an ESR, and any/all of the parameters/conditions therein differ from the default values in the subparagraph.

***********************************************************************************************************

- For adhesive concrete anchors, the concrete at the time anchor installation shall have a minimum 1) compressive strength of 2,500 psi, 2) age of 21 days, and 3) temperature of 50° F.  In addition, the concrete must be dry (vs. partially- or fully-saturated) at the time of installation if, at the time of installation, the anchors are protected from the environment/weather.  Finally, anchors shall be installed in holes drilled with a rotary impact drill or a rock drill.

- Grouted-masonry anchors shall not be installed in new masonry until it has cured for at least seven (7) days, and shall not be loaded until the masonry has attained its 28-day specified compressive strength.

- For grouted-masonry anchors, the masonry unit type, size, compressive strength, mortar, and grout compressive strength shall meet or exceed the properties indicated.

- Anchors shall be installed in sound concrete/masonry.  Surfaces showing obvious distress by way of porosity, disintegration, carbonation and cracks over 0.02 inches in width and 12 inches or longer and within the distance of hefN shall be reported to the LANL STR for evaluation.

- Anchors shall not be installed into the sides or bottoms of precast and pre-stressed T-beam stems without the pre-approval of the LANL STR.  Strand-cutting/nicking is prohibited.

- If concrete anchors through steel decking are indicated, and the anchorage includes a fixture that spans two (2) or more decking ribs/flutes, the resulting space(s) in-between the fixture and the decking shall not be filled, or have anything applied to the surfaces therein, unless such is indicated.

- Bending and welding of PI anchors, except grouted anchors, is prohibited.

# PREPARATION

- Anchors shall be installed in accordance with their respective MPII, including any/all components, devices, tools specified therein.*

* This includes “brand-name” drill bits, drills, setting tools, etc.

- Devices required for installation, inspection and testing (e.g., torque wrenches, hammer drills, manufacturer’s setting tools, etc.) shall be calibrated and controlled in accordance with LANL Procedure P330-2, Control and Calibration of Measuring and Test Equipment (M&TE), or equivalent.

- Obtain and comply with LANL Form 2074, Penetration Permit.

- Locate existing items in the concrete (that could interfere with proper and safe anchor installation, like rebar and other embedments) prior to drilling using a ground-penetration-radar (GPR) device.* Pilot holes shall be drilled with a carbide-tip bit to avoid rebar damage, and the depth of such holes shall not exceed 66% of the specified value of hef.

* NOTE:  Consider purchase of Hilti PS 1000 X-Scan Radar Detection System since it will locate more than just rebar, provides 2-D and 3-D visualization of concealed items, and is effective with concrete as thick as 12 inches.

- For safety, consider drill bits/drills that automatically shut off when the bit hits metal, particularly in older construction for which electrical configuration is not well-documented.

- Rebar cutting is only permitted with pre-approval by the LANL STR. Local* multi-cutting of the same bar is considered as one cut.  Rebar approved to be cut must be shown on as-built drawings at completion of Project.

  - The word “local” herein shall be taken to mean within the footprint of the fixture/baseplate.

  - If the manufacturer stipulates the use of particular devices for hole drilling and/or rebar-cutting then such shall be purchased and used.

- Rebar will be considered to be cut if:

  - For #4 through #7: Cuts, nicks, or drill into bar body is greater than 1/16”

  - For #8 and larger: Cuts, nicks, or drill into bar body is greater than 1/8”

Cutting of bar deformations is not considered a cut since the area of steel is not reduced.

- The installation of an anchor through cut rebar shall be performed in accordance with the manufacturer’s written procedure.  In the event that there is no such procedure, the anchoring mechanism shall be located at least two (2) anchor diameters clear beyond the cut rebar.

# DRILLING OF HOLES                 ****************************************************************************************************

The minimum concrete thickness can be a lot larger than hef.  And the drill-hole depth for many PI anchors also exceeds hef. Thus, EOR must ensure that the design-basis value of hef is actually achievable (in a manner that’s compliant with the entirety of the respective ESR).

****************************************************************************************************

  - Locations and embedment depths of anchors shall be as indicated.  The drill-hole diameters and depths shall be in accordance with the MPII unless otherwise specified herein.  Verify depth of the concrete meets or exceeds the minimum required before drilling holes, and contact the LANL STR in the event of a conflict between/amongst the various depths (i.e., hef, drill-hole, and concrete).

  - Drill holes for anchors in accordance with the MPII.

  - Clean drilled holes of chips, dust, loose material, and water prior to anchor installation.

# INSTALLATION OF ANCHORS

- Washers supplied with anchors shall be installed in all instances.  A supplementary/additional washer (i.e., a washer not supplied with anchor), if indicated for use, shall be installed underneath the washer supplied with the anchor. Supplementary washers may be trimmed to clear interferences. Per ASTM F 436, the trimmed edge shall not be closer than 7/8 of the anchor diameter from the center of the washer.

- Anchors shall be installed plumb, which is defined as follows: perpendicular to the nominal concrete surface within a + 5-degree tolerance. This criterion may be verified by visual inspection of the nut and washer being properly seated on the nominal surface of the fixture (i.e., flush all around).

*************************************************************************************************************

If project involves the use of undercut anchors, and the cone nut and stud are separable, retain the option at the end of following paragraph.

*************************************************************************************************************

- Care shall be exercised to avoid bending anchors to match baseplate holes, or loosening of anchors by prying sideways after tightening. [Care shall also be exercised to ensure that the cone nut of an undercut anchor does not become loose from the stud during the setting or tensioning operation.]

- When installing a concrete anchor in a grouted hole, the anchoring mechanism shall be located in “original concrete.” To ensure this occurs, the anchor setting/installation depth shall be at least two (2) anchor diameters or three (3) inches, whichever is greater, clear beyond the bottom of the grouted hole. If the depth of concrete won’t allow for setting/installation this deep, the LANL STR shall be contacted for an alternative.

- Grouted-masonry anchors shall not be installed pre-existing holes that have been grouted.

- The center-to-center distance between a new-concrete-anchor hole and an exploratory or unused hole, or an abandoned cut-off anchor, shall be at least three (3) times the diameter of the larger hole or one (1) inch clear distance of concrete between the holes, whichever is greater.

  - Exception: The clear-distance requirement (i.e., 1” of concrete between the holes) need not be considered if an exploratory/unused hole is grouted with a non-shrink grout specified in Section 03 6000 Grouting, the grout has attained the strength of the surrounding concrete, and if the center-to-center distance between the new hole and the exploratory/ unused hole, or abandoned anchor, is three (3) times the diameter of the larger hole.

- The center-to-center distance between a new-grouted-masonry-anchor hole and an exploratory or unused hole, an abandoned cut-off anchor, or an existing anchor shall be at least the minimum spacing indicated in the ER for the new grouted-masonry anchor.

*************************************************************************************************************

The intent of the minimum spacing indicated in the following paragraph are to ensure there’s no reduction in anchor capacity.

Summing the respective hef values is very conservative if/when hef for one anchor >> hef for the other. In such cases, it’s possible that there won’t be a reduction in capacity if the anchors are spaced closely enough (i.e., the concrete-breakout-failure prism of the “shallow anchor” might be contained within/not interact with that of the “deep anchor”).

Finally, the reason for the last sentence is because the “1.5hef + 15hef “ requirement comes from the Savanah River Site (SRS), and it’s based on their tabulation (in Guide 03251) of the capacities of several types, sizes, and shapes of anchors, which doesn’t include steel as strong as “A 193,” diameters > 5/8”, and hooked configuration/shape.

*************************************************************************************************************

- The center-to-center distance between a new concrete anchor and an existing anchor shall be at least the sum of 1.5 times the effective embedment depths of the new and existing anchors (i.e., 1.5hefN + 1.5hefE). If hefE can’t be determined, the minimum center-to-center distance shall be 1.5 times hefN plus 15 times the diameter of the existing anchor. If either of the two anchors is of ASTM A 193 material, or greater than 5/8” diameter, or if the existing anchor is a hooked (“J,” cast-in-place) anchor rod, contact the LANL STR for evaluation.

- Non-grouted fixtures installed with anchors may have a maximum 1/8-inch gap under exterior/perimeter edges provided there’s full bearing (on the concrete/ masonry surface) over the rest of the fixture and that the prescribed anchor installation/pretensioning torque can be applied. If the gap is excessive/too large, and/or the prescribed torque won’t result in complete/satisfactory anchor installation, one (1) of the following two (2) procedures shall be undertaken:

  - The concrete/masonry surface shall be reworked.

  - For gaps of up to one (1) inch, the fixture may be grouted per the following procedure:

    - Insert anchors and set the fixture.

    - Install nuts to finger-tight condition.

    - Install shims positioned no more than 1/2 inch away from the anchors to reduce gaps between fixture shims to 1/8 inch or less at anchor locations.

    - Apply prescribed installation torque slowly enough to determine whether or not the shims are close enough to the anchors. If initial torqueing results in downward bending of the fixture, the shims aren’t close enough. Untorque the anchors, and relocate the shims as necessary to permit re-torqueing without fixture bending.

    - Fill the gap with a non-shrink grout specified in Section 03 6000 Grouting leaving the shims in place. For fixtures on walls, where grouting is not feasible, the gap may be filled with shim plates. The shims may be stacked with up to four (4) shims per stack.

- Anchors that must be tensioned (via torque or direct tension) in order to be properly set/installed shall not be installed with leveling nuts beneath fixtures (in order to preclude interference with application of prescribed pretensioning/ installation torque).

# Additional Requirements for INSTALLATIO	N OF GROUTED CONCRETE ANCHORS

- In addition to the requirements in the PART-3 Article “Installation of Anchors,” grouted concrete anchors shall be installed in accordance with the requirements in this article.

- Holes shall be drilled as indicated.

  - For anchors up to 1 inch in diameter, provide 2-inch diameter hole in concrete.

  - For anchors greater than 2 inches in diameter, provide a hole at least 2 inches greater than the anchor diameter.

- Clean all surfaces of the anchor element of oil, grease, or other foreign material.

- The hole surfaces shall be wire brushed to clean them and to remove all loose particles. In addition, for core-drilled holes with diamond-tip bits, the holes shall be visually examined to confirm that there is no smooth glazing on the hole surface, and the sides of the hole may be roughened, as required, to ensure proper bond. Remove all debris, dust, cement, and other foreign materials from the hole.

- Soak the hole to saturation with potable water, and keep damp for a minimum of six hours prior to grouting.  Immediately prior to grouting, remove all free surface water using oil-free compressed air, sponge, or vacuum.

- Anchors shall be properly positioned in the hole prior to grouting, and supported to maintain that position during grouting.

- Use a non-shrink grout specified in Section 03 6000 Grouting.  Mix and place the grout, in accordance with same.

- Cold bending of ASTM A 36 material prior to grouting is permitted if /when necessary to clear an interference(s) (i.e., embedded reinforcing steel and/or other types of embedded items) provided the axis of bent anchor is not more than 30 degrees from straight as shown in appended Figure A1, the surface of the anchor isn’t cracked, and subject to the following limitations.

  - Cold bending in the field shall not occur more than once per anchor.

  - Field-bent anchors shall not be straightened without pre-approval of LANL STR.

- Use nut and washer(s) indicated.  With respect to the “washer paragraph” in the previous PART-3 Article “Installation of Anchors,” if more than one (1) washer is indicated for an anchor, then “supplemental/additional washer” shall be taken to mean the washer in-between the fixture and the washer below the nut.

- If use of a nut above the fixture (i.e., on the anchor projection) is indicated, it shall be installed after the grout has fully cured and using an amount of torque that does not exceed that which is prescribed by the grout manufacturer.

- Additional Requirements for Installation of adhesive Anchors

  - In addition to the requirements in the PART 3 Article Installation of Anchors, adhesive anchors shall be installed in accordance with the following Paragraph.

  - For adhesive concrete anchors that are indicated as being horizontal or upwardly inclined and supporting sustained tension loads, installation shall be performed by personnel certified by the ACI/CRSI Adhesive Anchor Installer Certification program, or an equivalent program pre-approved by the LANL Building Official.

- RELOCATING FIXTURE

  - Unless otherwise indicated, a fixture may be relocated up to one (1) inch in any direction with respect to its principal axis in order to avoid interferences (i.e., embedded reinforcing steel and/or other types of embedded items).

- RELOCATING HOLES WITHIN FIXTURE

  - Individual anchor holes that haven’t yet been drilled in a fixture may be relocated in order to avoid interferences (i.e., embedded reinforcing steel and/or other types of embedded items) subject to the following limitations:

      - If tolerances or ranges aren’t indicated for them, anchor holes in the fixture may be relocated up to one (1) inch in any direction provided the anchor-spacing criteria, and edge-distance criteria for both the fixture and the concrete, will be met.

*************************************************************************************************************

The following subparagraph, to include the figure referred to therein, is based on AISC 360; therefore, if the fixture is something other than “AISC 360 material,” editing is required.

For example, if the fixture is cold-formed steel (CFS) then the applicable standard is AISI S100 (Ch. E). In this example, an edit merely replacing AISC 360 with AISI S100 wouldn’t suffice [unless appended Figure A2 and the related sentence(s) below are deleted].

*************************************************************************************************************

      - The minimum edge distance from the center of a hole to the edge of the fixture shall comply with AISC 360 Chapter J Table J3.4.  Alternatively, back-up bars, as shown in Figure A2 (appended herein), shall be used; back-up bars shall be field-cut from stock material to match that of the fixture.  Another alternative, if feasible/not otherwise prohibited, is to use a larger fixture size.

*************************************************************************************************************

The major difference between the following paragraph and the previous one is the existence of a hole(s): In former paragraph, the anchor hole doesn’t exist, while in the subsequent paragraph it does (as a result of the project or otherwise).

The 1st and 4th subparas. in the following para. are based on the fixture being AISC-360 material. With regard to the 1st subpara., AISC 360-16 Sect. J2.2 indicates that arc spot/puddle welds are similar to plug welds; however, prior to editing (from AISC 360 to AISI S100), EOR must research whether or not it’s permissible to close CFS holes with puddle welds and to drill new holes through such welds. And similar applies to the 4th subpara. (on flame cutting.)

*************************************************************************************************************

  - The relocation or abandonment of existing anchor holes in a fixture shall meet the following requirements:

      - Holes may be relocated by abandoning the existing hole and redrilling a new hole. The existing hole may be closed by plug welds, and the surface ground smooth. It is permissible to drill new holes through the hole that was plug welded.

      - If the existing fixture hole resulted in a drill hole in concrete, the minimum center-to-center spacing between a new concrete-anchor hole and an exploratory/unused hole stipulated in the PART-3 Article, “Installation of Anchors*,” shall be met.

* NOTE:  The Paragraph in “Installation of Anchors” that includes the minimum spacing referred to here also includes an exception. That exception is applicable here too (if the conditions associated with it are met).

      - If the existing fixture hole resulted in a drill hole in masonry, the minimum center-to-center spacing between a new grouted-masonry-anchor hole and an exploratory/unused hole stipulated in the PART 3 Article “Installation of Anchors,” shall be met.

      - Flame cutting of holes in the fixture is permitted provided that those holes are reamed and/or ground to the final required dimensions.

- INSPECTION [AND TESTING]

***********************************************************************************************************
For ML-3 anchors, it is recommended that testing also be mandated herein to provide added assurance as opposed to increased rigor on procurement.  Refer to the testing requirements contained in 05 0521 for examples of possible changes that can be made to increase confidence, or it may be used as the starting point when the utmost confidence is desired.

For ML-4 anchors, testing is required only for grouted concrete anchors; thus, the option in this article title (above), the Testing Para. (below), and the Test-Record Para. in the subsequent Documentation Article can be deleted if grouted concrete anchors aren’t applicable to project.

***********************************************************************************************************

  - Inspection

- Visually inspect each anchor using appended Tables A1 and/or A2, as applicable, to verify that installation was performed in accordance with this section.

- If visual inspection reveals that a tabulated provision isn’t met/satisfied, the infraction shall be remedied in a manner that’s consistent with the requirements of this section. If hole drilling has occurred, or if anchor installation has been completed, remediation might consist of anchor relocation, or anchor removal and replacement, in accordance with the subsequent Article, “Rework and Abandonment of Anchors, and Repair.”

- The inspection(s) and its results shall be documented in an Installation Inspection Record in accordance with the subsequent Article, “Documentation.”

  - Testing

      - Testing of grouted anchors that are permanent (e.g., not temporary construction aids, etc.) is mandatory and shall be witnessed by the LANL Construction Inspector.

*************************************************************************************************************

In the following subpara., indicate whether tension and/or shear load must be used during testing, and the amount(s) of the load(s),  The amount(s) of load indicated shall be 100% of the required tensile and/or shear strengths (i.e., Nu and/or Vu) .

Do not specify a load type (and load amount) if there’s no such demand (i.e., Nu and/or Vu).

************************************************************************************************************

      - The Proof-load method, in accordance with ASTM E 3121, shall be used for testing.  Testing may be performed either before or after installation of the fixture.  The amount of applied [tension] [and] [shear] load shall be [_____ pounds] [and] [_______ pounds][, respectively].

        - Post-test restoration:  If the fixture was removed, or if the nut was loosened, then the fixture and/or nut shall be restored to their pre-test condition in accordance with the following:

- Re-install the fixture.

- Clean the threads of the anchor projection and nut.

- Re-install the nut, tightening it to snug-tight.

- Re-perform testing.

        - Testing frequency:  Unless otherwise specified, the following test frequencies shall apply:

*************************************************************************************************************

With regard to the following subpara., if the project includes both RC III/ IV anchors and RC I/ II anchors, be sure the drawings indicate “which anchors are which.”

If the project only includes RC III/IV anchors or RC I/II anchors, in addition to removing brackets and deleting bracketed content accordingly, consider also deleting mention of the respective RC(s).

*************************************************************************************************************

          - Randomly select and test [50% of the RC III/IV anchors in each group][, and] [10% of RC I/II anchors in each group].

          - A group of anchors consists of a homogeneous population with respect to the anchors themselves and their installation conditions.

          - If the aforementioned criteria results in the number of anchors to be tested being less than one (1), a minimum of one (1) anchor shall be tested.

          - If the tested anchors can achieve/withstand the stipulated proof-load-method loads (and, as applicable, are acceptable per the post-test-restoration provisions), and the concrete surrounding/beyond the anchors doesn’t break out, the other anchors in the group shall be considered satisfactory.

          - If a test anchor fails, double the specified (above) percentage of the anchors in the respective group shall be tested. If another anchor fails, all remaining anchors in the group shall be tested.

      - The testing and its results shall be documented in a Testing Record in accordance with the following Article, “Documentation.”

# DOCUMENTATION

## Installation Inspection Record

### The Installation Inspection Record shall contain the information listed in appended Tables A1 and/or Table A2 (as applicable).

## Test Record

## The Test Record shall include, at a minimum, the requirements of Section 01 4000 Quality Requirements, the information listed in the Report section of ASTM E 3121, and the following information:

## Complete anchor identification (as stipulated in Table A1).

## General location of anchor and description of group represented.

## Method of testing.

## Test results (i.e., acceptable/satisfactory or failed/rejected).

## Names of inspector and installer (if two different people).

## Date of test.

## For anchors that failed/were rejected, location of anchor and type of failure/reason for rejection.

# REWORK AND ABANDONMENT OF ANCHORS, AND REPAIR

*************************************************************************************************************

Mention the numerous instances in which “Testing option” can be deleted if grouted anchors aren’t used.

*********************************************************************************************************

- When a concrete anchor(s) doesn’t meet the inspection criteria applicable during or after installation, or the testing criteria stipulated the previous Article, “Inspection [and Testing],” remediation shall include whichever of the following two (2) options applies. And such anchors shall be re-inspected [and retested] afterward:

      - Failure due to concrete breakout:

        - Remove the concrete debris and concrete damaged by the failure.

        - If the integrity of the concrete surrounding/beyond the damaged concrete is intact, it’s likely a replacement anchor can be installed in the same location (after repair of the damaged concrete).

        - Prior to repairing the concrete, contact the LANL STR for evaluation of the damage and approval of the proposed repair.

        - The replacement anchor shall have an embedment depth of at least two (2) diameters or three (3) inches, whichever is greater, beyond the depth of the damaged concrete. If the depth of concrete won’t allow for this embedment depth, the LANL STR shall be contacted for an alternative

      - Failure due to anchor breakage, slippage, or loosening; or due to inadequate anchor embedment, or inadequate installation (including but not limited to anchor bending that doesn’t comply with Table A1):

        - Remove the defective anchor*.

* NOTE 1:  Some products can be fully removed (e.g., Hilti HDA, etc.), while others can’t be (e.g., some wedge anchors will leave wedges behind, etc.).  Even if full removal is possible, the removed anchor shall not be re-used unless re-use is permitted by the manufacturer and LANL STR.

NOTE 2:  The Bolt Extractor, manufactured by Drillco Devices Ltd., can be purchased (if not available) and used to remove installed anchors.

        - If the integrity of concrete surrounding/beyond the defective anchor is intact, it’s possible that a replacement anchor can be installed in the same location (after the hole is re-drilled).

*************************************************************************************************************

With regard to the following subparagraph selection of the replacement anchor can vary from being straightforward to being challenging. On the one hand, in most instances, using an anchor one size larger* than the failed/defective anchor will suffice “on paper.”  On the other hand, in practice, if the options to choose from for a given product line are limited, selection of a replacement anchor could prove to be “a handful.”

* For some products, BOTH diameter AND embed depth must be larger (e.g., Hilti HDA, etc.).

*************************************************************************************************************

        - Prior to re-drilling the hole, contact the LANL STR for evaluation of the failure, removed-anchor location, and selection of the replacement anchor

        - If the location of the defective anchor can’t be re-used (due to inadequate concrete depth or integrity), grout the existing hole with a non-shrink grout specified in Section 03 6000 Grouting, and relocate the replacement anchor in accordance with the minimum center-to-center spacing between a new concrete-anchor hole and an unused hole stipulated in the prior Article “Installation of Anchors.”*

* NOTE:  The Paragraph in “Installation of Anchors” that includes the minimum spacing referred to here also includes an exception. That exception is applicable here, too (if the conditions associated with it are met).

          - If another relocation (i.e., subsequent to that described above) is believed to be necessary, prior to proceeding, obtain written permission from the LANL STR.

- When a grouted-masonry anchor(s) doesn’t meet the inspection criteria applicable during or after installation (listed in Table A2), remediation shall be as follows. And such anchors shall be re-inspected afterward:

  - Remove the defective anchor.*

* NOTE:  Some products can’t be fully removed (e.g., some wedge anchors will leave wedges behind, etc.).  Even if full removal is possible, the removed anchor shall not be re-used unless re-use is permitted by the manufacturer and LANL STR.

  - Grout the existing hole with a non-shrink grout specified in Section 03 6000 Grouting, and relocate the replacement anchor in accordance with the minimum center-to-center spacing between a new grouted-masonry-anchor hole and an unused hole stipulated in the prior Article “Installation of Anchors.”

    - If another relocation (i.e., subsequent to that described above) is believed to be necessary, prior to proceeding, obtain written permission from the LANL STR.

- Mislocated anchors, or anchors installed for temporary purposes, need not be removed if they do not interfere with project-related work (e.g., subsequent anchor or fixture installations, etc.), pose a safety hazard to personnel, or are not “aesthetically offending.” Unremoved mislocated anchors shall be cut off flush with the concrete/masonry surface.

  - Anchors that will be covered by a fixture may also be cut off flush with the concrete/masonry surface.

*************************************************************************************************************

Regarding the following “trimming paragraph,” for products that have an excess projection (i.e., a portion of the anchor/anchor element extending beyond the nut on top of the fixture), although removing excess projection does not affect structural integrity, if that projection has a length-indicator/head-marking on it, it will be lost.

The reason for requiring a thread projection after trimming is to ensure full nut-thread engagement (that’s clearly visible to, for example, an inspector).

*************************************************************************************************************

- After installation is complete, if the anchor has a projection, the portion of the projection that extends beyond the nut (on top of the fixture) may be trimmed per the following stipulations. The projection before trimming* and the length trimmed must be recorded on the inspection record. The projection after trimming shall not be less than one (1) thread beyond the top of the nut. All trimming must be saw-cut, and the trimmed area shall be painted if the anchor is outdoors, or in a wet or corrosive area/environment.

* NOTE 1:  The projection before trimming is the distance from the tip of the exposed end of the anchor to the concrete/masonry surface.

NOTE 2: If the projection has a length-indicator/head-marking, trimming will result in the loss of it.

- Concrete/masonry surface repairs: Repair concrete/masonry surfaces that haven’t been previously addressed herein, and have been damaged as a result of the work/project, using a non-shrink grout specified in Section 03 6000 Grouting. Repaired surfaces shall be touched up with a paint acceptable to LANL STR.

  - Locally spalled areas not more than 1/4” away from an anchor, and not more than 3/4” depth and 3/4” width, are considered undamaged and do not require repair.

  - Areas less than two (2) square inches, and not exceeding a nominal depth of 1/4”, are considered undamaged and do not require repair provided that they do not intersect/overlap with item 1 (above).

  - If the area exceeds 20 square inches, or if the nominal depth exceeds 3/4”, contact the LANL STR for evaluation of the damage and approval of the proposed repair

- Masonry joint repairs:  Repair mortar joint in-between masonry units that have been damaged as a result of the work/project by repointing in accordance with Section 04 2220 Reinforced Unit Masonry.  Prior to proceeding with repointing, present the LANL STR with the proposed procedure, and obtain permission from same to execute the procedure.

END OF MAIN BODY OF SECTION

Appended (one page each):  Figure A1

Figure A2

Table A1

Table A2

*********************************************************

Do not delete the following reference information:

*********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 05 0520 Rev. 4 dated October 24, 2018.

Figure A1

Field Bending of Grouted CONCRETE Anchors

Figure A2

drilling holes in concrete/MASONRY and modifying baseplates

| BOLT DIA.A | MIN.EDGE DIST.B |
| --- | --- |
| 1/4 " | 7/8” |
| 3/8 " | 7/8” |
| 1/2" | 1-1/8” |
| 5/8” | 1-1/4” |
| 3/4” | 1-1/2” |
| 7/8” | 1-3/4” |
| 1” | 1-3/4” |
| 1-1/4” | 2-1/4” |
| 1-3/8” | 2-1/2” |
| 2” | 3-1/2” |

Table a1

Concrete Anchor Required Inspection Attributes1

| Attribute | Insp when | Attribute Requirements and/or Information | Anchor Type |
| --- | --- | --- | --- |
|  |  | 05 0520 PART-3 Article | Other | Wedge and Screw | Heavy Duty Sleeve | Undercut | Adhesive | Grouted |
| 1 | Complete Anchor Identification2 | P |  | Drawings and ER | ( | ( | ( | ( | ( |
| 2 | Number of Anchors and Respective Locations Installed | P |  | Drawings | ( | ( | ( | ( | ( |
| 3 | Concrete Condition (sound)3 | P | GENERAL |  | ( | ( | ( | ( | ( |
| 4 | Concrete Type (normal vs. light-weight) | P |  | Drawings and ER | ( | ( | ( | ( | ( |
| 5 | Minimum Concrete Compressive Strength (f’c) | P | GENERAL | Drawings and ER | ( | ( | ( | ( | ( |
| 6 | Concrete Thickness | P | DRILLING OF HOLES | Drawings and ER | ( | ( | ( | ( | ( |
| 7 | Minimum Anchor Spacing4 | P |  | Drawings and ER | ( | ( | ( | ( | ( |
| 8 | Minimum Anchor Edge Distance | P |  | Drawings and ER | ( | ( | ( | ( | ( |
| 9 | Adhesive Expiration Date | P |  | ITPER and MPII |  |  |  | ( |  |
| 10 | Drill and/or Drill Bit Type, Size, Power, etc. | P | PREPARATION | MPII | ( | ( | (5 | ( |  |
| 11 | Rebar Cutting | D | PREPARATION |  | ( | ( | ( | ( | ( |
| 12 | Drilled Hole Cleaning | D |  | MPII | ( | ( | (6 | ( | ( |
| 13 | Drilled Hole Dimensions | D |  | MPII | ( | ( | ( | ( | (7 |
| 14 | Steel Deck Hole Dia. < Concrete Hole Dia. + 1/8” | D |  | ER | ( |  |  |  |  |
| 15 | Environment (temperature and moisture) | D | GENERAL | Drawings and ER |  |  |  | (8 | (9 |
| 16 | Embedded Portion of Anchor Clean and Straight10 | D | ADD’TL REQMTS FOR INSTAL OF GROUTED ANCHORS10 |  | ( | ( | ( | ( | ( |
| 17 | Anchor Embedment Depth11 | D | DRILLING OF HOLES | Drawings and ER | ( | ( | ( | ( | ( |
| 18 | Setting Duration (time, in seconds or minutes) | D |  | MPII |  |  | (12 | (13 |  |
| 19 | Proper Setting14 | D |  | MPII | ( | ( | ( | ( | ( |
| 20 | Anchor Sleeve Position Relative to Concrete/Fixture | D |  | MPII |  |  | ( |  |  |
| 21 | Washer Installation | D | INSTALLATION OF ANCHORS15 |  | (16 | ( | ( | (16 | ( |
| 22 | Prescribed Installation Torque | D |  | MPII | ( | ( | ( | ( | (17 |
| 23 | Anchor Condition (perp. and projection not bent) | A |  |  | ( | ( | ( | ( | ( |
| 24 | Full Nut-thread Engagement | A |  |  | (18 | (19 | ( | (18 | ( |

LEGEND:  ER = Evaluation Report, P = inspect prior to anchor installation (AI), D = inspect during AI, A = inspect after AI, MPII = Manufacturer’s Printed Installation Instructions, ( = Attribute applicable, Dia. = diameter, < = less than or equal to, perp. = perpendicular to nominal concrete surface within + 5°, N/A = not applicable.

NOTES:

1 The intent of this table is to capture the applicable attributes of the anchor indicated.  If more than one anchor is indicated, and any of the applicable attributes differ from one anchor to another, use as many tables as necessary to capture all unique attributes; and use lower-case letters with “Table A1” to distinguish one table from another (e.g., Table A1a, Table A1b, etc. and update wording after END OF MAIN BODY OF SECTION that states “one page each”).

2 The manner in which the anchor(s) to be installed is indicated on the drawings may be enough to properly identify it.  The last portion of the main body of an ER typically describes proper identification/designation.  For grouted anchors, indicate the grout strength, and the material type and size of the anchor element.

3 If any of the provisions requiring the integrity of the concrete to be intact in the PART-3 Article, Rework and Abandonment of Anchors, and Repair, apply then this Concrete Condition shall be inspected (for).

4 This attribute is straightforward when the work involves only newly-installed anchors in concrete without existing anchors/holes. However, if the work involves any of the PART-3 provisions pertaining to other circumstances (e.g., min. spacing between a new anchor/hole and an existing anchor/exploratory/unused hole, etc.), then any/all applicable “min.-spacing requirements” shall (also) be inspected (for).

5 This is actually two separate “sub-attributes” for undercut-anchor products that require two (2) sets of tools and/or devices (i.e., one for creation of a basic, uniform drill hole, and another for creating undercut).

6 This is actually two separate “sub-attributes” for those undercut-anchor products that require the creation of both a drill hole and an undercut.

7 Instead of MPII, refer to PART-3 Article, ADDITIONAL REQUIREMENTS FOR INSTALLATION OF GROUTED ANCHORS for requirements on dimensions of drilled holes.

8 This is actually two separate “sub-attributes” for adhesive anchors:  concrete temperature and the dryness/wetness of the concrete.

9 This is actually two separate “sub-attributes” for grouted anchors:  ambient temperature and the wetness of the concrete.  Instead of Drawings and ER, refer to the PART-3 Article, ADDITIONAL REQUIREMENTS FOR INSTALLATION OF GROUTED ANCHORS for how wet the concrete has to be, and to the grout manufacturer (per 03 6000 Grouting) for the permissible ambient temperature.

10 The PART-3 article referenced is applicable only if Anchor Type is a grouted anchor and the embedded portion of the anchor element will be field-bent (in accordance with Figure A1), in which case the word “Straight” in the Attribute isn’t applicable.

11 Compliance with MPII, as required by the PART-3 Article, DRILLING OF HOLES will ensure newly-installed anchors in newly-drilled concrete will achieve the min. embedment depth stipulated on project drawings and in the ER. There are two (2) exceptions to this: 1) For grouted anchors, as required by the PART-3 Article, ADD’TL REQMTS FOR INSTAL OF GROUTED ANCHORS, the drill-hole depth shall be as indicated on the drawings; and 2) If any of the other PART-3 articles that include embedment-depth requirements (i.e., PREPARATION, Installation of Anchors; and Rework and Abandonment of Anchors, and Repair) apply then min. embedment depth(s) stipulated therein shall be inspected (for).

12 A Setting Duration isn’t indicated in the MPII in many instances.  Exceptions include the MPII for the various types of Hilti HDA, which indicate max. durations ranging from 30 sec to 2 min. Other products that create the undercut without the use of a drill (like the HDA) should have similar Setting Durations.  And, while other products that aren’t “self-undercutting” will take longer to set, their Setting Durations shouldn’t exceed a few-to-several minutes.  The concern with an inordinately long Setting Duration is that something is wrong (e.g., one or more of the anchor, device, tool, etc. aren’t performing properly; an unexpected interference within the concrete has been encountered; etc.).

13 This is actually two or more separate “sub-attributes” for adhesive anchors, all of which are all related to the adhesive (e.g., working time, initial curing time, full curing time, roughening time, etc.).

14 Regardless of whether or not the term “Setting” appears in the MPII in question, the intent of this attribute is ensure the anchor is properly set (and/or driven, or installed, or positioned) into the concrete.  For grouted anchors, the anchor element shall be properly positioned in the drill hole prior to and during grouting.  Finally, if the MPII in question indicates that a mark on the anchor is visible if it’s properly set then the visibility of this mark is all that need be inspected (for).

15 For grouted anchors, also see the PART-3 Article, ADD’TL REQMTS FOR INSTAL OF GROUTED ANCHORS.

16 N/A to screw anchors, and to some adhesive-anchor anchor elements.

17 Instead of MPII, refer to PART-3 Article, ADD’TL REQMTS FOR INSTAL OF GROUTED ANCHORS for requirements on installation torque.

18 N/A to Screw Anchors, and to some adhesive-anchor anchor elements.

19 Applicable only to stud-type (vs. bolt-type) configurations.

TABLE a2

grouted-masonry anchor required inspection attributes1

| Attribute | Insp when | Attribute Requirements and/or Information | Anchor Type |
| --- | --- | --- | --- |
|  |  | 05 0520 PART-3 Article | Other | Wedge | Screw | Adhesive |
| 1 | Complete Anchor Identification2 | P |  | Drawings and ER | ( | ( | ( |
| 2 | Number of Anchors and Respective Locations Installed | P |  | Drawings | ( | ( | ( |
| 3 | Masonry Condition (sound) | P | GENERAL |  | ( | ( | ( |
| 4 | Masonry Unit Type (min. Grade N, Type __)3 | P | GENERAL | Drawings and ER | ( | ( | ( |
| 5 | Masonry Unit Size (__ x 8 x 16)3 | P | GENERAL | Drawings and ER | ( | ( | ( |
| 6 | Masonry Compressive Strength (f’m > ____ psi)3 | P | GENERAL | Drawings and ER | ( | ( | ( |
| 7 | Masonry Mortar Type (min. __)3 | P | GENERAL | Drawings and ER | ( | ( | ( |
| 8 | Masonry Grout Compressive Strength (> ____ psi)3 | P | GENERAL | Drawings and ER | ( | ( | ( |
| 9 | Minimum Anchor Spacing | P |  | Drawings and ER | ( | ( | ( |
| 10 | Minimum Anchor Edge (and End) Distance(s) | P |  | Drawings and ER | ( | ( | ( |
| 11 | Adhesive Expiration Date | P |  | ITPER and MPII |  |  | ( |
| 12 | Drill and/or Drill Bit Type, Size, Power, etc. | P | PREPARATION | MPII | ( | ( | ( |
| 13 | Rebar Cutting | D | PREPARATION |  | ( | ( | ( |
| 14 | Drilled Hole Cleaning | D |  | MPII | (4 | ( | ( |
| 15 | Drilled Hole Dimensions | D |  | MPII | ( | ( | ( |
| 16 | Environment (temperature and moisture)5 | D | GENERAL | Drawings and ER |  |  | ( |
| 17 | Embedded Portion of Anchor Clean and Straight | D |  |  | ( | ( | ( |
| 18 | Anchor Embedment Depth6 | D | DRILLING OF HOLES | Drawings and ER | ( | ( | ( |
| 19 | Adhesive Time (seconds or minutes)7 | D |  | MPII |  |  | ( |
| 20 | Proper Insertion8 | D |  | MPII | ( | ( | ( |
| 21 | Washer Installation | D | INSTALLATION OF ANCHORS |  | ( |  | (9 |
| 22 | Prescribed Installation Torque | D |  | MPII | ( | ( | ( |
| 23 | Anchor Condition (perp. and projection not bent) | A |  |  | ( | ( | ( |
| 24 | Full Nut-thread Engagement | A |  |  | ( |  | (10 |

LEGEND:  ER = Evaluation Report, P = inspect prior to anchor installation (AI), D = inspect during AI, A = inspect after AI, MPII = Manufacturer’s Printed Installation Instructions, ( = Attribute applicable, min. = minimum, Dia. = diameter, < = less than or equal to, perp. = perpendicular to nominal concrete surface within + 5°, N/A = not applicable

NOTES:

1 The intent of this table is to capture the applicable attributes of the anchor indicated.  If more than one anchor is indicated, and any of the applicable attributes differ from one anchor to another, use as many tables as necessary to capture all unique attributes; and use lower-case letters with “Table A1” to distinguish one table from another (e.g., Table A1a, Table A1b, etc. and update wording after END OF MAIN BODY OF SECTION that states “one page each”).

2 The manner in which the anchor(s) to be installed is indicated on the drawings may be enough to properly identify it.  The last portion of the main body of an ER typically describes proper identification/designation.  For grouted anchors, indicate the grout strength, and the material type and size of the anchor element.

3 Permissible Masonry Unit Type (i.e., I or II) and size (i.e., 8x8x16 or 6x8x16) vary with anchor product.  ALL products can only be used in fully-grouted masonry units that have an f’m value that varies with product, and that comply with ASTM C 90.  Mortar Type (i.e., N, S or M) varies with product.  Masonry grout min. compressive strength = f’m, but > 2000 psi.

4 The MPII for some Wedge Anchors don’t required drill-hole cleaning.

5 For some adhesive-anchor products, this is actually two separate “sub-attributes:” masonry temperature and the dryness/wetness of the masonry.

6 Compliance with MPII, as required by the PART-3 Article, DRILLING OF HOLES will ensure newly-installed anchors in newly-drilled masonry will achieve the min. embedment depth stipulated on project drawings and in the ER.

7 This is two or more separate attributes for adhesive anchors, all of which are all related to the adhesive (e.g., bolt-up time, working time, curing time, etc.).

8 The intent of this attribute is ensure the anchor is properly inserted (to include driven, if applicable, and positioned) into the concrete.

9  N/A to some adhesive-anchor anchor elements.

10 N/A to some adhesive-anchor anchor elements.