SECTION 07 5217

Styrene-butadiene-styrene (SBS) modified bituminous 
membrane roofing, Cold Applied

************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at https://engstandards.lanl.gov/specs.shtml

Rev. 2 Summary of Changes Updated wind requirements, references, and other minor changes.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The document must also be edited to delete requirements for processes, items, or designs that are not included in the project, add requirements not contained herein as well as delete specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
************************************************************************************************************

- GEnERAl

  - Summary

    - Section Includes

      - Styrene-butadiene-styrene (SBS) modified bituminous membrane roofing-cold applied.

      - Substrate boards.

      - Roof Insulation.

      - Vapor retarder.

      - Cover board.

    - [Section includes the installation of insulation strips in ribs of acoustical roof deck.  Insulation strips are furnished under Section 05 3000 Metal Decking.]

    - Related Sections

      - Section 01 8113.13 [LEED v4 and] Guiding Principles 2020: Requirements for water efficiency, energy efficiency, material composition, and indoor air quality requirements

      - [Section 02 4119 Selective Demolition]

      - [Section 02 8233 Removal and Disposal of Asbestos (future Section for re-roofing of older roofs)]

      - [Section 06 1000, Rough Carpentry for Wood, Nailers, Curbs and Blocking]

      - [Section 07 0150.19, Preparation for Re-roofing]

      - [Section 07 6200, Sheet Metal Flashing and Trim]

      - [Section 07 7100, Roof Specialties]

      - [Section 07 9200, Joint Sealants for Joint Sealants, Joint Fillers and Joint Preparation]

      - [Section 22 1413, Facility Storm Drainage Piping for Roof Drains]

  - references

    - Definitions

      - Roofing Terminology: Refer to ASTM D 1079 and the glossary of the National Roofing Contractors Association (NRCA) Roofing and Waterproofing Manual for definitions of roofing terms related to this section.

    - References

      - American Society of Civil Engineers (ASCE).

        - ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

      - ASTM International

        - ASTM C 208 - Standard Specification for Cellulosic Fiber Insulating Board.

        - ASTM C 552- Standard Specification for Cellular Glass Thermal Insulation.

        - ASTM C 578- Standard Specification for Rigid, Cellular Polystyrene Thermal Insulation.

        - ASTM C 728- Standard Specification for Perlite Thermal Insulation Board.

        - ASTM C 1177 – Standard Specification for Glass Mat Gypsum Substrate for Use as Sheathing.

        - ASTM C 1278 - Standard Specification for Fiber-Reinforced Gypsum Panel.

        - ASTM C 1289- Standard Specification for Faced Rigid Cellular Polyisocyanurate Thermal Insulation Board.

        - ASTM C 1396 - Standard Specification for Gypsum Board.

        - ASTM D 41- Standard Specification for Asphalt Primer Used in Roofing, Dampproofing, and Waterproofing.

        - ASTM D 226 - Standard Specification for Asphalt-Saturated Organic Felt Used in Roofing and Waterproofing.

        - ASTM D 448 - Standard Classification for Sizes of Aggregate for Road and Bridge Construction.

        - ASTM D 1079 - Standard Terminology Relating to Roofing and Waterproofing.

        - ASTM D 1970 - Standard Specification for Self-Adhering Polymer Modified Bituminous Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection.

        - ASTM D 2178 - Standard Specification for Asphalt Glass Felt Used in Roofing and Waterproofing.

        - ASTM D 3617 - Standard Practice for Sampling and Analysis of Built-Up Roof Systems During Application.

        - ASTM D 4263 - Standard Test Method for Indicating Moisture in Concrete by the Plastic Sheet Method.

        - ASTM D 4397 - Standard Specification for Polyethylene Sheeting for Construction, Industrial, and Agricultural Applications.

        - ASTM D 4586- Standard Specification for Asphalt Roof Cement, Asbestos-Free.

        - ASTM D 6163 – Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Glass Fiber Reinforcements.

        - ASTM D 6164 - Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Polyester Reinforcements.

        - ASTM E 84 – Standard Test Method for Surface Burning Characteristics of Building Materials.

        - ASTM E 1980 - Standard Practice for Calculating Solar Reflectance Index of Horizontal and Low-Sloped Opaque Surfaces.

      - Factory Mutual (FM Global) – Factory Mutual Standard 4470 – Approval Standard for Class 1 Roof Covers.

      - Membrane Immersion Test:  Modified Bitumen Membrane Asphaltic Impregnation Evaluation, as published in the “Proceedings of the Fourth International Symposium on Roofing Technology.”

      - National Roofing Contractors Association (NRCA) - Low Slope Roofing and Waterproofing Manual, Current Edition.

      - National Institute of Standards and Technology (NIST) PS 2 – Voluntary Product Standard PS 2, Performance Standard for Wood-Based Structural-Use Panels.

      - Underwriters Laboratories (UL) – Roofing Systems and Materials Guide (TGFU).

  - administrative requirements

    - Pre-installation Roofing Conference:  Conduct conference at [Project site] <Insert location>.

      - Subcontractor to organize and document meeting with LANL Architect of Record, LANL’s Subcontract Technical Representative, LANL’s insurer if applicable, testing and inspecting agency representative, roofing installer, roofing system manufacturer’s representative, deck installer, and installers whose work interfaces with or affects roofing, including installers of roof accessories and roof-mounted equipment.

      - Review methods and procedures related to roofing installation, including manufacturer’s written instructions.

      - Review and finalize construction schedule and verify availability of materials, installer’s personnel, equipment, and facilities needed to make progress and avoid delays.

      - Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

      - Review structural loading limitations of roof deck during and after roofing.

      - Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

      - Review governing regulations and requirements for insurance and certificates if applicable.

      - Review temporary protection requirements for roofing system during and after installation.

      - Review roof observation and repair procedures after roofing installation.

- ************************************************************************************************************

- Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

- ***********************************************************************************************************

  - action SUBMITTALS

    - [Material List: A complete listing of all products intended for use on the project and be coordinated with the shop drawings.  List shall include all products and accessories to be incorporated into the finished roof system. Major items in the materials list include:

      - Insulation

      - Cover boards

      - APP base and cap sheets

      - Adhesives

      - Flashing systems

      - Accessories (primers, cements, fabric, caulking)]

    - [Product Data:  Manufacturer’s data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Specifications and general recommendations from manufacturers of modified bitumen roofing system materials to include the types of roofing required.  Include any data requiring special application considerations by the manufacturer.

      - Submit Material Safety Data Sheets on all roofing materials to be used.]

    - [Shop Drawings: Provide plan section, elevation, and perspective drawings as necessary to depict all flashing and project conditions on the project, including but not limited to the following:

      - Roof system and base flashing configuration.

      - Penetration details.

      - Termination details.

      - Fastening patterns.

      - Tapered insulation design.]

    - [Selection Samples:  For each product specified, two samples representing manufacturer’s full range of available colors and types.]

    - [Verification Samples:  For each finish product specified, two samples representing actual product, color, and finish.]

    - [Manufacturer Certificates:  Signed by roofing manufacturer certifying that roofing system complies with requirements specified in “Performance Requirements” Article.

      - Submit evidence of complying with performance requirements.]

    - [Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for components of membrane roofing system.]

    - [Research/Evaluation Reports:  For components of membrane roofing system, from [the ICC-ES] <Insert applicable model code organization>.]

    - [Manufacturer’s Instructions:

      - Manufacturer’s published installation instructions and methods.]

    - [Qualification Data:  For qualified [Installer] [and] [manufacturer].]

- ************************************************************************************************************

Include only sustainable design submittals that are appropriate for the project’s sustainable design goals, if any.

- ************************************************************************************************************

  - sustainable design submittals

    - Sustainable Design (LD) Submittals:  Comply with requirements specified in [individual specification sections]  Section 01 8113.13 - [LEED v4 and] Guiding Principles 2020: Requirements for water efficiency, energy efficiency, material composition, and indoor air quality requirements

    - Product Test Reports for roof materials, indicating that roof materials comply with Solar Reflectance Index requirement.

    - Product Data for adhesives and sealants, including printed statement of VOC content.

    - Submit manufacturer’s documentation of Energy Star labeled roofing materials.

  - close-out submittals

    - Maintenance Data:  For roofing system to include in maintenance manuals.

    - Warranties:

      - Submit copy of the membrane manufacturer’s warranty covering materials.

      - Submit copy of the Roofing Subcontractor’s warranty covering workmanship.

  - quality assurance

    - Apply roofing system by an approved Subcontractor authorized prior to bid by the roof membrane manufacturer.  Prior to bid, the Roofing Subcontractor must have completed a minimum of 500 roofing squares of SBS membrane in the Southwest.  To qualify for this requirement, the completed membrane must have met all conditions to obtain material and labor warranty and must be performing successfully.

    - Membrane manufacturer to provide a list of projects, completed in the Southwest, where the specified membrane has been in place and performing successfully for a period of not less than five (5) years. A minimum of 500 roofing squares must have been installed to meet this requirement.

    - Do not deviate from this specification or the approved shop drawings without prior written approval by the manufacturer and the LANL Subcontract Technical Representative (STR).

    - Code Requirements:  Meet the requirements of the following recognized code approval or testing agencies.  These requirements are minimum standards and no roofing work may commence without written documentation of the system’s compliance.

      - Underwriters Laboratories (UL) Class A membrane.

      - Factory Mutual (FM) 1-90 uplift rating, as indicated on Contract Documents per FM Approval Standard No. 4470.

    - Energy Star Roof Compliance:  Proposed roofing system will be Energy Star Roof-compliant and roofing materials will be Energy Star labeled.

    - For new installations, ponding will not occur in accordance with NRCA Roofing and Waterproofing Manual good roof design practice, which dictates that there will be no ponding water present 48-hours after rainfall.

    - There will be no more than 20 patches per 10,000 SF on new construction.

    - The approved Manufacturer shall make site visits to the job during construction and after construction by a Certified Technical Representative of the Company. Visits to include:

      - Pre-construction meeting

      - Project mid-point inspection

      - Final Inspection

      - [18-month warranty inspection]

  - delivery, storage, and handling

    - Store products in manufacturer’s unopened packaging until ready for installation.

    - Deliver roofing materials to the site in original containers, with factory seals intact.

    - Store pail goods in their original undamaged containers in a clean, dry location within their specified temperature range.

    - Store roll goods on end on pallets in a clean, dry, protected area.  Do not double stack modified bitumen products.

    - Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Store in a dry location.  Comply with insulation manufacturer’s written instructions for handling, storing, and protecting during installation.

    - Store and dispose of hazardous materials, and materials contaminated by hazardous materials, in accordance with requirements of local authorities having jurisdiction.

  - Project conditions

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer’s absolute limits.

    - Weather Limitations:  Proceed with installation only when existing and forecasted weather conditions permit roofing system to be installed according to manufacturer’s written instructions and warranty requirements.

  - Warranty

    - Special Warranty:  Manufacturer’s standard form, without monetary limitation, in which manufacturer agrees to repair or replace components of membrane roofing system that fail in materials or workmanship within specified warranty period.

      - Special warranty includes membrane roofing, base flashings, [roof insulation], [fasteners], [cover boards], [substrate board] [roofing accessories] [roof pavers] and other components of membrane roofing system.

      - Warranty Period: [10] [15] <Insert number> years from date of Substantial completion.

    - Special Project Warranty:  Submit roofing Installer’s warranty, signed by Installer, covering the Work of this Section, including all components of membrane roofing system such as membrane roofing, base flashing, roof insulation, fasteners, cover boards, substrate boards, vapor retarder, and walkway products, for the following warranty period:

      - Warranty Period: [Two] <Insert number> years from date of Substantial Completion.

- PRODUCTS

  - MANUFACTURERS

    - Manufacturers:  Subject to compliance with requirements, provide products by one of the following.  No substitutions for these manufacturers permitted.

- ************************************************************************************************************ Manufacturer’s specification number is based on application over non-nailable roof insulation. Modify specification number as required for steel, concrete, primer, lightweight concrete, nailable or existing built-up roof substrates.
************************************************************************************************************

      - Mineral-surfaced, modified-bitumen capsheet and modified-bitumen base sheet installed in cold-applied adhesive, UL Class A, Roofing Manufacturer’s 20-year type system.

        - Firestone Building Products, Specification No. [QS 539 SBS – Cool Concrete] [QS 540 SBS – Cool Insulated] [QS 543 SBS – Re-Cover]

        - Johns Manville Corporation Specification No. 2FID-CA

        - Siplast/Icopal Specification No. 2030 IA

  - performance / design criteria

    - General Performance: Installed membrane roofing and base flashings shall withstand specified uplift pressures, thermally induced movement, and exposure to weather without failure due to defective manufacture, fabrication, installation, or other defects in construction. Membrane roofing and base flashings shall remain watertight.

    - Material Compatibility: Provide roofing materials that are compatible with one another under conditions of service and application required, as demonstrated by membrane roofing manufacturer based on testing and field experience.

    - Perform work in accordance with all federal, state, and local codes.

    - Exterior Fire Test Exposure: Provide a roofing system achieving a UL Class rating for roof slopes indicated on the Contract Drawings.

      - UL Class A rating.

    - Windstorm Classification: Provide a roofing system that will achieve the required uplift resistance as calculated in accordance with the LANL-adopted edition of ASCE and ESM Chapter 5 Section II.

    - FM Approvals Listing: Provide membrane roofing, base flashings, and component materials that comply with requirements in current FM Approval Guide. Identify materials with FM Approvals markings.

      - Fire/Windstorm Classification: Class 1A-90

      - Hail Resistance Rating: [MH] [SH].

    - Foam Plastic Insulation: Maximum 75/450 flame/spread smoke developed index when tested in accordance with ASTM E 84.

    - Other Insulation: Maximum 25/450 flame spread/smoke developed index when tested in accordance with ASTM E 84.

    - Energy Performance: Provide roofing system with initial Solar Reflectance Index not less than 78 when calculated according to ASTM E 1980 based on testing identical products by a qualified testing agency.

    - Energy Performance: Provide roofing system that is listed on DOE’s ENERGY STAR “Roof Products Qualified Product List” for low-slope roof products.

    - Energy Performance: Provide roofing system with initial Solar Reflectance not less than 0.70 and Thermal Emittance not less than 0.75 when tested according to Cool Roof Rating Council’s CRRC-1.

    - Manufacturer’s Requirements

      - Except as modified and supplemented herein, follow the Roofing Manufacturer’s and other materials manufacturer’s catalogs, general and special requirements, and specific application recommendations.

      - With respect to methods of installation, industry practices apply only when these specifications do not address the matter.

    - Slopes and Underlying Materials

      - Use materials which are proper for the slopes and for the underlying material to which the other materials are attached.

    - Roof Membrane: Styrene-butadiene-styrene (SBS) modified bituminous capsheet, ply sheet, and base sheet in cold-applied adhesive with heat welded seams, UL Class A, Roofing Manufacturer’s 20-year type system.

    - Bituminous Flashings

      - Composition base flashings consisting of

        - Ply of modified-bitumen base sheet,

        - Ply of mineral-surfaced modified-bitumen flashing sheet; and

        - Modified-bitumen flashing cement or cold-applied adhesive

      - Roof drain flashings consisting of:

        - Modified-bitumen membrane base sheet and ply sheet in adhesive.

        - Primed metal sump flashing in modified-bitumen flashing cement.

      - One ply of modified-bitumen ply sheet and modified-bitumen flashing cement.

  - materials

    - Roof Insulation

- ************************************************************************************************************

- Select roof insulation from the following as required for compatibility with SBS cold-applied roofing system and applicable roof design requirements.

- ************************************************************************************************************

      - General:  Preformed roof insulation boards manufactured [or approved] by roofing manufacturer, selected from manufacturer’s standard sizes and suitable for application, of thicknesses indicated [and that produces FM Approvals-approved roof insulation].

      - Extruded-Polystyrene Board Insulation:  ASTM C 578, [Type IV, 1.6-lb/cu.ft.] [Type X, 1.3-lb/cu.ft.] minimum density, square edged.

      - Molded-Polystyrene Board Insulation:  ASTM C 578 [Type II, 1.35-lb/cu.ft.] [Type VIII, 1.15-lb/cu.ft.] [Type IX, 1.8-lb/cu.ft.] minimum density.

      - Composite Molded-Polystyrene Board Insulation:  ASTM C 578, [Type II, 1.35-lb/cu.ft.] [Type VIII, 1.15-lb/cu.ft.] [Type IX, 1.8-lb/cu.ft.] minimum density, with factory-applied facings as follows:

        - Facer:  ASTM C 208, Type II, Grade 2, cellulosic-fiber insulation board, asphalt coated, ½ inch thick.

        - Facer:  NIST PS 2, Exposure 1, OSB, 7/16 inch thick.

      - Polyisocyanurate Board Roof Insulation: Rigid, cellular thermal insulation with polyisocyanurate closed-cell foam core with a rated flame spread of 25 or less per ASTM E 84 and manufacturer's standard fiberglass reinforced facing laminated to both sides; Insulation shall meet the new LTTR requirements of ASTM C 1289 Standard, Type II Class 1, Grade 2 (20 psi).

        - Minimum Thickness: (2) layers of 2.5 inches, R-30 (unless noted otherwise in drawings).

        - Maximum board size 4' x 4'.

      - Composite Polyisocyanurate Board Insulation:  ASTM C 1289, with factory-applied facing board, as indicated below by type, on one major surface and felt or glass-fiber mat facer on the other surface.

        - Type IV, cellulosic-fiber-insulating-board facer, Grade 2, ½ inch thick.

        - Type V, OSB facer, 7/16 inch thick.

        - Type VII, glass-mat-faced gypsum board facer, 1/4 inch thick.

      - Perlite Board Insulation:  ASTM C 728, rigid, mineral-aggregate thermal insulation board composed of expanded perlite, cellulosic fibers, binders, and waterproofing agents with top surface seal coated.

      - Cellulosic-Fiber Board Insulation:  ASTM C 208, Type II, Grade 2, fibrous-felted, rigid insulation boards of wood fiber or other cellulosic-fiber and water-resistant binders, asphalt impregnated, chemically treated for deterioration.

      - Cellular-Glass Board Insulation:  ASTM C 552, Type IV, rigid, cellular-glass thermal board insulation faced with manufacturer’s standard kraft-paper sheets.

      - Tapered Insulation:  Provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope> unless otherwise indicated.

        - Maximum board size: 4 ft x 4 ft.

        - Minimum thickness: 1/2 inch.

      - Provide preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for positive drainage.  Fabricate to 1/2-inch slope minimum.

    - Substrate Boards

- ********************************************************************************************

- Select substrate boards from the following as required for compatibility with SBS cold-applied roofing system and applicable roof design requirements.

- ********************************************************************************************

      - Substrate Board:  ASTM C 1396 Type X gypsum board, 5/8 inch thick.

      - Substrate Board:  ASTM C 1177, glass-mat, water-resistant gypsum substrate, [1/4 inch] [1/2 inch] [Type X, 5/8 inch] thick, [factory primed].

        - Products:  Subject to compliance with requirements, provide the following:

          - Georgia-Pacific Corporation: [Dens Deck] [Dens Deck Prime] [Dens Deck DuraGuard].

          - USG Corporation: Securock Glass-Mat Roof Board

          - <Insert manufacturer’s name; product name or designation>.

      - Substrate Board: ASTM C 1278, cellulosic-fiber-reinforced, water-resistant gypsum substrate, [1/4 inch] [3/8 inch] [1/2 inch] [5/8 inch] thick.

        - Products:  Subject to compliance with requirements, provide the following:

          - USG Corporation; Securock.

          - USG Corporation; Securock Gypsum Fiber Roof Board.

          - <Insert manufacturer’s name; product name or designation>.

      - Substrate Board:  ASTM C 728, perlite board, [1/2 inch] [3/4 inch] [1 inch] thick, seal coated.

      - Fasteners: Factory-coated steel fasteners and metal or plastic plates complying with corrosion-resistance provisions in FM Approvals 4470, designated for fastening substrate board to roof deck.

      - Insulation Adhesives

        - Insulation adhesives shall be used to install the specified polyisocyanurate insulation to the specified vapor retarder and the Cover Board substrate boards to the polyisocyanurate insulation.

        - OlyBond 500 Polyurethane Foam Adhesive by OMG Roofing Products. Ribbon-Applied Adhesive and specified NDL year adhesion warranty must be included with roofing manufacturer’s warranty.

    - Vapor Retarder

- ******************************************************************************************

- Select vapor retarder from the following as required for compatibility with SBS cold-applied roofing system and applicable roof design requirements.

- *******************************************************************************************

      - Polyethylene Film:  ASTM D 4397, 6 mils thick, minimum, with maximum permeance rating of 0.13 perm.

        - Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

        - Adhesive:  Manufacturer’s standard lap adhesive, FM Approvals approved for vapor-retarder application.

      - Laminated Sheet:  Kraft paper, two layers, laminated with asphalt and edge reinforced with woven fiberglass yarn, with maximum permeance rating of 0.50 perm [and with manufacturer’s standard adhesive].

      - Self-Adhering Sheet Vapor Retarder:  ASTM D 1970, minimum of 40-mil- thick, polyethylene film laminated to layer of rubberized asphalt adhesive; maximum permeance rating of 0.1 perm; cold applied, with slip-resisting surface and release paper backing.  Provide primer when recommended by vapor-retarder manufacturer.

      - Self-Adhering Sheet Vapor Retarder: 30 to 40-mil-thick, polyethylene film laminated to layer of butyl rubber adhesive; maximum permeance rating of 0.1 perm; cold applied, with slip-resisting surface and release paper backing.  Provide primer when recommended by vapor-retarder manufacturer.

      - Smooth surfaced SBS membrane base.

    - Cover Board

- ********************************************************************************************

- Select cover board from the following as required for compatibility with SBS cold-applied roofing system and applicable roof design requirements.

- ********************************************************************************************

      - Cover Board: ASTM C 208, Type II, Grade 2, cellulosic-fiber insulation board, [1/4] [1/2] inch thick.

      - Cover Board: NIST PS 2, Exposure 1, OSB, 7/16 inch thick.

      - Cover Board: ASTM C 1177, glass-mat, water-resistant gypsum substrate, [1/4 inch] [1/2 inch] [5/8 inch] thick [factory primed].

        - Products: Subject to compliance with requirements, provide the following:

          - Georgia-Pacific Corporation; [Dens Deck] [Dens Deck Prime] [Dens Deck DuraGuard].

          - USG Corporation: Securock Glass-Mat Roof Board

          - <Insert manufacturer’s name; product name or designation>.

      - Cover Board:  ASTM C 1278, cellulosic-fiber-reinforced, water-resistant gypsum substrate, [1/4 inch] [3/8 inch] [1/2 inch] [5/8 inch] thick.

        - Products: Subject to compliance with requirements, provide the following:

          - USG Corporation; Securock Gypsum Fiber Roof Board

          - <Insert manufacturer’s name; product name or designation>.

    - Insulation Accessories

      - General:  Furnish roof insulation accessories recommended by insulation manufacturer for intended use and compatibility with membrane roofing.

      - Fasteners:  Factory-coated steel fasteners and metal or plastic plates complying with corrosion-resistance provisions in FM Approvals 4470, designed for fastening roof insulation [and cover boards] to substrate, and acceptable to roofing system manufacturer.

      - Modified Asphaltic Insulation Adhesive:  Insulation manufacturer’s recommended modified asphaltic, asbestos-free, cold-applied adhesive formulated to attach roof insulation to substrate or to another insulation layer.

      - Bead-Applied Insulation Adhesive:  Insulation manufacturer’s recommended bead-applied, low-rise, one-component or multi-component urethane adhesive formulated to attach roof insulation to substrate or to another insulation layer.

      - Full-Spread Applied Insulation Adhesive:  Insulation manufacturer’s recommended spray-applied, low-rise, two-component urethane adhesive formulated to attach roof insulation to substrate or to another insulation layer.

      - Insulation Cant Strips:  ASTM C 728, perlite insulation board.

      - Insulation Cant Strips:  ASTM C 208, Type II, Grade 1, cellulosic-fiber insulation board.

      - Wood Nailer Strips:  Comply with requirements in Section 06 6100, Rough Carpentry.

      - Tapered Edge Strips:  ASTM C 728, perlite insulation board.

      - Tapered Edge Strips:  ASTM C 208, Type II, Grade 1, cellulosic-fiber insulation board.

      - Substrate Joint Tape:  6- or 8- inch wide, coated, glass-fiber joint tape.

    - SBS-Modified Asphalt-Sheet Materials

      - Asphalt-saturated Organic Felt: ASTM D 226, Type I, (No. 15), non-perforated; 36 inches wide.

      - Asphalt Glass Felt: ASTM D 2178, Type IV or VI, as required by Roofing Manufacturer for a 20-year type system; 36 inches.

      - Roofing Membrane Sheet: ASTM D 6163, Grade S, Type I or II, SBS-modified asphalt sheet (reinforced with glass fibers) smooth surfaced; suitable for application method specified.

        - Firestone Building Products, SBS Base

        - Johns Manville Corporation, DynaBase

        - Siplast Paradiene 20.

      - Granule-Surface Roofing Membrane Cap Sheet: ASTM D 6164, Grade G, Type I or II, SBS-modified asphalt sheet (reinforced with polyester fabric) or ASTM D 6163, Grade G, Type I or II, SBS-modified asphalt sheet (reinforced with glass fibers) granular surfaced; suitable for application method specified, and as follows:

        - Firestone Building Products, SBS FR CR (cool roof); ASTM D 6164, Type I, Grade G, fire rated.

        - Johns Manville Corporation, DynaGlass 30 FR CR (cool roof); ASTM D 6163, Type I, Grade G, fire rated.

        - Siplast/Icopal, Paradiene 30 FR CR (cool roof); ASTM D 6163, Type I, Grade G, fire rated

        - Granule Color: [White] [Gray] [Tan] <Insert color>.

    - Base Flashing Sheet Materials

      - Backer Sheet: ASTM D 6164, Grade S, Type I or II, SBS-modified asphalt sheet (reinforced with polyester fabric) or ASTM D 6163, Grade S, Type I or II, SBS-modified asphalt sheet (reinforced with glass fibers) smooth surfaced; suitable for application method specified.

      - Granule-Surfaced Flashing Sheet: ASTM D 6164, Grade G, Type I or II, SBS-modified asphalt sheet (reinforced with polyester fabric) or ASTM D 6163, Grade G, Type I or II, SBS-modified asphalt sheet (reinforced with glass fibers) granular surfaced; suitable for application method specified, and as follows:

        - Firestone Building Products, SBS Flashing; ASTM D 6164, Type I, Grade G.

        - Johns Manville Corporation, DynaFlex; ASTM D 6164, Grade G, Type II.

        - Siplast Paradiene 40 FR; ASTM D 6163, Grade G, Type II.

        - Granule Color: [White] [Gray] [Tan] <Insert color>.

    - Auxillary Roofing Membrane Materials

      - General: Auxiliary materials recommended by roofing manufacturer for intended use and compatible with roofing membrane.

        - Liquid-type auxiliary materials shall comply with VOC limits of authorities having jurisdiction.

        - Adhesives and sealants that are not on the exterior side of weather barrier shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

          - Plastic Foam Adhesives: 50g/L.

          - Multipurpose construction Adhesives: 70 g/L.

          - Fiberglass Adhesives: 80 g/L.

          - Contact Adhesives: 80 g/L.

          - Other Adhesives: 250 g/L.

          - Nonmembrane Roof Sealants: 300 g/L.

          - Sealant Primers for Nonporous Substrates: 250 g/L.

          - Sealant Primers for Porous Substrates: 775 g/L.

      - Asphalt Primer: ASTM D 41.

      - Cold-Applied Adhesive: Roofing manufacturer’s standard asphalt-based, one- or two-part, asbestos-free, cold-applied adhesive specially formulated for compatibility and use with [roofing membrane] [and] [base flashings].

        - Firestone Building Products, Multi-purpose MB Cold Adhesive

        - Johns Manville Corporation, MBR Bonding Adhesive.

        - Siplast, PA-311 M Adhesive.

      - Asphalt Roofing Cement: ASTM D 4586, Type I, Class 1, asbestos free, of consistency required by roofing manufacturer for application.

      - Mastic Sealant: Polyisobutylene, plain or modified bitumen, non-hardening, non-migrating, non-skinning, and nondrying.

      - Modified-bitumen Flashing Cement: trowel-grade, one-component, styrene-butadiene-styrene, modified-asphalt, flashing cement; Roofing Manufacturer’s standard.

      - Water Block: One part butyl based high viscosity sealant suitable for sealing between flashing membrane and substrate surface behind exposed termination bars and for sealing between roofing membrane and drain flange.

      - 2-Part Pourable Sealant: 100 percent solids epoxy based two-part sealant suitable for filling sealant pans at irregularly shaped penetrations. Epoxy is part A. Polylamide is part B.

      - Lip Termination Bar: Extruded aluminum termination bar with angled lip caulk receiver and lower leg bulb stiffener. Pre-punched slotted holes a 6 inch or 8-inch centers, 3/4 inch by 10 inch with 0.090 inch cross section.

      - Mineral Granules: ASTM D 448, size, color and die lot to match membrane and flashing sheets; manufactured or supplied by the roofing manufacturer.

      - Separator Sheet: Polyethylene sheet, 4 mils thick, minimum.

      - Walkway Pads: Mineral-granule-surfaced, reinforced modified asphalt composition, slip-resisting pads manufactured as a traffic pad for foot traffic provided by roofing system manufacturer, with a pad size of 32-inch x 32-inch.

      - Miscellaneous Accessories: Provide those recommended by roofing system manufacturer.

- EXECUTION

  - EXAMINATION

    - Examine substrates, areas, and conditions, with Installer present, for compliance with the following requirements and other conditions affecting performance of insulation and roofing systems:

      - Verify that roof openings and penetrations are in place and curbs are set and braced and that roof drain bodies are securely clamped in place.

        - Raise all roof curbs, and roof penetrations to provide a minimum eight (8) inch flashing at all locations.

        - Raise plumbing vents to provide a minimum twelve (12) inch flashing height at all locations.

      - Verify that wood cants, blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thickness of insulation.

      - Verify that surface plane flatness and fastening of steel roof deck complies with requirements in Section 05 3000 Metal Decking.

      - Verify that minimum concrete drying period recommended by roofing system manufacturer has passed.

      - Verify that concrete substrate is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263.

      - Verify that concrete-curing compounds that will impair adhesion of roofing components to roof deck have been removed.

      - Verify that deck is securely fastened with no projecting fasteners and with no adjacent units more than 1/16 inch out of plane relative to adjoining deck.

    - Report unsatisfactory conditions to the LANL STR.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - PREPARATION

    - Clean substrate of dust, debris, moisture, and other substances detrimental to insulation and roofing installation according to roofing system manufacturer’s written instructions.  Remove sharp projections.

    - Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.  Remove roof-drain plugs when no work is taking place or when rain is forecast.

    - Prime surface of concrete deck with asphalt primer as recommended by roofing manufacturer and allow primer to dry.

    - Install insulation strips in ribs of acoustical roof decks according to acoustical roof deck manufacturer’s written instructions.

  - substrate board INSTALLATION

    - Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows. Tightly butt substrate boards together.

      - Fasten substrate board to top flanges of steel deck according to recommendations in FM Approval Guide for specified Windstorm Resistance Classification.

      - Fasten substrate board to top flanges of steel deck to resist uplift pressure at corners, perimeter, and field of roof according to membrane roofing system manufacturers’ written instructions.

      - Structural Concrete Deck

        - Minimum deck thickness for structural concrete is 4 inches (102 mm).

        - Only poured in place concrete decks that provide bottom side drying are acceptable.

        - The roof deck shall be properly cured prior to application of the roofing system. Curing agents shall be checked for compatibility with roofing materials. Prior to the installation of the roof assemblies, evaluation of the surface moisture and deck's dryness per ASTM D 4263 or hot bitumen test procedures shall be conducted.

        - The deck shall be smooth, level and cannot be wet or frozen.

        - With retrofit roof applications, it is required that the deck be inspected for defects. Defects are to be corrected per the deck manufacturer's recommendations prior to the roofing application.

        - Treat cracks greater than 1/8 inch (3 mm) in width in accordance with the deck manufacturer's recommendations.

  - vapor-retarder Installation

- **************************************************************************************************

- Select vapor-retarder installation method as required for selected vapor-retarder.

- **************************************************************************************************

    - Polyethylene Film:  Loosely lay polyethylene-film vapor retarder in a single layer over area to receive vapor retarder, side ad end lapping each sheet a minimum of 2 inches and 6 inches, respectively.

      - Continuously seal side and end laps with [tape] [adhesive].

    - Laminate sheet:  Install laminate-sheet vapor retarder in a single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches and 6 inches, respectively.  Bond vapor retarder to substrate as follows:

      - Apply adhesive at rate recommended by vapor-retarder manufacturer.  Seal laps with adhesive.

    - Self-Adhering Sheet Vapor Retarder:  Prime substrate if required by manufacturer.  Install self-adhering sheet vapor retarder over area to receive vapor retarder, side and end lapping each sheet a minimum of 3-1/2 inches and 6 inches, respectively.  Seal laps by rolling.

    - Material and Application

      - Install 1 layer of Smooth Surfaced SBS Membrane Base Sheet over the prepared substrate overlapping a minimum of three inches at the side laps and 12 inches at the end laps. Install membrane layer in adhesive and hot air weld side and end laps. The membrane shall be fully bonded to the substrate, without wrinkles, creases, or fish mouths. Broom in each layer assuring complete adhesion.

  - Insulation installation

- **************************************************************************************************

- Select insulation installation method as required for selected insulation.

- **************************************************************************************************

    - Comply with roofing system manufacturer’s written instructions for installing roof insulation.

    - Install one lapped base-sheet course and mechanically fasten to substrate according to roofing system manufacturer’s written instructions.

    - Nailer Strips:  Mechanically fasten 4-inch nominal (89-mm actual) width wood nailer strips of same thickness as insulation perpendicular to sloped roof deck at the following spacing:

      - [16 feet] <Insert spacing> apart for roof slopes steeper than 1 inch per 12 inches (1:12) but less than 3 inches per 12 inches (3:12).

      - [48 inches] <Insert spacing> apart for roof slopes steeper than 3 inches per 12 inches (3:12).

    - Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes more than 45 degrees.

    - Install tapered insulation under area of roofing to conform to slopes indicated.

    - Install insulation with long joints of insulation in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding ¼ inch with insulation.

      - Cut and fit insulation within 1/4 inch of nailers, projections, and penetrations.

    - Install insulation under area of roofing to achieve required thickness.  Where overall insulation thickness is 2.7 inches or more, install two or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches in each direction.

      - Where installing composite and non-composite insulation in two or more layers, install non-composite board insulation for bottom layer and intermediate layers, if applicable, and install composite board insulation for top layer.

    - Trim surface of insulation where necessary at roof drains so completed surface is flush and does not restrict flow of water.

    - Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

    - Adhered Insulation:  Install each layer of insulation and adhere to substrate as follows:

      - Prime surface of concrete deck with asphalt primer at rate of 3/4 gal. /100 sq.ft. and allow primer to dry.

      - Set each layer of insulation in ribbons of bead-applied insulation adhesive, firmly pressing and maintaining insulation in place.

      - Set each layer of insulation in a uniform coverage of full-spread insulation adhesive, firmly pressing and maintaining insulation in place.

    - Mechanically Fastened Insulation:  Install each layer of insulation and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

      - Mechanically fasten insulation to substrate with fasteners/plates and pattern complying with FM 1-90 requirements and approved by membrane manufacturer.

      - Fasten insulation to resist uplift pressure of corners, perimeter, and field of roof.

    - Mechanically Fastened and Adhered Insulation:  Install first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

      - Mechanically fasten insulation to substrate with fasteners/plates and pattern complying with FM 1-90 requirements and approved by membrane manufacturer.

      - Fasten first layer of insulation to resist uplift pressure at corners, perimeter, and field of roof.

      - Set each subsequent layer of insulation in ribbons of bead-applied insulation adhesive, firmly pressing and maintaining insulation in place.

- **** [or] ****

      - Set each subsequent layer of insulation in a uniform coverage of full-spread insulation adhesive, firmly pressing and maintaining insulation in place.

  - Cover board installation

    - Install cover boards over insulation with long joints in continuous straight lines with end joints staggered between rows.  Offset joints a minimum of 6 inches in each direction from joints of insulation below.  Loosely butt cover boards together [and fasten to roof deck].  Tape joints if required by roofing system manufacturer.

      - Fasten cover boards according to requirements in FM Approvals’ “RoofNav” for specified Windstorm Resistance Classification.

      - Fasten cover boards to resist uplift pressure at corners, perimeter, and field of roof.

      - Adhere the cover board per manufacturer’s written instructions to comply with and ESM Chapter 5 Section II and applicable Building Codes, and per Manufacturer’s specified NDL wind and warranty requirements.

  - roofing membrane installation, general

    - Install roofing membrane system according to roofing system manufacturer’s written instructions and applicable recommendation in NRCA’s Quality Control Guidelines for the Application of Polymer Modified Bitumen Roofing and as follows:

      - Deck type: [N (nailable)] [I (insulated)] [C (concrete or non-nailable)].

      - Adhering Method: [L (cold-applied adhesive)]

      - Number of Glass-Fiber Base Sheets: One

      - Number of Glass-Fiber Base-Ply Sheets: One.

      - Number of SBS-Modified Asphalt Cap Sheets: One.

      - Surfacing Type: [M (mineral-granule-surfaced cap sheet)] .

    - Start installation of roofing membrane in presence of roofing system manufacturer’s technical personnel.

    - Where roof slope exceeds [1/2 inch per 12 inches (1:24)] [3/4 inch per 12 inches (1:18)] <Insert slope>, install roofing membrane sheets parallel with slope.

      - Backnail roofing membrane sheets to [nailer strips] [substrate] according to roofing system manufacturer’s written instructions.

    - Cooperate with testing agencies engaged or required to perform services for installing roofing system.

    - Coordinate installation of roofing system so insulation and other components of the roofing membrane system not permanently exposed are not subjected to precipitation or left uncovered at the end of the workday or when rain is forecast.

      - At end of each day’s work, provide tie-offs to cover exposed roofing membrane sheets and insulation with a course of coated felt set in roofing cement or hot roofing asphalt, with joints and edges sealed.

      - Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

      - Remove and discard temporary seals before beginning work on adjoining roofing.

    - Substrate-Joint Penetrations:  Prevent roofing asphalt and adhesives from penetrating substrate joints, entering building, or damaging roofing system components or adjacent building construction.

  - base sheet installation

    - Install lapped base sheet course, extending sheet over and terminating beyond cants. Attach base sheet as follows:

      - Unroll and relax all membrane sheets prior to installation. Rolls shall be relaxed for a minimum of thirty minutes prior to application.

      - Adhere to substrate in a uniform coating of cold-applied adhesive.

  - BAse-ply sheet installation

    - Install glass-fiber base-ply sheets according to roofing system manufacturer’s written instructions starting at low point of roofing system.  Align glass-fiber base-ply sheets without stretching. Extend glass-fiber base-ply sheets over and terminate beyond cants.

      - Shingle side laps of glass-fiber base-ply sheets uniformly to ensure that required number of glass-fiber base-ply sheets cover substrate at all points. Shingle in direction to shed water.

      - Over the prepared substrate apply the membrane layers overlapping a minimum of 3 inches at the side laps and 12 inches at the end laps.

      - Install each membrane layer adhesive applied with hot air welded side and end laps.

      - The membrane layers shall be fully bonded to their substrates, without wrinkles, creases, or fish mouths. Broom in each layer assuring complete adhesion.

  - SBS-modified bituminous membrane installation

    - Install modified bituminous roofing membrane [sheet and] cap sheet according to roofing manufacturer’s written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

      - Install membrane cap sheet over two-ply base system with cold adhesive and hot air welded side and end laps.

      - Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

    - Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

      - Repair tears and voids in laps and lapped seams not completely sealed.

      - Apply roofing granules to cover exuded bead at laps while bead is hot.

      - Seam and end laps shall be rolled with a minimum 20 lb. roller when being heat welded.  On Wood Deck Areas, do not heat weld seams and laps with flame producing equipment, use hot air welding equipment only.

    - Install roofing membrane sheets so side and end laps shed water.

  - Flashing and stripping installation

    - Install base flashing over cant strips and other sloped and vertical surfaces, at roof edges, and at penetrations through roof; secure to substrates according to roofing system manufacturer’s written instructions, and as follows:

      - Prime substrates with asphalt primer if required by roofing system manufacturer.

      - Backer Sheet Application:  Mechanically fasten backer sheet to walls or parapets.  Adhere backer sheet over roofing membrane at cants in cold-applied adhesive.

      - Backer Sheet Application: Adhere backer sheet to substrate in cold-applied adhesive at rate required by roofing system manufacturer.

      - Flashing Sheet Application: Adhere flashing sheet to substrate in cold-applied adhesive at rate required by roofing system manufacturer.

    - Extend base flashing up walls or parapets a minimum of [8 inches] above roofing membrane and [4 inches] onto field of roofing membrane.

    - Mechanically fasten top of base flashing securely at terminations and perimeter of roofing.

      - Seal top termination of base flashing with a strip of glass-fiber fabric set in asphalt roofing cement.

      - Membrane base flashings are to be secured at the top edge with fasteners spaced a maximum of 6" on center under metal counterflashings or cap, as detailed. Secure top of flashing membrane with aluminum termination bar with coated heavy-duty masonry fastener or lead anchor fastener 6" on center, for masonry substrates.

    - Install roofing membrane cap-sheet stripping where metal flanges and edgings are set on membrane roofing according to roofing system manufacturer’s written instructions.

    - Metal Counter Flashing:  Cover all vertical base flashings with metal counter flashing to form a continuous water shedding surface over the top of membrane flashing.  Extend metal counter flashing a minimum of 3 inches over the top of the membrane flashing.

    - Metal Face Securement:  Install hook strips (cleats) on all metal extending over roof edges (coping metal, gravel stop/eave strip, perimeter curb metal, etc.) in accordance with recommendations in the NRCA Roofing and Waterproofing Manual.  Appropriate provision must be made in accessory metal to allow for expansion and contraction of the metal sections without interrupting the integrity of the waterproofing assembly.

    - Roof Drains:  Set [30-by-30-inch] <Insert size> square metal flashing in bed of roofing-manufacturer-approved asphaltic adhesive on completed roofing membrane.  Cover metal flashing with roofing membrane cap-sheet stripping and extend a minimum of [4 inches] [6 inches] beyond edge of metal flashing onto field of roofing membrane.  Clamp roofing membrane, metal flashing, and stripping into roof-drain clamping ring.

      - Install stripping according to roofing system manufacturer’s written instructions.

    - Pipe Penetration Flashing: Set new Primed 4 lb. Pipe boot primed lead sheet in a bed of mastic, over smooth surfaced modified bitumen inner ply sheet. Over the primed lead sheet, strip-in with an additional layer of modified bitumen base flashing ply sheet lapping onto membrane inner ply sheet by a minimum of 6”.

      - Raise plumbing vents to provide a minimum twelve (12) inch flashing height at all locations.

    - Raise all roof curbs, and roof penetrations to provide a minimum eight (8) inch flashing at all locations.

  - coating installation

    - Apply coating to [roofing membrane] [and] [base flashings] according to manufacturer’s written instructions, by spray, roller, or other suitable application method [to provide a dry film thickness of not less than 20 mils].

  - walkway installation

    - Walkway Pads:  Install walkway pads using units of size indicated, or, if not indicated, of manufacturer’s standard size according to walkway pay manufacturer’s written instructions.

      - Install walkways at all traffic concentration points (such as roof hatches, access doors, rooftop ladders, mechanical equipment that requires servicing, etc.) and all locations as identified on the Contract Drawings.

      - Set walkway pads in cold-applied adhesive.

    - Walkway Cap Sheet Strips: Install walkway cap sheet strips over roofing membrane using same application method as used for roofing membrane cap sheet.

  - field quality control

    - Testing agency:  LANL will engage a qualified testing agency to perform tests and inspections and to prepare test reports.

    - Test Cuts:  Test specimens will be removed to evaluate problems observed during quality-assurance inspections of roofing membrane as follows:

      - Approximate quantities of components within roofing membrane will be determined according to ASTM D 3617.

      - Test specimens will be examined for interplay voids according to ASTM D 3617 and to comply with criteria established in Appendix 3 in NRCA’s “Quality Control Guidelines for the Application of Polymer Modified Bitumen Roofing.”

      - Repair areas where test cuts were made according to roofing system manufacturer’s written instructions.

    - Final Roof Inspection:  Arrange for roofing system manufacturer’s technical personnel to inspect roofing installation on completion.

      - Notify LANL STR 48 hours in advance of date and time of inspection.

    - Roofing system will be considered defective if it does not pass tests and inspections.

      - Additional testing and inspecting, at Construction Subcontractor’s expense will be performed to determine if replaced or additional work complies with specified requirements.

  - protecting and cleaning

    - Do not leave installed insulation exposed to weather.  Cover and waterproof immediately after installation.

      - Temporarily seal exposed insulation edges at the end of each day by lapping roofing membrane over edge to form a seal.  Remove seal when Work resumes.

      - Remove installed insulation that has become wet or damaged and replace the new insulation material.

    - Protect insulation from traffic with protective covering materials during and after installation.

    - Protect roofing system from damage and wear during remainder of construction period.  When remaining construction will not affect or endanger roofing, inspect roofing for deterioration and damage, describing its nature and extent in a written report, with copies to LANL STR.

    - Correct deficiencies in or remove roofing system that does not comply with requirements, repair substrates, and repair or reinstall roofing system to a condition free of damage and deterioration at time of Substantial completion and according to warranty requirements.

    - Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

    - Maintain job site in a clean, orderly fashion, and free of debris.  Store materials and equipment so operations of building are not interrupted.

END OF SECTION

*************************************************************

Do not delete the following reference information:

*************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 07 5217 Rev. 2, dated December 13, 2022.