SECTION 07 8400

FIRESTOPPING

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Fire POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

summary

SECTION INCLUDES

Firestopping through-penetrations of fire rated assemblies.

Firestopping joints in fire rated assemblies.

Firestopping tops of fire rated walls.

Smoke sealing in vertical and horizontal smoke barriers.

RELATED SECTIONS

Section 09 2116 - Gypsum Board Systems: Gypsum board fireproofing.

Division 22 - Plumbing work requiring firestopping.

Division 23 - HVAC work requiring firestopping.

Division 26 - Electrical work requiring firestopping.

Division 27 – Communications work requiring firestopping.

Division 28 – Electronic Safety and Security work requiring firestopping.

REFERENCES

********************************************************************************************

List reference standards included within text of this section. Edit the following for Project conditions. Differing tests are utilized by manufactures in qualifying similar products to regulatory agency performance criteria.

For FOD 1 (TA-55), add to below listing:

4.  LANL FOD Procedures

      - TA55-AP-123 – TA-55 Fire Barrier Program

      - TA55-AP-124 – Penetration Numbering and Labeling

****************************************************************************************************

ASTM International

        - ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials

        - ASTM E119 - Standard Test Methods for Fire Tests of Building Construction and Materials

        - ASTM E814 - Standard Test Method for Fire Tests of Through-Penetration Fire Stops

        - ASTM E1966- Standard Test Method for Fire-Resistive Joint Systems.

Intertek Testing Services (Warnock Hersey Listed):

        - WH – Certification Listings

South Coast Air Quality Management District:

        - SCAQMD  Rule 1168 – Adhesive and Sealant Applications

Underwriters Laboratories Inc.:

        - UL 263 - Fire Tests of Building Construction and Materials

        - UL 1479 – Fire Tests of Through-Penetration Firestops

        - UL 2079 – Tests for Fire Resistance of Building Joint Systems

        - UL – Fire Resistance Directory

Factory Mutual Research Approval Guide

        - Wall and Floor Penetration Fire Stops

California Department of Health Services

        - CA/DHS/EHLBR/R-174 - “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers.” Including 2004 Addenda.

International Building Code

National Fire Protection Association (NFPA) as referenced in the International Building Code (IBC).

DEFINITIONS

Firestopping (Through-Penetration Protection System): Sealing or stuffing material or assembly placed in spaces between and penetrations through building materials to arrest movement of fire, smoke, heat, and hot gases through fire rated construction.

Smoke Seal: A firestopping assembly of at least ½ hour fire rating. The International Building Code requires smoke seals as a minimum between stories in multi-story buildings.

action submittals

**********************************************************************************************************

Action Submittals must be approved by FP-DO prior to installation.  Indicate that the following Action Submittals are to be concurrently reviewed by FP-DO on the Exhibit I Submittal List.
***********************************************************************************************************

Product Data: Submit data on product characteristics, performance and limitation criteria.

Schedule: Submit schedule of opening locations and sizes, penetrating items, and required listed design numbers to seal openings to maintain fire resistance rating of adjacent assembly.

Manufacturer’s Certificate: Certify [products] meet or exceed [specified requirements,] [applicable code requirements.]

Engineering Judgments: For conditions not covered by UL, FM or WH listed designs, submit judgments by licensed professional engineer suitable for presentation to authority having jurisdiction for acceptance as meeting code fire protection requirements.

Manufacturer’s Installation Instructions: Submit preparation and installation instructions.

INFORMATIONAL SUBMITTALS

Qualification Data: For qualified Installer.

Product Test Reports: Based on evaluation of comprehensive tests performed by a qualified testing agency, for penetration firestopping.

Submit Material Safety Data Sheets for each product supplied.

sustainable design submittals

Materials Resources Certificates:

Certify recycled material content for recycled content products.

Certify source for regional materials and distance from Project site.

Indoor Air Quality Certificates:

Certify volatile organic compound content for each interior [adhesive] [and] [sealant] and related primer.

Certify firestopping products contain no added ureaformaldehyde resins.

Laboratory Test Reports: For penetration firestopping sealants and sealant primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers.”

closeout submittals

Submit complete maintenance material and detailed instructions for repair/modifications for each product supplied.

Installer Certificates: From installer indicating penetration firestopping has been installed in compliance with specified requirements and manufacturer’s written recommendations.

quality assurance

Manufacturer Qualifications:  Company specializing in manufacturing products specified in this section with a minimum of three years documented experience.

Installer Qualifications: A firm that has been approved by FM Global according to most current version of FM Global 4991, “Approval of Firestop Contractors,” or been evaluated by UL and found to comply with the latest version of its “Qualified Firestop Contractor Program Requirements.”

Installer Qualifications: A firm experienced in installing penetration firestopping similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful performance. Qualifications include having the necessary experience, staff, and training to install manufacturer’s products per specified requirements. Manufacturer’s willingness to sell its penetration firestopping products to Subcontractor or to Installer engaged by Subcontractor does not in itself confer qualification on buyer.

Fire-Test-Response Characteristics: Penetration firestopping shall comply with the following requirements:

Penetration firestopping tests are performed by a qualified testing agency acceptable to LANL authorities having jurisdiction.

Penetration firestopping is identical to those tested per testing standard referenced in “Penetration Firestopping” Article. Provide rated systems complying with the following requirements:

- Penetration firestopping products bear classification marking of qualified testing and inspecting agency.

- Classification markings on penetration firestopping correspond to designations listed by the following:

- UL in its “Fire Resistance Directory.”

- Intertek ETL SEMKO in its “Directory of Listed Building Products.”

- FM Global in its “Building Materials Approval Guide.”

- <Insert name of qualified testing and inspecting agency>.

delivery, storage, and handling

Deliver firestopping products to Project site in original, unopened containers or packages with intact and legible manufacturer’s labels identifying product and manufacturer.

Store and handle firestopping materials in accordance with manufacturers written instructions and the applicable Material Safety Data Sheet (MSDS).

field or site conditions

Do not apply materials when temperature of substrate material and ambient air is below 60 degrees F.

Maintain this minimum temperature before, during, and for minimum 3 days after installation of materials.

Install and cure penetration firestopping per manufacturer’s written instructions using natural means of ventilations or, where this is inadequate, forced-air circulation.

Coordinate construction of openings and penetrating items to ensure that penetration firestopping is installed according to specified requirements.

Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to accommodate penetration firestopping.

Notify LANL Subcontract Technical Representative (STR) at least seven days in advance of penetration firestopping installations; confirm dates and times on day preceding each series of installations.

products

  - manufacturers

Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

A/D Fire Protection Systems Inc.

Grace Construction Products.

Hilti, Inc.

Johns Manville.

Nelson Firestop Products.

Specified Technologies Inc.(STI)

3M Fire Protection Products.

Tremco, Inc.; Tremco Fire Protection Systems Group.

USG Corporation.

<Insert manufacturer’s name>.

description

Regulatory Requirements

****************************************************************************************************

Use this article carefully; restrict statements to identify system performance requirements or functional criteria only.
*************************************************************************************************************

Conform to [applicable code] [FM] [UL] [WH] for fire resistance ratings and surface burning characteristics.

Provide certificate of compliance from LANL authority having jurisdiction indicating approval of materials used.

Sustainability Characteristics

VOC Content: Penetration firestopping sealants and sealant primers shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

- Sealants: 250 g/L.

- Sealant Primers for Nonporous Substrates: 250 g/L.

- Sealant Primers for Porous Substrates: 775 g/L.

Low-Emitting Materials: Penetration firestopping sealants and sealant primers shall comply with the testing and product requirements of the California Department of Health Services’ “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers.”

performance / design criteria

Through-penetration fire stop systems shall have been tested in accordance with ASTM E814 or ANSI/UL 1479 to achieve fire ratings of adjacent construction [shown on the Drawings] [noted in Schedule at end of this section.]

All firestop systems and materials shall be UL Listed, ETL Semko Listed or FM Approved, and shall conform to the construction type, penetrant type, annular space requirements, and fire rating involved in each separate instance.

Through-penetration fire stop systems shall conform to applicable requirements for flame spread and smoke developed ratings.

Ensure that products from only one manufacturer are installed throughout the facility in order to maintain consistency.

UL Joint and Perimeter Fire Containment Systems Numbering System

| Alpha Characters | Description of Joint System |
| --- | --- |
| FF | Floor-to-Floor |
| WW | Wall-to-Wall |
| FW | Floor-to-Wall |
| HW | Head-to-Wall |
| BW | Bottom-to-Wall |
| CG | Wall-to-Wall Joints Intended for Use as Corner Guards……… |
| CW | Perimeter fire containment system (for use at the interface of a fire rated floor and a nonfire-rated exterior curtain wall. |
| The third alpha character is movement capability (S or D) | S – joint or perimeter fire containment systems that do not have movement capabilities D – joint or perimeter fire containment systems that do have movement capabilities |
| Number Range | Nominal Joint Width or Max. Clearance Distance Between Curtain Wall & Perimeter of Floor |
| 0000-0999 | Less than or equal to 2 inches |
| 1000-1999 | Greater than 2 inches and less than or equal to 6 inches…….. |
| 2000-2999 | Greater than 6 inches and less than or equal to 12 inches |
| 3000-3999 | Greater than 12 inches and less than or equal to 24 inches……. |
| 4000-4999 | Greater than 24 inches |

materials

PENETRATION FIRESTOPPING

Provide penetration firestopping that is produced and installed to resist spread of fire according to requirements indicated, resist passage of smoke and other gases, and maintain original fire-resistance rating of construction penetrated. Penetration firestopping systems shall be compatible with one another, with the substrates forming openings, and with penetrating items if any.

Penetrations in Fire-Resistance-Rated Walls: Provide penetration firestopping with ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg.

- Fire-resistance-rated walls include [fire walls] [fire-barrier walls] [smoke-barrier walls] [and] [fire partitions].

- F-Rating: Not less than the fire-resistance rating of constructions penetrated.

Penetrations in Horizontal Assemblies: Provide penetration firestopping with ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg.

- Horizontal assemblies include [floors] [floor/ceiling assemblies] [and] [ceiling membranes of roof/ceiling assemblies].

- F-Rating: At least 1 hour, but not less than the fire-resistance rating of constructions penetrated.

- T-Rating: At least 1 hour, but not less than the fire-resistance rating of constructions penetrated except for floor penetrations within the cavity of a wall.

Penetrations in Smoke Barriers: Provide penetration firestopping with ratings determined per UL 1479.

- L-Rating: Not exceeding 5.0 cfm/sq.ft. of penetration opening at 0.30-inch wg at both ambient and elevated temperatures.

W-Rating: Provide penetration firestopping showing no evidence of water leakage when tested according to UL 1479.

Exposed Penetrations Firestopping: Provide products with flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

Accessories: Provide components for each penetration firestopping system that are needed to install fill materials and to maintain ratings required. Use only those components specified by penetration firestopping manufacturer and approved by qualified testing and inspecting agency for firestopping indicated.

- Permanent forming/damming/backing materials, including the following:

          - Slag-wool-fiber or rock-wool-fiber insulation

          - Sealants used in combination with other forming/damming/backing materials to prevent leakage of fill materials in a liquid state.

          - Fire-rated form board

          - Fillers for sealants

- Temporary forming materials.

- Substrate primers.

- Collars.

- Steel sleeves.

Fill Materials

Cast-in Place Firestop Devices: Factory-assembled devices for use in cast-in-place concrete floors and consisting of an outer metallic sleeve lined with an intumescent strip, a radial extended flange attached to one end of the sleeve for fastening to concrete formwork, and a neoprene gasket.

Latex Sealants: Single-component latex formulations that do not re-emulsify after cure during exposure to moisture.

Firestop Devices: Factory-assembled collars formed from galvanized steel and lined with intumescent material sized to fit specific diameter of penetrant.

Intumescent Composite Sheets: Rigid panels consisting of aluminum-foil-faced elastromeric sheet bonded to galvanized-steel sheet.

Intumescent Putties: Nonhardening dielectric, water-resistant putties containing no solvents, inorganic fibers, or silicone compounds.

Intumescent Wrap Strips: Single-component intumescent elastomeric sheets with aluminum foil on one side.

Mortars: Prepackaged dry mixes consisting of a blend of inorganic binders, hydraulic cement, fillers, and lightweight aggregate formulated for mixing with water at Project site to form a nonshrinking, homogeneous mortar.

Pillows/Bags: Reusable heat-expanding pillow/bags consisting of glass-fiber cloth cases filled with a combination of mineral-fiber, water-insoluble expansion agents, and fire-retardant additives. Where exposed, cover openings with steel-reinforcing wire mesh to protect pillows/bags from being easily removed.

Silicone Foams: Multi-component, silicone-based liquid elastomers that, when mixed, expand and cure in place to produce a flexible, nonshrinking foam.

Silicone Sealants: Single-component, silicone-based, neutral-curing elastomeric sealants of grade indicated below:

Grade: Pourable (self-leveling) formulation for openings in floors and other horizontal surfaces, and nonsag formulation for openings in vertical and sloped surfaces, unless indicated firestopping limits use of nonsag grade for both opening conditions.

Mixing

For those products requiring mixing before application, comply with penetration firestopping manufacturer’s written instructions for accurate proportioning of materials, water (if required), type of mixing equipment, selection of mixer speeds, mixing containers, mixing time, and other items or procedures needed to produce products of uniform quality with optimum performance characteristics for application indicated.

Labels: Red background and white lettering (or other contrasting color combination outside of TA-55) self-adhesive label with adhesives capable of permanently bonding labels to surfaces on which labels are placed, or plastic or metal plate. As a minimum stating the installation is a “fire rated assembly” or “through-penetration fire stop system,” and installation data (UL-Listed or FM-Approved configuration number, date installed, installer and organization). Also state “Modify/remove only with LANL Fire Group approval” if space permits. Examples of acceptable products:

Hilti sticker P/N 00339611; STI Sticker Z1005-892-CG; 3M Sticker 98040056289

Hilti plate P/N 00306219

EXECUTION

  - EXAMINATION

Examine substrates and conditions, with Installer present, for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

Verify openings are ready to receive firestopping (items penetrating the opening have been installed, opening is appropriately sized to allow use of the proposed firestopping system, etc.).  Verify site conditions (ex., weather) are appropriate for installation of necessary materials.

Before firestoppping installation, notify LANL STR so that inspection of existing conditions and installation can occur.

PREPARATION

Surface Cleaning: Clean out openings immediately before installing penetration firestopping to comply with manufacturer’s written instructions and with the following requirements:

Remove from surfaces of opening substrates and from penetrating items foreign materials that could interfere with adhesion of penetration firestopping.

Clean opening substrates and penetrating items to produce clean, sound surfaces capable of developing optimum bond with penetration firestopping. Remove loose particles remaining from cleaning operation.

Remove laitance and form-release agents from concrete.

Priming: Prime substrates where recommended in writing by manufacturer using that manufacturer’s recommended products and methods. Confine primers to areas of bond; do not allow spillage and migration onto exposed surfaces.

Masking Tape: Use masking tape to prevent penetration firestopping from contacting adjoining surfaces that will remain exposed on completion of the Work and that would otherwise be permanently stained or damaged by such contact or by cleaning methods used to remove stains. Remove tape as soon as possible without disturbing firestopping’s seal with substrates.

installation

General: Install penetration firestopping to comply with manufacturer’s written installation instructions and published drawings for products and applications indicated.

Install forming materials and other accessories of types required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of firestopping.

Install fill materials for firestopping by proven techniques to produce the following results:

Fill voids and cavities formed by openings, forming materials, accessories, and penetrating items as required to achieve fire-resistance ratings indicated.

Apply materials so they contact and adhere to substrates formed by openings and penetrating items.

For fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

*****************************************************************

Delete Paragraph 4 when work is not for FOD 1 (TA-55)

*****************************************************************

Complete the Through Penetration Spreadsheet and ensure that the applicable fire barrier drawings are updated as required as identified in TA55-AP-123 and TA55-AP-124.  Provide a completed copy of the spreadsheet to the appropriate barrier system engineer.

permanent identification of fire walls and penetrations

All fire-resistance-rated walls and smoke partitions shall be labeled with specified labels to indicate that the wall is either fire-resistance-rated or is a smoke partition. If the wall is fire-resistance rated, indicate “FIRE RATED – X HOURS” and the applicable fire-resistance rating (one, two, three, or four-hours). If the wall is a smoke partition, indicate “SMOKE PARTITION” (no fire-resistance rating is required to be labeled. The labeling shall be located on the fire-resistance-rated wall or smoke partition above ceilings and at exposed areas (such as Mechanical and Electrical Equipment Rooms) on 10-foot intervals and as high as possible and still visible from the finished floor. Areas of fire-resistance-rated walls and smoke partitions exposed to viewing by the public shall be exempt from labeling.

Identify penetration firestopping with preprinted metal or plastic labels on both sides of the penetrated fire barrier. Attach labels permanently to surfaces adjacent to and within 6 inches of firestopping edge so labels will be visible to anyone seeking to remove penetrating items or firestopping. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. [For FOD 1 (TA-55), install labels per TA55-AP-123 Fire Barrier Program and TA-55-AP-124 Penetration Numbering and Labeling]. Include the following information on labels:

The words “Warning – Penetration Firestopping – Do Not Disturb. Notify Facility Management of Any Damage.”

Contractor’s name, address, and phone number.

Designation of applicable testing and inspecting agency.

Date of installation.

Manufacturer’s name.

Installer’s name.

repairs and modifications

All repairs and modifications shall be made using the same manufacturer’s products as the original system.

Identify damaged or disturbed seals requiring a repair or modification.

Remove loose or damaged materials.

If penetrating items are to be added, remove enough material to insert new items, being careful not to cause damage to the balance of the firestop system. Re-seal voids in the penetration.

Ensure that surfaces to be sealed are clean and dry.

All repaired and modified firestop systems shall be labeled.

field quality control

LANL will engage a qualified testing agency to perform tests and inspections.

Where deficiencies are found or penetration firestopping is damaged or removed because of testing, repair or replace penetration firestopping to comply with requirements.

Proceed with enclosing penetration firestopping with other construction only after inspection reports are issued and installations comply with requirements.

cleaning and protection

Clean off excess fill materials adjacent to openings as the Work progresses by methods and with cleaning materials that are approved in writing by penetration firestopping manufacturers and that do not damage materials in which openings occur.

Provide final protection and maintain conditions during and after installation that ensure that penetration firestopping is without damage or deterioration at time of Substantial Completion. If, despite such protection, damage or deterioration occurs, immediately cut out and remove damaged or deteriorated penetration firestopping and install new materials to produce systems complying with specified requirements.

penetration firestopping schedule

Where UL-classified systems are indicated, they refer to system numbers in UL’s “Fire Resistance Directory” under product Category XHEZ.

Where Interek ETL SEMKO—listed systems are indicated, they refer to design numbers in Intertek ETL SEMKO’s “Directory of Listed Building Products” under “Firestop Systems.”

Where FM Global-approved systems are indicated, they refer to design numbers listed in FM Global’s “Building Materials Approval Guide” under “Wall and Floor Penetration Fire Stops.”

Firestopping with No Penetrating Items [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-L-] <Insert four-digit number> [0001-0999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Firestopping for Metallic Pipes, Conduit, or Tubing [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [1001-1999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

#### Firestopping for Nonmetallic Pipe, Conduit, or Tubing [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [2001-2999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Electrical Cables: [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [3001-3999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Cable Trays with Electric Cables [FS<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [4001-4999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Insulated Pipes [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] [W-N-] <Insert four-digit number> [5001-5999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Miscellaneous Electrical Penetrants [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [W-L-] [W-J-] <Insert four-digit number> [6001-6999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Miscellaneous Mechanical Penetrants [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [7001-7999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

Firestopping for Groupings of Penetrants [FS-<#>]:

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [8001-8999].

Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

FM Global-Approved Systems: <Insert design numbers>.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq.ft.>.

L-Rating at 400 deg. F: Less than <Insert cfm/sq.ft.>.

W-Rating: No leakage of water at completion of water leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

THIS STATEMENT FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 07 8400 Rev. 4, dated September XX, 2017.