SECTION 08 9100

LOUVERS

*************************************************************************************************************

LANL MASTER SPECIFICATION

When editing to suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  To seek a variance from applicable requirements, contact the ESM Architectural/Mechanical POC.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Delete information within “stars” during editing.

Specification developed for ML-3 projects.  For ML-1 / ML-2, additional requirements and QA reviews are required.

*************************************************************************************************************

PART 1  GENERAL

1.1	SECTION INCLUDES

A.	Exterior wall, drainable blade  stationary louver assemblies with removable bird screens.

1.2	QUALITY ASSURANCE

A.	Use products of a company specializing in the manufacture of AMCA certified louvers that bear the AMCA certified rating seal for air performance and water penetration.

1.3	SUBMITTALS

A.	Submit the following in accordance with the requirements of Section 01 3300, Submittal Procedures.

1.	Catalog data describing materials and finish, and product criteria.

2.	Manufacturer’s installation instructions.

3.	Samples or color charts of standard colors for metal and screen.

4.	Shop drawings indicating component details, framed openings, bearing, and anchor location of fasteners and accessories.

PART 2  PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

A. 	Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

MANUFACTURERS

A.	Dowco Corporation

B.	Construction Specialties, Inc.

C.	Industrial Louvers, Inc.

MATERIALS

A.	Aluminum Extrusions: ASTM B221, alloy 6063-T5.

- Aluminum Sheet: ASTM B209, alloy 3003 or 5005, with temper as required for forming.

- Fasteners: Use aluminum or 300 series stainless steel fasteners. Provide other accessories as required for complete and proper installations.

- Bird Screen: Standard expanded aluminum mesh, maximum ¾ inch.

ACCESSORIES

A.	Use flashings of same material as louver frame.

B.	Use sealants as specified in Section 07 9200.

FABRICATION

A.	Fabricate with nominal frame depth of 6 inches.

B.	Provide louvers of sizes indicated on the Drawings.

FINISHES

A.	Use submittal-approved finish and colors for exterior and interior metal surfaces and screens.

PART 3  EXECUTION

3.1	INSPECTION

A.	Verify that prepared openings and flashings are ready to receive work, and openings are as indicated on shop drawings.

B.	Beginning of installation indicates acceptance of existing conditions.

3.2	INSTALLATION

A.	Install louver in accordance with manufacturer’s installation instructions.

B.	Install louvers level and plumb.

C.	Secure louvers in opening with fasteners that are removable for maintenance purposes.

D.	Install flashings and align louver assembly to ensure moisture shed from flashings and diversion of moisture to the exterior.

E.	Install bird screen to interior of louver, removable for access.

F.	Install perimeter sealant in accordance with Section 07 9200.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 08 9100 Rev. 1, dated March 8, 2006.