SECTION 09 6919

STRINGERLESS ACCESS FLOORING

*************************************************************************************************************

LANL MASTER SPECIFICATION

When editing to suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  To seek a variance from applicable requirements, contact the ESM Architectural POC.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Delete information within “stars” during editing.

Specification developed for ML-3 projects.  For ML-1 / ML-2, additional requirements and QA reviews are required.

*************************************************************************************************************

PART 1  GENERAL

1.1	SECTION INCLUDES

A.	Floor support system  of stringerless framing type

B.	Removable floor panels

1.2	PERFORMANCE REQUIREMENTS

A.	Provide pedestals to support a maximum axial load of 5,000 pounds without causing permanent deformation. Ultimate strength shall be not less than twice the design load.

B.	Provide floor panels meeting the following requirements:

1.	Live load capacity of 250 psf.

2.	Maximum deflection of 0.080 inch with a concentrated load of 1,000 pounds on 1 square inch at any location.

3.	Permanent deformation of 0.01 inch maximum at design load.

4.	Ultimate strength of not less than twice the design load.

5.	Flame spread of 5 or less in accordance with ASTM E84.

C.	Design system for lateral stability in all directions, with or without panels in place.

D.	Maximum surface electrical resistance of one ohm per panel.

1.3	SUBMITTALS

A.	Submit the following in accordance with the requirements of Section 01 3300.

1.	Catalog data for grid system, panels and accessories.

2.	Manufacturer’s certification that products meet or exceed specified design strength and electrical resistance requirements.

3.	Manufacturer’s installation instructions.

4.	Color chart or samples of vinyl tile for color selection.

5.	Shop drawings indicating panel layout, interruptions to grid, special sized panels, panels requiring drilling or cutout for services, appurtenances or interruptions, and edge details.

6.	Maintenance data including recommended cleaning methods, cleaning materials, stain removal methods, and polishes and waxes.

PART 2  PRODUCTS

2.1	MANUFACTURERS

A.	C-Tec, Inc., Tec-Cor products

B.	Donn, AS-100 products

C.	Cate Access Floors, Series 600 products

2.2	SUPPORT COMPONENTS

A.	Provide steel pedestals with flat bottomed base plates, threaded supporting rods, vibration-proof lock nuts to permit 1 1/2 inch adjustment, and manufacturer’s standard finish.

B.	Pedestal to achieve finish floor elevation [ 12 ]  inch nominal height above subfloor.

2.3	PANEL COMPONENTS

A.	Provide floor panels with die formed steel top and bottom plates and reinforcing stiffeners, and plywood cores laminated with galvanized sheet steel structurally bonded with thermosetting adhesive to both faces.

B.	Provide 24 by 24 inch floor panels.

C.	Provide vinyl tile floor finish of static conductive type, 1/8 inch thick.

D.	Use vinyl tile adhesive of moisture resistant, electrically conductive type recommended by vinyl tile manufacturer.

2.4	ACCESSORIES

A.	Use extruded polyvinyl chloride or neoprene edging, 3/8 inch thick, self-extinguishing cable cutout protection.

B.	Provide a panel lifting device of manufacturer’s standard type.

C.	Use extruded plastic edge trim.

2.5	FABRICATION TOLERANCES

A.	Floor panel flatness - plus or minus 0.02 inch in any direction.

B.	Floor panel length or width from specified size - plus or minus 0.02 inch.

C.	Floor panel squareness - plus or minus 0.03 inch difference between opposite diagonal dimensions.

PART 3  EXECUTION

3.1	INSPECTION

A.	Verify that surfaces and openings are ready to receive Work of this Section.

B.	Verify that field measurements are as shown on shop drawings.

C.	Verify that required sub-floor utilities are available, in proper locations, and ready to receive Work of this Section.

3.2	PREPARATION

A.	Clean subfloor surfaces.

B.	Protect materials surrounding the Work of this Section from damage.

3.3	INSTALLATION

A.	Install assembly in accordance with approved shop drawings and manufacturer’s installation instructions.

B.	Secure pedestal baseplates to subfloor with adhesive.

C.	Install additional pedestals where grid pattern is interrupted by room appurtenances and at cutouts.

D.	Install floor panels solidly on pedestals.

E.	Cut holes in floor panels for installation of University’s equipment as directed. Install cable cutout protection.

F.	Seal field cuts of floor panels with edge trim.

3.4	ADJUSTING

A.	Adjust floor pedestals to achieve a level floor and to assure adjacent floor panel surfaces are flush.

3.5	CLEANING

A.	Clean Work under provisions of Section 01 7700.

3.6	PROTECTION OF FINISHED WORK

A.	Do not permit traffic over unprotected floor finish.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 09 6919 Rev. 0, dated January 6, 2006.