SECTION 21 1313

WET-PIPE SPRINKLER SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Fire POC.  Please contact the POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1 and 2 applications, additional requirements must be added for increased confidence in procurement or execution (and may be added for ML-3), and independent review is required; see ESM Chapter 1 Section Z10 Specifications and Quality sections.  Also, for ML-1 (Safety Class) and ML-2 (Safety Significant) sprinkler systems and water supplies only, DOE has issued guidance in DOE-STD-1066; this guidance will exceed NFPA 13 requirements and some expectations in this section, and requirements will need to be added herein.

*************************************************************************************************************

As a minimum, include the following Sections in bid package.

01 2500	Substitution Procedures

01 3300	Submittal Procedures

01 3545	Water Discharge Requirements

01 4200	References

01 4444	Offsite Welding and Joining Requirements:  General Welding Requirements

01 4455	Onsite Welding and Joining Requirements:  General Welding Requirements

01 7700	Closeout Procedures

01 7839	Project Record Documents

Applicable Division 05 sections on Post-Installed Anchors

09 9100	Painting

Applicable Division 21 section on Fire Alarm System

22 0554	Identification for Plumbing, HVAC, and Fire Piping and Equipment

22 0816	Disinfection of Potable Water Piping

22 0813	Testing Piping Systems

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Scope of Work: Provide design, shop drawings, project record drawings (as-built), equipment, fabrication, labor, transportation and supervision necessary to install, flush, test and place into service a complete hydraulically designed automatic wet pipe sprinkler system.

************************************************************************************************************

For existing fire sprinkler systems that are to be revised and/or extended, provide a detailed scope of work.  Note the design parameters for the existing system including the design density and area for hydraulically designed systems or type of pipe schedule for older systems that were not hydraulically designed.

*************************************************************************************************************

Components: The wet pipe fire sprinkler system shall consist of, but not be limited to, interconnecting piping, fittings, control valves, check valves, alarm valve with trim, fire department connection, sprinkler heads, hangers, bracing, Inspector's test stations, drains, sprinkler alarm and other devices for a complete installation in accordance with codes, standards and recommended practice referenced in this Section.

LANL-PERFORMED WORK

The LANL fire protection division will coordinate with the Los Alamos Fire Department to provide the subcontractor with water supply test data for existing fire protection water supplies.

DESIGN

The Subcontractor is responsible for performing hydraulic calculations for the sprinkler system in accordance with NFPA 13 that account for all flow and pressure requirements to the location of the flow test hydrant that was used to determine the static and residual pressures.  The Subcontractor is also responsible for determining the location and elevation of the static and residual test gauge relative to the riser reference point and providing this information on the sprinkler design plans in accordance with NFPA 13 (2010 edition sections 22.2.1 & 22.1.3(10)).

[Design the system in accordance with the most current edition of NFPA 13.]

*****OR*****

[Modifications to existing systems involving less than 10 sprinklers may be designed in accordance with the Code of Record edition of NFPA 13.  Modifications involving 10 or more sprinklers shall comply with the current edition of NFPA 13.]

At a minimum, design the system to protect an Ordinary Hazard Group II occupancy in accordance with NFPA 13, or as specified by the LANL Fire Marshal.

Regardless of the NFPA 13 occupancy or the response type of sprinkler head selected, the minimum design area shall be 1,500 ft2, or as specified by the LANL Fire Marshal.

A minimum 500 gpm hose stream allowance shall be provided.

Conform to extra or special hazard requirements where required or indicated.

Conform to NFPA 13 for storage occupancies with potential storage height greater than 12 feet and other special hazard occupancies.

System to operate at 7500 feet altitude.

Provide necessary devices and design the system to separate the system into individual and distinct alarm zones.  Provide a minimum of one zone per floor.

*************************************************************************************************************

The following seismic design requirement applies to fire protection sprinkler piping (FPSP) systems located in “commercial facilities.”   They are based on 2015 IBC, ASCE 7-10, NFPA 13-13, & ESM Ch. 5 Sect. II, R9.

The IBC requirements are found in its Sect. 1613, which references ASCE 7.  ASCE 7 para. 13.6.8.2, defers to NFPA 13 for the design & construction of FPSP, pipe hangers, and bracing.  Other components of fire protection systems (e.g., pumps and control panels, etc.) are subject to the general requirements of ASCE 7.

Referring to subparagraph 3 (below), the reason NFPA 13 para. 9.3.5.9.5 is N/A is the value of Cp that shall be used is stipulated in subparagraph 1 (below).

Seismic design for fire sprinkler systems located in Hazard Category 1–3 nuclear facilities; or facilities with biological hazards, or significant chemical or toxicological hazards shall be in accordance with ESM Chapter 5 Section III (in addition to the documents referred to in the first author note of this Section template).

*************************************************************************************************************

Seismic Design:  Design sprinkler system piping for protection against damage in accordance with NFPA 13 (Section 9.3 of the 2013 edition) subject to the following modifications:

- In Para 9.3.5.9.3, replace the phrase “where Cp is… Ss” with “where Cp is 0.52.”

  - For Work in TA-50/55, Cp = 0.42 can be used if desired.

- If Para 9.3.5.9.4 is used to determine the horizontal force, revise it to read as follows: “The horizontal force…Structures,” and paragraph 1.4.1 of LANL ESM Chapter 5 Section II, “multiplied by…(ASD).”

- Para 9.3.5.9.5 is not applicable.

**************************************************************************************************** 
The following sprinkler location design requirements apply to sprinkler systems installed below exposed concrete single and double TEE ceiling/roof construction. They are based on FM Global Property Loss Prevention Data Sheet 2-0, Installation Guidelines for Automatic Sprinklers, and differ from NFPA 13. DOE directives and standards establish the expectation for DOE facilities to meet Highly-Protected Risk (HPR) criteria, and applying the FM Global criteria for concrete TEE construction is responsive to this expectation. Concrete TEEs are typically considered obstructed construction for the purposes of applying NFPA 13 and FM Global Loss Prevention Data Sheet 2-0, and often have very deep stems on 3 to 8 feet centers that have the potential to adversely affect sprinkler operating performance.
****************************************************************************************************

Sprinkler Location Design for Exposed Concrete TEE Construction: Design for pendent or upright sprinklers to be located in every channel by formed by the obstructing exposed concrete TEE, and position the centerline of the sprinkler’s thermal sensing element a minimum of 1 inch and a maximum of 12 inches vertically below the underside of the ceiling bay. When sprinkler head spacing does not exceed of 130 ft2, the following exceptions may be applied when the criteria are met:

Concrete TEE members spaced up to 7.5 ft. on-center and extending no more than 21 inches from the underside of the ceiling bay: Locate the centerline of the sprinkler’s thermal sensing element on the horizontal plane no more than 6 inches vertically below the underside of the concrete TEE stem, and no more than 22 inches below the underside of the ceiling bay. The distance between sprinkler heads perpendicular to the concrete TEE stems shall not exceed 13 ft.

Concrete TEE members extend more than 21 inches from the underside of the ceiling bay: Locate the centerline of the sprinkler’s thermal sensing element on a horizontal plane no more than 22 inches below the underside of the ceiling bay.  The NFPA 13/FM Global Loss Prevention Data Sheet 2-0, Installation Guidelines for Automatic Sprinklers, criteria for structural obstructions must be met to allow development of the sprinkler discharge pattern. The distance between sprinkler heads perpendicular to the concrete TEE stems shall not exceed 13 ft.

ACTION SUBMITTALS

All submitted items must be approved by FP-DO prior to installation.  Submit the following per project submittal procedures:

Hydraulic Calculations prepared in accordance with NFPA 13.  Submit calculations with shop drawings.

****************************************************************************************************

Where static pressure is too low for these margins, seek variance per ESM Ch 1 Section Z10.

****************************************************************************************************

Provide a minimum 10% or 10 psi, whichever is greater, safety factor between the calculated sprinkler flow and pressure demand and the design basis water supply curve.  The calculated sprinkler demand shall include a minimum 500 gpm hose stream requirements in accordance with LANL ESM Fire Chapter Section D4010 (Para. 2.0B).

Include in calculations elevation differences between point of water test and base of riser.  Include graphical representation (N1.85) of design basis water supply curve and system demand.

The following preliminary flow data is provided to the Subcontractor for bidding purposes: static ______ psig, residual _____ psig, flow _____ gpm, hydrant number ____, hydrant elevation _______ feet.

Base system design on actual flow information provided by LANL.  Request actual flow data in a timely manner to maintain project schedules.

Seismic Design Documents:

Calculations, prepared in accordance with LANL AP-341-605 or LANL-FP-approved equivalent, that demonstrate compliance with 1.3.C.

Drawings, prepared in accordance with the LANL CAD Standard that convey the design to the constructor.

Test and Inspection Plan, prepared in accordance with LANL ESM Chapter 16, as necessary / applicable.

Items 1-3 (above) shall be stamped and sealed by a PE licensed in the state of NM.

Catalog Data with selected options marked.

Certifications for welders in accordance with NFPA 13.

Installation Instructions

Materials Part List (Bill of Materials) with manufacturer, model number, and quantity.

Shop Drawings using a minimum scale of 1/8" = 1'0" for plans and 1/4" = 1'0" for details.  All lettering shall be a minimum of 1/8 inch high.

Show information required by NFPA 13, including piping, sprinklers, hangers, flexible couplings, roof construction, electro-mechanical devices, occupancy of each area, and ceiling and roof heights.  See Chapter 22 of NFPA 13 for guidance on information required to be included on plans and calculations.

Base working plans on actual survey of existing conditions.

Show hydraulic reference points and remote areas.

Test Reports

Operation and Maintenance Manual: Submit system description, system final inspection, and Subcontractor's material and test certificates per NFPA 13, of the completed system project record documents.

Include in operation and maintenance manuals, instructions, a brief description of type of system installed, routine maintenance work defined by step-by-step instructions, and recommended frequency of performance.

Also include in instructions, possible malfunctions with diagnostic methods and suggested correction of each.

Describe function of each component or subassembly.

List recommended spare parts (manufacturer, model number, and quantity).

Project Record Drawings (As-Built) on CDs and prints reflecting as-built conditions showing Work completed under this Section.

Base as-built drawings on actual survey of the completed installation.

Include notes on all special systems or devices such as dry pendent heads, antifreeze loops and inspector's test stations.

Provide revised hydraulic calculations demonstrating water supply restrictions have not been exceeded when conditions of installation are different from those anticipated during preparation of Project Record Documents.

The project manager shall submit as-built plans to the LANL Records office in accordance with Section 01 7700, Closeout Procedures and Section 01 7839, Project Record Documents.

QUALITY ASSURANCE

Provide proof that installation firm has satisfactorily performed at least ten projects of equivalent nature and scope of the Projects herein; and is licensed within the USA to engage in design, fabrication and installation of automatic sprinkler systems for fire protection.

DELIVERY, STORAGE, AND HANDLING

Materials and Equipment: Protect materials and equipment from damage during shipping, storage and installation.

Plugs and Cover Plates: Protect threaded ends, flanged openings with gasketed metal cover plates to prevent damage during shipment and to prevent foreign materials from entering.  Cap or plug drains, vents, small piping, and gauge connections.

Store sprinkler heads at temperatures required by the manufacturer prior to installation.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

MATERIALS

Provide new fire protection materials and equipment, UL Listed or FM Approved, conforming to NFPA 13.

PIPING AND FITTING MATERIALS

Provide in accordance with NFPA 13, except that piping 2 inches and smaller shall be Schedule 40 minimum.

Provide flange bolting per ASME 16.1 and 16.5 for ductile and steel flanges respectively.

VALVES AND STRAINERS

Provide Listed or Approved valves and strainers rated at 175 psi or greater working pressure.

Check Valves: In sizes 3 inch and larger, provide 3/4 inch NPT drainage taps.

Strainers: Provide "Y" type strainers with cast iron body and 30-mesh stainless steel screen.

Alarm Valve: Minimum acceptable size is 4 inches.  Provide retardant chamber, two (2) calibrated/verified water pressure gauges, and necessary valves and trim for alarm valve operation.

Provide bypass valve in trim to allow test operation of pressure alarm switch.

Equip alarm valve with retard chamber and pressure alarm switch with one normally open contact and one normally closed contact, suitable for 24 VDC.

Provide check valve in retard chamber drain line when retard chamber drain line ties into main riser drain.

PRESSURE GAUGES

Provide listed/approved calibrated/verified pressure gauges designed for use with water.

Gauge Scale: Dial marking subdivision no finer than 1 percent of maximum scale reading and accurate to 3 percent or less.  Provide minimum scale range twice the maximum working pressure (when possible).

VALVE SUPERVISION (tamper switches)

Equip valves which control water to automatic sprinkler heads with supervisory switches.

Provide valve supervisory switches with single pole double throw switching contacts, housed in gasketed, weather-tight enclosure, suitable for 24 VDC.

Supply supervisory device specifically designed to mount on, and operate reliably with, type of control valve being monitored.

Adjust valve position switches to transmit a supervisory signal within two revolutions of valve operating hand wheel or crank (away from its full open position).

Control valves in alarm lines, if provided, shall be electrically supervised.  Provide alarm control valve with supervisory switch, Potter Electric part number BVS, or approved equivalent, suitable for 24 VDC.

WATER FLOW SWITCHES

Provide a Potter Model PS10A Pressure Switches, or approved equivalent, (suitable for 24 VDC) at the sprinkler riser to detect a water flow condition in the system.

For waterflow alarm switches at located at other than the system riser, provide Potter Electric vane-type flow switches, or approved equivalent, with field adjustable pneumatic retard and 175 psi working pressure.

Use single pole double throw, normally open switches, suitable for 24 VDC.

Adjust water flow switches to transmit an alarm within 90 seconds of opening the inspector’s test valve.

Provide a minimum of one water flow switch per floor.

SPRINKLERS AND ACCESSORIES

All sprinklers shall be listed by a nationally recognized testing laboratory and shall be selected in accordance with their Listing, manufacturer’s instructions, and applicable NFPA requirements.  Provide sprinklers as follows:

Upright Sprinklers: Brass upright type.  Use in areas without suspended ceilings.

Pendent Sprinklers: Chrome plated.  Use below suspended ceilings if required by the design.

Sprinkler Guards: Provide where sprinkler heads are exposed to external damage.

Corrosion-Resistant Sprinklers: Provide in locations where chemicals, moisture or other corrosive vapors exist. Stainless steel, polyester or Teflon-coated sprinklers are preferred over wax-coated. Confirm selection of corrosion-resistant sprinkler heads with the LANL Fire Marshal.

Concealed Sprinklers: Use listed/approved concealed type sprinklers in clean rooms when required by the design.

Where indicated, provide other types of sprinklers in accordance with their Listing.

WATER SHIELDS

Provide in areas where there is no ceiling, and when multiple-level protection is required, e.g., at open-grating or open high-roofed areas.

Provide compatible Listed/Approved water shields and/or intermediate level sprinklers in accordance with NFPA 13.

Water shields shall not be considered/used as ‘heat collectors’ for sprinkler heads.

FIRE DEPARTMENT CONNECTIONS

Provide fire department connections with 4 inch minimum outlet, two 2-1/2 inch minimum inlets, National Fire Standard threads, cast brass body, clapper in each inlet, plugs, and attached chains.

Fire department connections shall be located on the fire department approach side of the building and be readily visible from the designated fire lanes and where they will remain unobstructed by equipment, landscaping, parking, or other features.

When wall-mounted, locate pumper connections on blank masonry wall, or provide wall with one hour fire barrier for 10 feet in all directions from pumper connection, and identify automatic sprinkler connection.

Identify individual devices by raised letters on the individual devices, or attach escutcheon plates of same material.

Erosion Protection

Concrete splash blocks or other approved methods shall be provided at system exteriors drains that do not discharge to a hard covered surface to protect landscape from erosion due to discharge from the drains.

ANTIFREEZE Systems

#### *************************************************************************************************************

#### Provide a backflow preventer (BFP) in the antifreeze loop when a BFP is not installed in the sprinkler riser supplied from a potable water system.  Systems supplied from a dedicated loop or tank (non-potable water) do not require backflow protection.

#### *************************************************************************************************************

Install antifreeze systems in accordance with NFPA 13 and with an approved factory pre-mixed solution of 48% glycerin and 52% water.

Provide an approved sign in an approved location in the vicinity of the antifreeze system control valve that states the following information in accordance with NFPA 13:

    - Antifreeze solution type and concentration

    - Antifreeze solution brand/manufacturer

    - Antifreeze solution volume.

SPRINKLER RISER BACKFLOW PREVENTER

#### *************************************************************************************************************

#### Provide a backflow preventer in a new system when the fire protection system is supplied from a potable water system.  Systems supplied from a dedicated fire loop or tank (non-potable water) do not require backflow protection.  Refer to Fire Protection Standard Drawings ST D4010-1 for riser detail with backflow preventer.
*************************************************************************************************************

Manufacturers: Backflow preventers shall be one of the following:

FEBCO, Model LF880V.

Wilkins, Model 475V.

Reduced pressure type, vertical orientation, ductile iron body epoxy coated internal and external, with UL/FM OS & Y gate valves, flanged ends, test cocks for in-line field testing and relief valve air gap drain funnel. Provide BFPs listed as “Lead Free” construction by the manufacturer. Maximum water temperature range 33 to 140 degrees F, maximum rated working pressure 175 psi.  Assembly shall be listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulics Research.  Size to match alarm check valve.

Means shall be provided to drain backflow discharge to outside the building or to a floor drain with sufficient capacity to contain the discharge.  The discharge drain pipe size shall be the same nominal diameter as the backflow preventer.  The drain pipe shall be routed to the exterior of the building where the exposed pipe opening shall be covered by ¼-inch hardware cloth.

Means shall be provided downstream of all backflow prevention valves for flow tests at system demand (NFPA 13, 2010 ed., Section 8.17.4.6.1) to make sure the backflow prevention device operates correctly  by allowing the fire sprinkler demand, including hose stream demand if required, through the device at the designed pressure loss.

A test header and/or bypass around the fire department connection check valve will be required for Ordinary Hazard and greater sprinkler designs.

The test header connection shall be clearly and permanently marked as “BACKFLOW TEST CONNECTION”

The test connection control valve shall be supervised in the closed position.  Supervision by locking the valve will be acceptable.

Means, such as an automatic ball drip valve, shall be provided to prevent accumulations of water at the test connection that are subject to freezing.

SPRINKLER SYSTEM AIR VENT

An air vent, or means to vent air from the piping network, shall be installed at an approved location at the high-point of the system to allow air to be removed per NFPA 13.

Manufacturers: Where provided, automatic air vents shall be one of the following:

Potter Electric Signal Company, Model PAV

LANL-approved equivalent.

EXECUTION

  - EXAMINATION

Prior to installation carefully inspect installed Work of other trades, whether pre-existing or part of this Project, and verify that such work is complete to the point where installation of sprinkler system may start.

Notify the LANL Subcontract Technical Representative (STR) should conditions exist, not resulting from Work of this Project, that prohibits the installation from conforming to referenced codes, regulations, standards and approved design.

Install materials and equipment that are free of moisture, scale, corrosion, dirt and other foreign materials.

INSTALLATION

General:

Install system in accordance with NFPA 13.

Do not locate sprinkler heads closer than 12 inches to supply air registers.

Visually examine pipe, fittings, valves, equipment and accessories to ensure they are clean and free of burrs, cracks and other imperfections before installation.  Clean pipe interiors by flushing.

Verify dimensions in field.

Drawings show only approximate building outlines and interior construction details as an aid in understanding the scope of Work.  Investigate structural and finish conditions affecting the Work and arrange Work accordingly, providing such sprinkler heads, fittings, traps, draining valves, piping, and accessories as required to meet such conditions.  Show relevant structural details on Drawings.

Do not render inoperative any system without the prior approval of the LANL STR.  Coordinate necessary shutdowns of existing systems by notifying the LANL STR a minimum of 7 working days before rendering such systems inoperative.

Coordinate sprinkler piping, sprinkler heads and associated equipment with existing ceiling or roof materials, lighting, ductwork, conduit, piping, suspended equipment, structural and other building components.

Dispose of equipment removed for completion of this Project as directed by the LANL STR.

Provide access openings in areas where concealed sprinkler piping is installed.

Piping:

Mark and identify sprinkler piping in accordance with Section 22 0554 Identification for Plumbing, HVAC, and Fire Piping and Equipment.

Conceal sprinkler piping in areas with suspended ceilings.  Install piping in exposed areas as high as possible using necessary fittings and auxiliary drains.  Keep sprinkler piping a minimum of 7 feet 6 inches above finish floor.  Where not possible, run piping at same elevation as existing piping and ducts.  Obtain prior approval from the LANL STR.

Install Inspector's Test piping at the hydraulically most remote point of automatic sprinkler system and discharge to the exterior of building.  Also install inspector’s test piping for each water flow switch.  Where possible, conceal test piping in wall and provide access panels for valve and sightglass and protect from freezing.  Locate Inspector's Test Station in an easily accessible location approved by the LANL STR.

Diamond core drill or sleeve concrete penetrations, then grout and seal with fire-resistive material, securely held in place.  Use Listed/ through penetration fire stop system assemblies for piping penetrating fire resistance rated construction.

Hanging, Bracing and Restraint of System Piping:

Install pipe hangers for pipe supports inside buildings in accordance with NFPA 13.

Install the seismic protection of the system piping, including sway bracing, as indicated and in accordance with the version of NFPA 13 indicated.  Include the required features indentified therein that are applicable to the specific piping system.

Install concrete anchors as indicated and in accordance with Division 5 sections on post-installed anchors.

Do not hang other piping, wiring or equipment from sprinkler pipe, hangers or supports.

Welding:

Shop weld pipe and fittings using approved welding fittings.  Comply with NFPA 13 for welding methods.

Provide a blind flange or grooved cap at each end of welded headers.

Comply with 01 4444 -- Offsite Welding and Joining Requirements and 01 4455 -- Onsite Welding and Joining Requirements.

Alarm Valve: Set plumb and unobstructed.  Provide minimum clear distances from walls to centerline of alarm valve as follows:

Rear - 12 inches

Sides - 20 inches

Front - 36 inches

System Riser: Install riser from underground so that no joint or fitting occurs within the bearing zone of foundation structures or occurs at least 5 feet from any foundation structure.

Control Valves: Provide Listed OS&Y fire protection control valves.  Installed so open or closed status can be readily seen from finish floor.

Install control valves on supply lines (outside protected area) into elevator shaft and elevator equipment room, computer rooms, and identified special protection areas. Control valves to be accessible from floor level. Provide valve with tamper supervision switches.

Sprinklers and Accessories:

Provide upright sprinklers on exposed piping below ceiling.  Pendent sprinklers may be used where necessary due to spacing, location and position requirements.

Provide chrome plated pendent, recessed, or flush mounted sprinklers below finish ceilings.  Route supply piping above ceiling.

Align sprinklers below ceiling parallel to ceiling features and walls, and locate as close to center as possible in halls and corridors.

Provide chrome-plated escutcheons where exposed piping passes through finished floors, walls, partitions and ceilings.  Secure to pipe with set screws or spring clips.

Protect sprinklers subject to mechanical injury with guards as follows:

- Provide guards in mechanical equipment rooms, electrical equipment rooms, janitor's closets, and storage areas where distance from sprinkler deflector to finish floor is less than 15 feet.

- In all other areas, provide guards where distance from sprinkler deflector to finish floor is less than 7 feet.

To prevent freezing, extend dry pendent sprinklers a minimum of 6 inches into heated area before connection to wet sprinkler piping.

Provide one spare sprinkler cabinet, complete with sprinklers of assorted temperature ratings of the type necessary and in use throughout the installation, at each main riser valve.  Equip each cabinet per NFPA 13.

Signs:

Install as required by NFPA 13.

Post indicator valves (PIVs) shall be provided with a permanent weatherproof placard identifying the building or area protected by the sprinkler system for which the PIV controls the water supply.

Provide a sign attached in the vicinity of control valves to antifreeze systems designating the type, concentration, manufacturer/brand and volume of antifreeze solution installed in the system.

Provide a permanent, weatherproof sign noting “BACKFLOW TEST CONNECTION” located on the exterior of the building in the immediate vicinity of the backflow test connection valves.

****************************************************************************************************

Edit “Painting” (Para 3.2.J) to clearly define the extent of painting of sprinkler system piping and appurtenances (e.g., which rooms). Painting need not be provided for factory-painted/-finished alarm check valves, backflow preventers, control valves and similar devices. Painting of piping may be warranted for the protection of the piping to mildly corrosive environments, where easy identification of the sprinkler system is desired from a facility operations perspective, or for cosmetic purposes when exposed (e.g., stairwells).

***************************************************************************************************

Painting: Paint unfinished sprinkler riser piping, unfinished fire department connection (FDC) piping, exposed sprinkler piping in stairwells, and sprinkler piping in all mechanical, electrical and telecommunications equipment rooms with two (2) coats of Fire Protection RED.  Do not paint sprinkler heads.  Any sprinkler heads receiving paint require replacement.  Comply with Section 09 9100, Painting.

Unsupervised Water Supplies: Install approved water flow detection device on underground water supplies entering buildings when fire protection riser is more than 10 lineal feet from exterior of building.

Water Supply Control Valve: Where not otherwise provided for, provide water supply control valve(s) conforming to the requirements of NFPA 24.

Provide UL Listed or FM valves, with listed indicating post.  Post Indicator Valves (PIVs) shall be located at minimum of 40 feet from building in accordance with NFPA 24.  PIVs may be located closer than 40 feet from building providing they are located outside the collapse area of the building’s walls.  Fire hydrants and PIVs proposed to be located closer than 40 feet away from a building shall receive prior approval of the location from LANL Fire Protection.

When a PIV is located less than 20 feet from building, or when a wall PIV is provided, the wall 10 feet in all directions of the valve shall be blank masonry or one-hour fire-resistance-rated construction.

PIVs shall be set so that the top of the post is 32 inches to 40 inches above the final grade.

PIVs shall be protected against mechanical damage (e.g., bollards).

Air Vent(s): Manual air vent valve location(s) shall be accessible. Automatic and manual air vent device location(s) shall not be installed in areas with finished ceilings or reliance placed on access panels in ceilings for accessibility.

Special Tools and Devices: Provide one complete set of special tools or special devices required for operation, testing and/or maintenance of equipment furnished under this Section.

EQUIPMENT INSTALLATION

Install devices or equipment not specifically covered by these Specifications in accordance with manufacturer's instructions.

CONNECTIONS TO EXISTING SYSTEMS

Final connection of new systems to existing underground piping systems will be made by LANL with materials furnished by the Subcontractor.

Final connection of new systems to other existing systems above grade shall be done by the Subcontractor after contacting the LANL STR who will implement LANL Fire Protection Impairment Procedure.  Do all final connections of this type with only one outage per existing system.

STERILIZATION

Sterilize sprinkler system underground piping upstream of alarm valve in accordance with Section 22 0816, Disinfection of Potable Water Piping.

Do not sterilize sprinkler system downstream of alarm valve.

EXISTING CONDITIONS

Area Restoration: Restore areas disturbed by the fire protection system installation to the condition existing prior to start of construction.

Field Inspection: Field inspect areas of sprinkler installation for potential interference with ducts, cable trays, electrical or mechanical equipment, and other similar interferences.  Carefully coordinate Work under this section with other Work.

TESTING

Hydrostatically test piping in accordance with Section 22 0813, Testing Piping Systems, and NFPA 13.

Flush system with water in accordance with NFPA 13 and 24.

Comply with the discharge requirements in Section 01 3545, Water Discharge Requirements.

Notify LANL STR, LANL Fire Protection Division, and LANL Facility Operations Director (FOD) representative at least 5 working days in advance to witness all system tests.

INSPECTION

Inspect new fire protection system in accordance with NFPA 13 and 24, in the presence of the LANL STR.  Provide advance notice, as specified below, to the STR prior to any tests.

Notify the LANL STR upon completion of installation of all materials and equipment.  LANL STR will schedule inspection of installation within 5 working days after Subcontractor notification.

Correct deficiencies noted during this inspection and correct prior to further testing.

END OF SECTION

#### ***********************************************************

#### Do not delete the following reference information:

#### ***********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Spec Section 21 1313 Rev. 8, dated April 25, 2018.