SECTION 22 0529

HANGERS AND SUPPORTS FOR PLUMBING PIPING AND EQUIPMENT

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these. This specification template is tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM).  To seek a variance from requirements of the ESM that are applicable, contact the Engineering Standards Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

PART 1  GENERAL

  - SECTION INCLUDES

- Furnish and install pipe hangers, supports, hanger rods, and sleeves, and other positive fastenings for mechanical non-structural components such that gravity loads are safely transferred to the structure.

  - Related REQUIREMENTS

- Refer to Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems for seismic control/protection requirements for mechanical non-structural components.

  - ACTION SUBMITTALS

    - Product Data: For each type of product indicated.

*************************************************************************************************************

NOTE: Shop drawing submittals typically not required for ML-4 projects, may be required for engineered supports.

*************************************************************************************************************

    - Shop Drawings: Show fabrication and installation details [and include calculations] for the following; include Product Data for components:

      - Trapeze pipe hangers.

      - Metal framing systems.

      - Pipe stands.

    - For custom fabrications, certification of offsite welders and qualified welding procedure per Section 01 4444 (follow 01 4455 for onsite work).

  - QUALITY ASSURANCE

- Hangers and supports shall conform to the requirements of the following codes and standards as applicable:

- ASME B31.1 [year], Power Piping

- ASME B31.5 [year] , Refrigeration Piping and Heat Transfer Components

- ASME B31.9 [year], Building Services Piping

- Uniform Plumbing Code – [2015], (UPC)

- NFPA 13, Standard for the Installation of Sprinkler System

- MSS SP-58 [year], Pipe Hangers and Supports

- Qualify welding processes and welding operators in accordance with AWS D1.1 “Structural Welding Code - Steel” for hangers and supports.

PART 2  PRODUCTS

## PRODUCT OPTIONS AND SUBSTITUTIONS

- Alternate products may be accepted; follow Section 01 2500, Substitution Procedures

## PIPE HANGERS AND SUPPORTS

    - MSS-SP-58, Types 1 through 58, factory-fabricated components

    - Hangers for Pipe Sizes 1/2 to 1-1/2 inches: Malleable iron or carbon steel, adjustable swivel, split ring.

    - Hangers for Cold Pipe Sizes 2 inches and over: Carbon steel, adjustable, clevis.

    - Hangers for Hot Pipe Sizes 2 to 4 inches: Carbon steel, adjustable, clevis.

    - Hangers for Hot Pipe Sizes 6 inches and over: Adjustable steel yoke, cast iron roll, double hanger.

    - Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods.

    - Multiple or Trapeze Hangers for Hot Pipe Sizes 6 inches and over: Steel channels with welded spacers and hanger rods, cast iron roll.

    - Wall Support for Pipe Sizes to 3 inches: Strut clamp or cast iron hook.

    - Wall Support for Pipe Sizes 4 inches and over: Welded steel bracket and wrought steel clamp.

    - Wall Support for Hot Pipe Sizes 6 inches and over: Welded steel bracket and wrought steel clamp with adjustable steel yoke and cast iron roll.

    - Vertical Support: Steel riser clamp.

    - Floor Support for Cold Pipe: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.

    - Floor Support for Hot Pipe Sizes to 4 inches: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.

    - Floor Support for Hot Pipe Sizes 6 inches and over: Adjustable cast iron roll and stand, steel screws, and concrete pier or steel support.

    - Copper Pipe Support: MSS SP-58, Types 1 through 59, non-metallic coating, jacket, or liner on steel factory-fabricated components.

## HANGER RODS

- Mild steel threaded both ends, threaded on one end, or continuous threaded.

- Rods for trapeze hangers shall be a minimum 3/8-inch.  The use of pipe hooks, chains, perforated iron strapping, or wire for pipe supports are NOT permitted.

## SLEEVES

- Sleeves for Pipes through Non-Fire Rated Beams, Walls, Footings, and Floors:  Steel pipe or 18 gage galvanized steel.

- Sleeves for Pipes through Fire Rated and Fire Resistive Floors, Walls, and Roof: Prefabricated fire rated sleeves including seals, approved by a nationally recognized testing laboratory (UL listed).

- Sleeves for Ductwork: Galvanized steel.

PART 3  EXECUTION

*************************************************************************************************************

NOTE: Verify that supporting structural elements are adequate to support the imposed hanger load.

*************************************************************************************************************

- PIPE HANGERS AND SUPPORTS

- Support piping to maintain its alignment, and prevent sagging.

- Place hangers within 12 inches of each horizontal elbow.

- Support vertical piping with riser clamps secured to the piping and resting on the building structure at each floor.

- Install hangers to provide minimum 1/2 inches space between finished covering and adjacent work.

- Use hangers with 1-1/2 inches minimum vertical adjustment.

- Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

- Support riser piping independently of connected horizontal piping.

- Provide coated, jacketed, or liner on steel hangers and supports for copper piping.

- Provide insulation continuous through hangers and rollers.  Protect insulation by steel shields in accordance with Section 22 0713, Plumbing and HVAC Insulation.

- Provide hangers on piping on each side of, and within 6 inches of, hubless pipe couplings so the couplings will bear no weight.

- Provide supports that allow free axial movement and only support the weight of the piping or tubing. Provide additional hangers or brackets to support valves, flanges, specialties, etc., to prevent excessive deflection.

- [Prime coat exposed steel hangers and supports.  Refer to Section 09 9100, Painting.  Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed.]

- SLEEVES

- Provide sleeves for all pipe penetrations through walls, roof, or slab above grade.

- Neatly cut holes in existing walls, floors, or roof for placement of sleeves.  Place sleeve and grout and caulk annular space to provide finished appearance.

- Extend sleeves through floor slab 2 inches above finished floor level.  Caulk sleeves full depth and provide floor plate.

- Seal space between pipe and sleeve watertight for all sleeves penetrating the roof.

- Where piping or ductwork penetrates a fire rated wall or floor, provide fire-stopping insulation so that the assembly when complete retains the fire rating of construction penetrated by the sleeve.

- HANGER SPACING

*************************************************************************************************************

The hanger spacing tables are for straight runs of standard and heavier steel pipe, and Type L and heavier copper tube.  They are not intended to be used as specifications for all installations.  These do not apply where span calculations are made or where there are concentrated loads between supports, such as flanges, valves, specialties, etc, or changes in direction requiring additional supports.

For Victaulic flexible systems and other piping material, consult with the manufacturer for suggested hanger spacing.  For Victaulic rigid couplings used in steel piping systems, the spacing below may be used.

*************************************************************************************************************

- Plumbing Piping - Water, Gas, Drain, Waste and Vent (DWV)

- Comply with the requirements of the Uniform Plumbing Code, (IAPMO), Hangers and Supports, Table 313.3.

- Fire Protection Piping

- Comply with the requirements of NFPA-13 for hanger spacing and materials.

- Steam/Condensate Piping Inside Building, up to 15 psig.

- Comply with the requirements of ASME B31.9, Building Services Piping.

- Maximum Hanger Spacing:

| Steel Pipe Size (Inches) | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |

- Steam/Condensate Piping Outside Building, up to 150 psig.

- Comply with the requirements of ASME B31.1, Power Piping.

- Maximum Hanger Spacing

| Steel Pipe Size (Inches) | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) | 9 | 9 | 9 | 13 | 15 | 17 | 21 | 24 |

- Water Building Services Piping, up to 150 psig (Heating, Cooling, and Tower Water)

- Comply with the requirements of ASME B31.9, Building Services Piping.

- Maximum Hanger Spacing

| Size (Inches) | Less Than 1 | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 6 | 9 | 11 | 12 | 13 | 16 | 18 | 23 | 25 |
| Spacing (Feet) Copper Tube | 5 | 7 | 7 | 8 | 9 | 10 | 12 | 14 | 16 |

- Air and Laboratory Gas Building Services Piping, up to 150 psig

- Comply with the requirements of ASME B31.9, Building Services Piping.

- Maximum Hanger Spacing:

| Size (Inches) | 1/4 to 1/2 | 5/8 to 7/8 | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 6 | 6 | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |
| Spacing (Feet) Copper/SS Tube | 3 | 5 | 7 | 9 | 10 | 12 | 15 | 17 | 21 | 24 |

- Refrigeration Piping

      - Comply with the requirements of ASME B31.5.

      - Maximum Hanger Spacing:

| Size (Inches) Nominal | 1/4 | 3/8 to 1/2 | 3/4 | 1 | 1 ¼ | 1 ½ to 2 | 2-1/4 to 2-1/2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Copper Tube (Liquid or Vapor Service) | 5 | 5 | 5 | 6 | 7 | 8 | 9 |

- HANGER ROD SIZE

- Plumbing (UPC) Piping (Water, Gas, DWV)

| Pipe Size (Inches) | 1/2 - 4 | 5 - 8 |
| --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 |

- HVAC Piping (Steam, Condensate, Water, Air, Laboratory Gas)

| Pipe or Tubing Size (Inches) | 3/8 - 2 | 2 ½ - 3 ½ | 4 - 5 | 6 – 8 | 10 - 12 |
| --- | --- | --- | --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 | 5/8 | 3/4 | 7/8 |

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0529 Rev. 6, dated October 21, 2020.