SECTION 22 0554

IDENTIFICATION FOR PLUMBING, HVAC, AND FIRE PIPING AND EQUIPMENT

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Valve Tags.

Pipe Markers/Arrow Tape Above Ground.

Underground Piping Warning Tape.

Ceiling Tacks.

Duct Markers.

Mechanical Equipment and HVAC Controls Identification.

Safety Signs.

Fire Hydrants and Isolation Valves Numbering.

LANL Performed work

LANL Utilities will identify hydrants and hydrant isolation valves.  Refer to PART 3.

[Labeling for mechanical equipment and HVAC controls will be furnished and installed by LANL.]

Definitions

Exposed Areas: Finished areas and other areas used by personnel in normal use of building, such as equipment rooms and storage rooms.

Concealed Areas: Duct or pipe tunnels, duct or pipe chases, spaces above accessible ceilings, and crawl spaces.

SUBMITTALS

- Submit the following in accordance with Section 01 3300, Submittal Procedures:

Catalog data.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

MANUFACTURER

W. H. Brady Co. catalog numbers are used as a basis of identification.

Stock catalog numbers are listed in PART 2 and PART 3 schedules.  Subcontractor is responsible to review schedules and provide required markers. In some instances, "non-stock" markers (special) may be required.

VALVE TAGS

Metal Tags: Brass or aluminum with stamped or engraved letters; tag sizes minimum 2 inches (round, square, or rectangle) with smooth edges.  Thickness 19 gauge (.040 inches) minimum.

Beaded Chain: Size 6, brass or aluminum, 4 1/2 inches long with locking link.

PIPE MARKERS/ARROW TAPE ABOVE GROUND

Color: Conform to ANSI A13.1.

Self-Sticking Pipe Markers/Arrow Tape: Material B-946, flexible, vinyl film tape with pressure sensitive permanent adhesive backing and printed markings.

Suitable for indoor/outdoor application.

Temperature range: Minus 40 degrees to 180 degrees F.

UNDERGROUND PIPING WARNING TAPE

Comply with Section 31 2000, Earth Moving.

CEILING TACKS

No. 23250 series, steel with 7/8-inch diameter color-coded head.

Color code as follows:

| 1. | Yellow | HVAC Equipment |
| --- | --- | --- |
| 2. | Red | Fire Dampers / Smoke Dampers |
| 3. | Green | Plumbing Valves, Trap-Priming Devices, etc. |
| 4. | Blue | Heating / Cooling Valves |

DUCT MARKERS

Plastic Tape Duct Marker and Arrows: Material No. B-946, flexible vinyl film tapes with pressure sensitive permanent adhesive backing and printed markings.

Suitable for indoor/outdoor application.

Temperature range: Minus 40 degrees to 180 degrees F.

Letter style block, 2 inches height minimum.

MECHANICAL EQUIPMENT and HVAC CONTROLS IDENTIFICATION

*************************************************************************************************************

Consult with the facility engineer to determine labeling requirements (numbering scheme, bar code, labels, Subcontractor vs. LANL furnished and installed labeling, etc.) and edit this section as required.

*************************************************************************************************************

Labeling shall be furnished and installed by the [Subcontractor] [LANL].

Engraved signs shall be dark letters on light background.

Identify mechanical equipment and HVAC controls, e.g., air handling units, pumps, heat transfer equipment, water treatment devices, controls instruments, stationary tanks/containers, and similar items, with nameplates or tags.

*************************************************************************************************************

Provide the following unless otherwise directed by the facility engineer.

*************************************************************************************************************

Provide engraved nameplates made of rigid plastic laminate in which colored top and bottom layers of the material are thermoset with a contrasting color core. Minimum thickness 0.062 inch.

Size: [1 x 3], [2 x 3], [1.5 x 4], [2 x 4] or [               ] inches.

Material Color: [White background/ black lettering] or [                     ].

Manufacturer: Brady, No. B-1

Provide lettering as follows:

Size: 10 point minimum (larger preferred).

Spacing: 1/4 inch from top, 1/8 inch from bottom, 1/16 inch between lines.

Provide nameplate with component nomenclature as noted in the Subcontract Documents.

As a minimum, identify the system, e.g., HVAC (heating, ventilating, and air conditioning), the component, e.g., FGF (furnace, gas fired), and the sequence number.

Refer to the ESM, Chapter 1, Section 230, for component nomenclature for new and major modifications to facilities.

Provide fume hoods (FH) and other local exhaust ventilation (LEV) systems with nameplates as specified below to indicate the following information:

Fume hood and other local exhaust ventilation system inlets.

Served by nameplates: Exhaust fan information.

Exhaust fan data.

Fan static pressure

Fan RPM

Motor current.

Coordinate equipment nameplates with equipment numbering scheme provided by Subcontract Technical Representative.

Provide nameplates made of one of the following materials.

Laminated plastic adhesive tape with machine printed letters. (Indoor Applications Only)  Manufacturer: Brother, Seton, Brady.

Two-ply plates with letters engraved through surface color showing core color.  Use UV stabilized material for outdoor applications.  Manufacturer: Seton Nameplate Corp.

Provide 10 point minimum size lettering.

Provide nameplates with black letters on a white background.

Dimensions of nameplates shall be 1 inch by 2 ½ inch minimum.

Stationary Tanks/Containers of Hazardous Materials: Identify the hazardous material and label to comply with NFPA 704, Standard System for the Identification of Hazards of Materials for Emergency Response.

Name of Hazardous Material: Provide 2 inch high minimum lettering.  Use same material as pipe identification markers, yellow background with black letters.

Hazardous Material Signal and Characters: Provide 2 inch high minimum characters and a 5 inch square (overall size) diamond shaped material signal made of outdoor grade pressure sensitive vinyl.  Refer to the Material Safety Data Sheet (MSDS) for the hazardous material for numbers, letters, or symbols to be used within the NFPA 704 hazardous material signal.  Material signal: Brady catalog number 58501.  Characters: Brady catalog numbers 
[            ].

SAFETY SIGNS

Colors associated with specific words such as "Danger," "Warning," "Caution," or "Notice" shall conform to ANSI Z35.1.

Provide signage identifying each fixture, including fume hood cup sinks, being served by non-potable water.

EXECUTION

  - FIRE HYDRANTS

LANL Utilities and Infrastructure will number fire hydrants and the hydrant isolation valves (valve box lids).

PREPARATION

Degrease and clean surfaces to receive adhesive for identification materials.

INSTALLATION

Valve Tags:

Install with brass beaded chain.

Steel stamp or engrave valve tag in accordance with schedule herein.

Letter style block, 1/4-inch height minimum.

Tag all valves in concealed or exposed areas except isolation and by-pass valves installed adjacent to the equipment they serve.

Provide typewritten letter size list of applied tags and location.  [Frame under glass and hang where directed].

Pipe Markers Above Ground:

Install in accordance with manufacturer's instructions.

Seal markers with clear lacquer.

Identify piping in exposed or concealed areas in accordance with schedule herein.

Pipe marker consists of pipe contents identification with flow direction arrow tape. Provide consistent color scheme, unless otherwise noted.

Wrap arrow tape completely around pipe at both ends of pipe markers.

Install in clear view and align with axis of piping.

Label piping at intervals of not more than 20 feet on horizontal and vertical runs, 
at each branch connection, and where pipe penetrates walls, ceilings and floors (both sides).

Label waste piping below laboratory sinks to indicate destination.

Size of label depends on outside diameter (OD) of pipe.  Pipe OD includes insulation or protective coating.

Minimum length of marker including arrows:

| Outside Diameter | Length (inches) |
| --- | --- |
| 2 inches or smaller | 8 |
| Greater than 2 inches to less than 8 inches | 12 |
| 8 inches to 10 inches | 24 |
| Over 10 inches | 32 |

Ceiling Tacks: Provide ceiling tacks to locate HVAC equipment, valves or dampers above accessible suspended ceilings.  Locate tacks in corner of panel closest to equipment.

Duct Markers:

Install in accordance with manufacturer's instructions.

Seal markers with clear lacquer.

Identify ducts in exposed or concealed areas in accordance with the schedule.

Duct markers consist of duct identification name with flow direction arrows.  Provide consistent color scheme.

Install in clear view and align with axis of duct.

Label ducts at intervals of not more than 20 feet on horizontal and vertical runs, at each branch connection, and where duct penetrates walls, ceilings and floors (both sides).

Mechanical Equipment and HVAC Controls Identification:

Install component identification tag on the front of each piece of mechanical equipment including fans, pumps, compressors, fume hoods, LEVs, etc.

Position tags so they can be read from floor.

Safety Signs: Install in clear view.

SCHEDULES

Pipe Markers and Valve Tag Legend:

|  |  | Outside Diameter (Letter Height) |  |
| --- | --- | --- | --- |
| Pipe Identification | Background Color/ Letter Color | 6" or greater (3 1/2" high) Style 1HV* | 3" to less than 6" (2" high) Style 1* | 1" to less than 3" (3/4" high) Style 4* | Less than 1" (5/16" high) Style 3C* | Valve Tag Legend |
|  |  | Pipe Marker Catalog Numbers |  |
| Acetylene Gas | Yel/Blk | 7001 | AC |
| Argon | Grn/Wht | 7015 | AR |
| Breathing Air | Grn/Wht | 7035 | BA |
| Chemical/Supply | Yel/Blk | 7042/7311 | CS |
| Chilled Water Return | Grn/Wht | 7046 | CWR |
| Chilled Water Supply | Grn/Wht | 7047 | CWS |
| Compressed Air | Yel/Blk | 7058 | CA |
| Condensate Pump Discharge | Yel/Blk | 7064 | CONPMP |
| Deionized Water/Drain | Grn/Wht | 7073/7090 | DIWD |
| Deionized Water Return | Grn/Wht | 7074 | DIWR |
| Deionized Water Supply | Grn/Wht | 7075 | DIWS |
| Drain | Grn/Wht | 7090 | D |
| Drain | Yel/Blk | 7091 | D |
| Fire Protection Water | Red/Wht | 7110 | F |
| Fuel Oil Return | Yel/Blk | 7116 | FOR |
| Fuel Oil Supply | Yel/Blk | 7117 | FOS |
| Fuel Oil Vent | Yel/Blk | 7118 | FOV |
| Electric Traced | Yel/Blk | 7096 | ------ |
| Heating Water Return | Yell/Blk | 7129 | HWR |
| Heating Water Supply | Yel/Blk | 7130 | HWS |
| Helium | Grn/Wht | 7132 | HE |
| High Pressure Condensate (Above 15 PSIG) | Yel/Blk | 7137 | CONHP |
| High Pressure Natural Gas (Above 5 PSIG) | Yel/Blk | 7139 | NG |
| High Pressure Steam (Above 15 PSIG) | Yel/Blk | 7141 | STMHP |
| Hydrogen | Yel/Blk | 7157 | H2 |
| Instrument Air | Blu/Wht | 7168 | IA |
| Liquid Nitrogen | Yel/Blk | 7172 | LN |
| Low Pressure Condensate (15 PSIG or less) | Yel/Blk | 7175 | CONLP |
| Low Pressure Natural Gas (Less than 14" W.C.) | Yel/Blk | 7177 | NGL |
| Low Pressure Steam (15 PSIG or less) | Yel/Blk | 7179 | STMLP |
| Medium Pressure Natural Gas (14" W.C. to 5 PSIG) | Yel/Blk | 7190 | NGM |
| Nitrogen | Grn/Wht | 7198 | N2 |
| Non-Potable/Cold Water | YelBlk/ GrnWht | 7203/7055 | NPWC |
| Non-Potable/Hot Water | Yel/Blk | 7203/7146 | NPWH |
| Non-Potable/Make-up Water | Yel/Blk Grn/Wht | 7203/7182 | NPMU |
| Non-Potable/Hot Water Recirculation | Yel/Blk | 7203/7147 | NPWHR |
| Oxygen | Yel/Blk | 7209 | O2 |
| Potable/Cold Water | Grn/Wht | 7217/7055 | PWC |
| Potable/Hot Water (Use Grn/Wht Arrows) | GrnWht/ YelBlk | 7217/7146 | PWH |
| Potable/Hot Water Recirculation (Use Grn/Wht Arrows) | GrnWht/ YelBlk | 7217/7147 | PWHR |
| Process/Cooling Water Return | Grn/Wht | 7224/7071 | PCWR |
| Process/Cooling Water Supply | Grn/Wht | 7224/7072 | PCWS |
| Process Liquid Waste-Hazardous | Yel/Blk | Special | PLWH |
| Process Liquid Waste- Non Hazardous | Grn/Wht | Special | PLWNH |
| Radioactive Liquid Waste | Yel/Blk | Special | RLW |
| Radioactive Liquid Waste Vent | Yel/Blk | Special | RLWV |
| Refrigerant Discharge (Hot Gas) | Yel/Blk | 7234 | RFND |
| Refrigerant Liquid | Yel/Blk | 7235 | RFNL |
| Refrigerant/Relief | Yel/Blk | 7235/7239 | RFNR |
| Refrigerant Suction | Yel/Blk | 7236 | RFNS |
| Sanitary Vent | Yel/Blk | 7252 | SWV |
| Sanitary Waste | Yel/Blk | 7253 | SW |
| Sanitary Wastewater Treated Effluent | Yel/Blk | Special | SWTE |
| Storm Water | Grn/Wht | 7275 | STW |
| Sump Pump Discharge | Yel/Blk | 7280 | SPD |
| Tower Water/Drain | Grn/Wht | 7285/7090 | TWD |
| Tower Water Return | Grn/Wht | 7286 | TWR |
| Tower Water Supply | Grn/Wht | 7287 | TWS |
| Vacuum | Yel/Blk | 7291 | VAC |
| Vacuum/Pump Discharge | Yel/Blk | 7291/7280 | VACPD |

* Include style number in parenthesis (      ) following the catalog number.

AIR DUCT MARKERS

| Duct Identification | Background Color/ Letter Color | Catalog Number |
| --- | --- | --- |
| Air Return | Blu/Wht | 7008 |
| Air Supply | Blu/Wht | 7010 |
| HEPA Exhaust Air | Yel/Blk | Special/7098/7005 |
| Lab Exhaust Air | Blu/Wht | Special/7100 |
| Mixed Air | Blu/Blk | Special/7006 |
| Outside Air | Blu/Wht | 7206 |
| Perchloric Exhaust Air | Yel/Blk | Special/7098/7005 |
| Relief Air | Blu/Wht | 7240 |
| Toilet Exhaust Air | Blu/Wht | Special/7100 |
| Vacuum Exhaust Air | Yel/Blk | 7291/7098/7005 |

SAFETY SIGNS

| Location | Wording | Size/Catalog Number |
| --- | --- | --- |
| Each fixture served by non-potable water | NOTICE Non-Potable Water not to be used for drinking, washing or cooking purposes. | 7 X 10/40925 |
| First steam valve inside the building. | CAUTION Only Utilities is authorized to operate this valve. Call 7-4842 to schedule valve operation. | Special order. Yellow background color/black lettering. Size 5 x 10 (min.), aluminum. |
| Fire Hydrant served by non-potable water | CAUTION Non-Potable Water – Do Not Drink. | 7 X 10/40846 |

END OF SECTION

**********************************************************

Do not delete the following reference information:

**********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0554 Rev. 2, dated June 4, 2009.