SECTION 22 1316

SANITARY WASTE AND VENT PIPING

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  This specification template is tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM). To seek a variance from requirements of the ESM that are applicable, contact the ESM Mechanical POC Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Refer to Section 33 3000 for site sanitary sewerage utilities.

Seismic: In order to edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the Seismic Specification Guide for Nonstructural Components: Mechanical Components posted with the templates for guidance on properly editing this section.

*************************************************************************************************************

GENERAL

- SECTION INCLUDES

- Building piping, fittings, and accessories within building and 5 feet beyond building wall.

- RELATED SECTIONS

*************************************************************************************************************

Seismic:  Refer to Guide for editing guidance for this article.

*************************************************************************************************************

    - [Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements pertaining to [manufacturer’s certification] [and] [special certification].]

    - [Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.]

- ACTION SUBMITTALS

- Submit the following in accordance with Project submittal procedures:

Catalog data on pipe materials, fittings and accessories.

Manufacturer's Installation Instructions for piping and accessories.

- QUALITY ASSURANCE

    - Comply with the Uniform Plumbing Code, IAPMO, [2015].

    - Comply with NSF/ANSI 14, "Plastics Piping Systems Components and Related Materials," for PVC piping components.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

    - Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - [SEISMIC PERFORMANCE REQUIREMENTS]

    - The [______] shall remain in place without separation of any parts when subjected to the design-basis earthquake [per Section 01 8734, Seismic    Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems].

  - SANITARY WASTE PIPING, BURIED WITHIN 5 FEET OF BUILDING

*************************************************************************************************************

Coordinate material selection with Civil Designer. See Article 2.4 author’s Note 1 for limitations on the use of PVC DWV piping.

*************************************************************************************************************

    - Cast Iron Pipe and Fittings: ASTM A74 service weight, bell and spigot ends.

      - Joints: Hub and spigot, CISPI HSN compression type with ASTM C564 rubber gaskets.

    - PVC Pipe and Fittings: ASTM D2665, polyvinyl chloride (PVC) material, Schedule 40 DWV.

      - Joints: ASTM D2855, solvent weld with ASTM D2564 solvent cement.

  - SANITARY WASTE AND VENT PIPING, ABOVE GRADE INSIDE BUILDING

************************************************************************************************************

1.	Limitations: The maximum temperature for continuous drainage application is 140°F (IAPMO/ANSI UPC 1-2015, Section 810.1).

2.	Occupied Areas:  Run PVC DWV piping in pipe chases or within walls with framing and minimum 5/8” type x gypsum wall board.

- Supply and Return Air Plenums:  Enclose PVC DWV piping with framing and gypsum wall board (as noted above) to exclude it from the plenum.  Option: Use cast iron in plenums (does not have to be enclosed with gypsum wall board).

- Mechanical Equipment Rooms:  Enclose or insulate PVC DWV piping only when adequate clearance between PVC DWV piping and heat producing equipment and piping cannot be achieved, e.g., steam boilers and piping, etc.

- Firestop Protection:  Comply with IAPMO/ANSI UPC 1-2015, Chapter 14.

- Usage:  PVC DWV piping is intended to be used in conventional DWV piping systems. Do not use for special waste systems and in radiological areas unless approved by the Mechanical ESM POC.

*************************************************************************************************************

    - Cast Iron Pipe and Fittings: CISPI 301 hubless, service weight.

      - Joints: CISPI 310, neoprene gaskets and stainless steel clamp/shield assemblies.

    - Cast Iron Pipe and Fittings: ASTM A74 service weight, bell and spigot ends.

      - Joints: Hub and spigot, CISPI HSN compression type with ASTM C564 rubber gaskets.

**************************************************************************

Specify the following (2.4.C) for pressure systems (non-gravity)

**************************************************************************

    - PVC Pipe and Fittings: ASTM D2665, polyvinyl chloride (PVC) material, Schedule 40 DWV.

- Joints: ASTM D2855, solvent weld with ASTM D2564 solvent cement and ASTM F656 purple primer

    - Ductile Iron Pipe: AWWA C151, Class 150, bell and spigot ends.

      - Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

      - Joints: Hub and spigot, AWWA C111 rubber gaskets.

  - FLOOR DRAINS

*************************************************************************************************************

Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturer’s specification.

Select floor drains with sufficient size and free area to pass anticipated flow.  Refer to manufacturer’s catalog data for selection criteria.

*************************************************************************************************************

- ASME A112.6.3, [Galvanized] Cast iron [     ] diameter [side outlet] [adjustable] drain with [light duty] [heavy duty] [vandal proof] cast iron grate and cast iron [slotted] [sediment] bucket,  double drainage flange, [reversible clamping collar,] adjustable nickel-bronze [heavy duty] strainer [with polished bronze funnel or anti- splash rim] [trap primer with ½ inch connection].

      - Manufacturer: JR Smith Model 2010-[ ]

    - Floor drain trap seal protection device: ASSE 1072, for installation in the drain outlet of all drains that require a trap primer per UPC 1007.1.

      - Manufacturer: JR Smith, Model 2692-[02, 03, 035, 04, 06]

  - FLOOR SINKS

*************************************************************************************************************

Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturer’s specification.

Specify floor sinks when the discharge of indirect waste pipes discharges into the sanitary waste system.  Refer to manufacturer’s catalog data for selection criteria.

*************************************************************************************************************

A.	ASME A112.6.7, Cast iron [galvanized] body with dome strainer [and seepage flange].

- Manufacturer: JR Smith Model 2410.

  - CLEANOUTS

***********************************************************************************************************

Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturer’s specification.

Select cleanouts to suit project.  Refer to manufacturer’s catalog data for selection criteria.

************************************************************************************************************

- Floor Cleanouts: ASME A112.36.2M, Cast iron cleanout assembly with [heavy duty] [round] [square] adjustable, scoriated, cast iron [nickel bronze] cover [with threaded spanner wrench cover] [stainless steel access cover secured with machine screw] [and no-hub outlet] [and a speed-set outlet] [with an inside caulk outlet].

      - Manufacturer: JR Smith 4020 Series

- Wall Cleanouts: Cast bronze taper thread plug with stainless steel round cover and screw.

1.	Manufacturer: JR Smith 4470 Series

EXECUTION

- PREPARATION

Ream pipe ends and remove burrs.

- Buried Piping

Provide earth cover, bedding and warning tape per Drawings and Section 31 2000, Earth Moving.

- INSTALLATION – Above Ground piping

  - Comply with Uniform Plumbing Code (IAPMO).

  - Install a floor drain trap seal protection device for all drains that require a trap primer. This device does not replace the requirement for trap primers.

  - Extend cleanouts to finish floor or wall surface.  Lubricate threaded cleanout plugs with non-hardening thread lubricant.  Ensure clearance at cleanout for snaking drainage system.

  - Encase exterior cleanouts in concrete, flush with grade.

  - Install floor cleanouts at elevation to accommodate finished floor.

  - Route piping in orderly manner and maintain gradient.  Route parallel and perpendicular to walls.

  - Install piping penetrating roofed areas to maintain integrity of roof assembly.

  - Install bell and spigot pipe with bell end upstream.

  - Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (i.e., walls, floors, etc.).

  - Test piping system with water in accordance with Section 22 0813, Testing Piping Systems, at the pressures and durations indicated below.

***************************************************************************************

Revise 22 0813 to eliminate redundant material on test criteria as necessary.

***************************************************************************************

      - Sanitary Waste and Vent Piping Within Building to Building Wall, including condensate drain line from cooling coils:

        - Test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

        - Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative method may not be used for plastic piping.

        - For modifications to existing plug the outlet of the drain piping, and fill pipe with water to the point of overflow. After 15 minutes, check piping for leaks. No loss of water from the piping for the duration of the test indicates that the system meets the requirements of the project. [If it is not possible to isolate the modifications from the remainder of the system, a visual inspection is acceptable.]

      - Sanitary Sewer Piping Beyond Building Wall (other than Force Main): Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

        - For partial system tests, test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

        - Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative testing method may not be used for plastic piping.

***************************************************************************************

Test force main piping to 1.5 times operating pressure, 25 psig minimum.

***************************************************************************************

      - Sanitary Sewer Force Main: Test with water at [    ] psig for 2 hours.

  - Label piping in accordance with Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.

  - Support piping in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

  - Install cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook," Chapter IV, "Installation of Cast Iron Soil Pipe and Fittings".

- LANL ACCEPTANCE INSPECTION

- Notify LANL Subcontract Technical Representative (STR) at least 10 working days in advance to schedule inspection of piping system.

- LANL STR to ensure all drains or buildings connected to the sanitary collection system has an approved Waste Profile Form (WPF) for discharge to the sanitary sewer for all anticipated wastewater.  Documentation shall be submitted to the LANL Utilities and Infrastructure Group wastewater representative.

END OF SECTION

************************************************

Do not delete the following information:

************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 22 1316 Rev. 5, dated October 21, 2020.