SECTION 23 2215

STEAM AND CONDENSATE HEATING PIPING and Specialties

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

NOTE: Supersedes LANL Master Specification Section 23 2213 Rev 3, Steam and Condensate Heating Piping and Section 23 2217 Rev 1, Steam and Condensate Specialties.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Building steam and condensate service piping, fittings, valves, etc. downstream of the first steam shutoff valve inside building.

Piping specialties downstream of first steam shutoff valve inside building:

Steam traps

Steam air vents

Vacuum breakers

Pressure gauges

Moisture separators

Pressure reducing valves

Safety relief valves

Condensate pressure-motive pumps

submittals

Submit the following in accordance with Project submittal procedures:

Catalog data on pipe materials, pipe fittings, valves, and piping specialties specified including electrical characteristics and connection requirements.

Product description, model, dimensions, component/service sizes, rough-in requirements, and finishes.

Manufacturer’s catalog information with valve data and rating for each service

Certification of welders.

QUALITY ASSURANCE

Comply with ASME B31.9, Building Services Piping for installation of piping systems and ASME Section IX for welding materials and procedures.

****************************************************************************************************

Comply with ASME B31.1, Power Piping for all piping upstream of the building steam PRV. Design steam piping for 150 psig and 500°F and condensate piping for 250°F. ****************************************************************************************************

Welders Certifications and Qualified Procedure Standards per Section [01 4444] [and] [01 4455].

Comply with AWS D1.1 for welding hanger and support attachments to building structure.

PRODUCTS

*************************************************************************************************************

Piping, fittings, and materials described herein are generally restricted to a maximum 150 psig working steam pressure (WSP).  For other pressure and temperature ratings, additional specification and restrictions may be required.

*************************************************************************************************************

2.1	PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - STEAM PIPING, ABOVE GRADE (150 PSIG MAXIMUM)

Pipe and Fittings: Black steel, Schedule [40] [80], ASTM A53, Type E, Electric-Resistance-Welded (ERW) Grade B, or ASTM A106, Grade B (welded or flanged joints).

Pipe and Fittings: Black steel, Schedule [40] [80], ASTM A53, Type S, Grade B, or ASTM A106, Grade B (threaded joints).

Fittings (threaded): Malleable iron, ASME B16.3, Class 150 for pressures of 15 psig or less, Class 300 for pressures above 15 psig.  NOTE: Eccentric threaded fittings are not available in malleable iron.  Use steel butt welded eccentric fittings or threaded carbon steel, ASTM A234, reducing eccentric swage nipples.

Fittings (socket weld, for pipes up to 2 inches): Forged steel, ASTM A105, Class 3000, ASME B16.11.

Fittings (butt weld, for pipes above 2 inches): Steel, ASTM A234, Grade WPB.

Joints: Threaded for pipe sizes up to 2 inches, welded or flanged for pipe sizes above 2 inches.

CONDENSATE PIPING, ABOVE GRADE (150 PSIG MAXIMUM)

Pipe and Fittings: Black steel, Schedule 80, ASTM A53, Type E, ERW Grade B, or ASTM A106, Grade B (welded or flanged joints).

Pipe and Fittings: Black steel, Schedule 80, ASTM A53, Type S, Grade B, or ASTM A106, Grade B (threaded joints).

Fittings (threaded): Malleable iron, ASME B16.3, Class 150 for pressures of 15 psig or less, Class 300 for pressures above 15 psig.  NOTE: Eccentric threaded fittings are not available in malleable iron.  Use steel butt welded eccentric fittings or threaded carbon steel, ASTM A234, reducing eccentric swage nipples.

Fittings (socket weld, for pipes up to 2 inches): Forged steel, ASTM A105, Class 3000, ASME B16.11.

Fittings (butt weld, for pipes above 2 inches): Steel ASTM A234, Grade WPB.

Joints: Threaded for pipe sizes up to 2 inches, welded or flanged for pipe sizes above 2 inches

UNIONS and FLANGES

Unions for pipe sizes up to 2 inches:  ASME B16.39, malleable iron, threaded, Class 150 for pressures of 15 psig or less, Class 300 for pressures above 15 psig.

Flanges for pipe sizes above 2 inches:  Forged steel, ASTM A105, Class 150, weld neck, raised face, dimensions per ASME B16.5.

GASKET MATERIAL

Pressures above 20 psig: Flexitallic, non-asbestos, CG style

Pressures 20 psig or less:  Sheet gasket, branded material, 1/16 inch thick, non-asbestos, suitable for steam service up to 500°F.

BOLTS, STUDS AND NUTS

Bolts/Studs: Alloy steel, ASTM A193, Grade B7.

Nuts: Alloy steel, ASTM A194, Grade 2H.

STEEL GATE VALVES (Up to 2 inches)

Manufacturer: Vogt, Series 12111.

Forged steel, ASTM A105, Class 800, steam service, 500°F at 1595 psig, rising stem, threaded ends, hard faced seat and disc.

STEEL GATE VALVES (above 2 inches)

Manufacturer: Powell, Figure 1503N.

Cast carbon steel, ASTM A216, Grade WCB, Class 150, steam service, 500°F at 170 psig, rising stem, flanged or welded ends to suit piping, hard-faced seat and disc.  Furnish chain-wheel operators for valves 6 inches and larger mounted over 7 feet above the floor.

STEEL GLOBE VALVES (Up to 2 inches)

Manufacturer: Vogt, Series 12141.

Forged steel, ASTM A105, Class 800, steam service, 500°F at 1595 psig, rising stem, threaded ends, hard-faced seat and disc.

STEEL GLOBE VALVES (above 2 inches)

Manufacturer: Powell, Figure 1531.

Cast carbon steel, ASTM A216, Grade WCB, Class 150, steam service, 500°F at 170 psig, rising stem, flanged or welded ends to suit piping, hard-faced seat and disc.  Furnish chain-wheel operators for valves 6 inches and larger mounted over 7 feet above the floor.

BRONZE GATE VALVES (Up to 2 inches)

Manufacturer: Nibco, T-111 Rising Stem.

Bronze, ASTM B62, Class 125, steam service, 350°F at 125 psig, screw-in bonnet, rising stem, solid wedge, threaded ends.

BRONZE GLOBE VALVES (Up to 2 inches)

Manufacturer: Nibco, T211.

Bronze, ASTM B62, Class 125, steam service, 350°F at 125 psig, screw-in bonnet, integral seat, renewable seat and disc, threaded ends.

BRONZE CHECK VALVES (Up to 2 inches)

Manufacturer: Nibco, T413.

Bronze, ASTM B62, Class 125, steam service, 350°F at 125 psig, horizontal swing, renewable seat and disc, threaded ends.

STEEL CHECK VALVES (Up to 2 inches)

Manufacturer: Vogt, No.  S74.

Forged steel, ASTM A105, steam service, 350°F at 125 psig, horizontal swing.

STRAINERS

Pressures 15 psig or less: “Y” Type, rated for 125 psig steam, service to 350°F, 20 mesh stainless steel screens, bronze body, ASTM B62 with blowoff gate valve and plug.

Pressures above 15 psig: “Y” Type, rated for 250 psig steam, service to 400°F, 20 mesh stainless steel screens, steel body, ASTM A216 with blowoff gate valve and plug.

FLOAT AND THERMOSTATIC TRAP

    - Manufacturer: Watson McDaniel, Series FT.

    - Trap: ASTM A216, Carbon Steel body, with stainless steel interior parts, maximum operating pressure 125 psig at 350°F.

      - Capacity: [      ] lbs/hr condensate at [      ] psig inlet pressure.

      - Size: [       ] inch.  [Minimum size 3/4 inch.]

THERMOSTATIC TRAP

Manufacturer: Watson McDaniel, Series WT 3000.

B.	Trap: Stainless steel construction, maximum operating pressure 300 psig at 750°F.

Capacity: [      ] lbs/hr condensate at [      ] psig inlet pressure.

Size: [       ] inch.  [Minimum size 3/4 inch.]

STEAM AIR VENTS

Manufacturer: Watson McDaniel, AV2000.

Air Vent: Stainless steel body with stainless steel interior parts, bellows operated, suitable for steam service to 150 psig.

Size: 1/2 [     ] inch NPT inlet and outlet.

VACUUM BREAKER

Manufacturer: DFT Inc., No. BSSV.

Vacuum Breaker: Stainless steel body with stainless steel interior parts, suitable for steam service to 150 psig.

Size: 1 inch MNPT.

PRESSURE GAUGE

*************************************************************************************************************

Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the expected normal pressure is recommended, with maximum working pressure not exceeding 75 percent of the range. If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.

*************************************************************************************************************

Manufacturer: Ashcroft, Type 1009

Gauge: ASME B40.100, Accuracy Grade IA, minimum 2 1/2 inch dial, 1/4 inch NPT brass bottom connection, phosphor bronze bourdon tube, maximum plus or minus 1 percent accuracy full scale, stainless steel case, with Schedule 40 steel siphon tube.

Range: [     ] psi or [See Drawings].

MOISTURE SEPARATOR

*************************************************************************************************************

Size moisture separator inlet to match building supply steam piping.

*************************************************************************************************************

Manufacturer: Watson McDaniel, Series WDS.

Moisture Separator: Steam service, cast iron construction, maximum operating pressure 125 psig at 350°F.

Size: [     ] inch [NPT or 125 lb. flanged connections].

PRESSURE REDUCING VALVE

Manufacturer: Watson McDaniel, Type HDP.

Pressure Reducing Valve: Steam service, cast iron construction, self operating, external pilot, single seated, normally-closed, maximum inlet pressure 250 psig at 450°F.

Capacity: [      ] lbs/hr at [     ] psig inlet and [     ] psig outlet pressures.

Size: [     ] inch - threaded up to 2 inches, flanged over 2 inches.

Valve Spring: [3 to 25 psig, yellow] [20 to 100 psig, blue] [80-200 psig, red].

SAFETY RELIEF VALVES

Manufacturer: Kunkle, [No. 6010 (threaded ends, bronze body)] [No. 252 (flanged ends, iron body).

Valve: Steam service, ASME approved, N.B. certified, lever handle, factory tested and adjusted, maximum pressure setting 250 psig at 406°F.

Capacity: [       ] lbs/hr at 10 percent accumulation.

Orifice Size: [      ] sq. inch.

Size: [      ] inch - threaded up to 2 inches, flanged over 2 inches.

Accessories: Drip pan elbow shipped loose, same size as relief valve outlet.

CONDENSATE PRESSURE MOTIVE PUMPS

*************************************************************************************************************

Complete skid-mounted unit, including receiver tanks, pump(s), check valves, etc., all fully piped are available.  It is recommended that a receiver tank be specified when above ground steam/condensate distribution lines feed the building.  Consult with the motive pump distributor for selection guidance.  Specify ASME coded receiver tanks.

*************************************************************************************************************

Manufacturer: Watson McDaniel, [Series PMP C, (Ductile Iron Body)] or  [         ].

EXECUTION

- PREPARATION

Ream pipe and tube ends. Remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Prepare piping connections to equipment with flanges or unions.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, protect open ends with temporary plugs or caps.

After completion, fill, clean, and chemically treat systems.  Refer to Section 23 2500, HVAC Water Treatment.

  - INSTALLATION

Install steam and condensate service piping, fittings, valves, and specialties in accordance with manufacturers’ instructions, design drawings and this specification.

Route piping in orderly manner, plumb and parallel to building structure, and maintain gradient.

Install piping to conserve building space and not interfere with use of space.

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (i.e., walls, floors, etc).

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide clearance for installation of insulation and access to valves and fittings.

Provide safe access or remote operators where valves and fittings are not exposed or installed over 7 feet in height above finished floor.

Slope steam and condensate piping 1 inch in 40 feet (0.25 percent) in direction of flow.

Install valves with stems upright or horizontal, not inverted.

Use threaded bronze valves and strainers in piping up to 2 inches, for design pressures 15 psig or less.

Use threaded steel valves and strainers in piping up to 2 inches, for design pressures above 15 psig.

Use welded or flanged steel valves and strainers in piping above 2 inches.

Provide eccentric reducers, flat on bottom, in horizontal runs of steam and condensate piping.

Provide globe valves for throttling, bypass, or manual flow control services.

Provide gate valves inside building to isolate equipment or part of piping system.

Connect steam and condensate branch lines into top of main or at a 45-degree angle from top of main.

Provide condensate piping no smaller than trap inlet.

Label Piping in accordance with Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.

Pressure test piping in accordance with Section 22 0813, Testing Piping Systems.

Support piping in accordance with Section 22 0529, Hangers and Support for Plumbing Piping and Equipment.

Insulate piping in accordance with Section 22 0713, Plumbing and HVAC Insulation.

Sleeve pipe penetration and caulk in accordance with Section 22 0548, Vibration and Seismic Control for Plumbing Piping and Equipment.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 2215 Rev. 0, dated September 23, 2009.