SECTION 23 7413

Packaged, Outdoor, Central-Station Air-Handling Units

*********************************************************************************************************************

LANL MASTER SPECIFICATION

When editing to suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  To seek a variance from applicable requirements, contact the Engineering Standards Manual (ESM) Mechanical POC.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 01, General Requirements.

Delete information within “stars” during editing.

Specification developed for ML-4 projects.  For ML-1, 2, and 3, additional requirements and independent reviews may be required; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*********************************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Packaged rooftop air conditioning units

SUBMITTALS

*********************************************************************************************************************

Additional submittals may be required if the project is seeking LEED certification. Consult with the project’s LEED Accredited Professional.

*********************************************************************************************************************

Section 01 1330, Submittal Procedures.

Product Data: Submit data indicating:

Cooling and heating capacities.

Dimensions.

Weights.

Rough-in connections and connection requirements.

Duct connections.

Electrical requirements with electrical characteristics and connection requirements.

Controls.

Accessories.

Test Reports: Submit results of factory test at [time of unit shipment] [________].

Manufacturer's Installation Instructions: Submit assembly, support details, connection requirements, and include start-up instructions.

Manufacturer's Certificate: Certify products meet or exceed the requirements of this specification.

Manufacturer’s Field Reports: Submit start-up report [for each unit].

CLOSEOUT SUBMITTALS

Refer to Section 01 7700, Closeout Procedures.

Project Record Documents: Record actual locations of controls installed remotely from units.

Operation and Maintenance Data: Submit manufacturer's descriptive literature, operating instructions, installation instructions, and maintenance and repair data.

QUALITY ASSURANCE

Cooling Capacity: Rate in accordance with ARI 210/240.

*********************************************************************************************************************

Coordinate any special acoustical requirements with the project Functional and Operational Requirements

*********************************************************************************************************************

Sound Rating: Measure in accordance with ARI 270.

Energy Efficiency: Comply with the requirements of ASHRAE/IESNA 90.1-2004.

Electrical: Meet the requirements of NFPA 70, Article 100.

Insulation and adhesives: Meet requirements of NFPA 90A.

QUALIFICATIONS

Manufacturer: Company specializing in manufacturing products specified in this section with minimum [three] [________] years [documented] experience.

Installer: Company specializing in performing Work of this section with minimum [three] [________] years [documented] experience [approved by manufacturer].

DELIVERY, STORAGE, AND HANDLING

Section 01 6000, Product Requirements: Product storage and handling requirements.

WARRANTY

Furnish [five] [________] year manufacturers warranty for compressors.

Furnish [five] [________] year manufacturers warranty for heat exchangers.

EXTRA MATERIALS

Furnish [one set] [________] of [filters] [fan belts] for each unit.

PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

ROOFTOP AIR CONDITIONING UNITS, UP TO 25 TONS

Manufacturers:

[Carrier Corp.] Model [________].

[The Trane Company] Model [________].

[York International] Model [________].

*********************************************************************************************************************

Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturers specified above.

*********************************************************************************************************************

Product Description: Self-contained, packaged, factory assembled and wired, consisting of [roof curb,] cabinet, supply fan, evaporator coil, compressor, refrigeration circuit, condenser, [gas-fired heating section,] [electric heating coil,] [hot water heating coil,] air filters, [outside air section], [exhaust-return section], controls, and accessories.

Configuration: [Downflow air delivery.] [Horizontal air delivery.] [As indicated on Drawings].

Roof Mounting Curb: [14] [24] [________] inch high, galvanized steel, channel frame with gaskets, nailer strips. Full perimeter type for mounting under entire unit.

Cabinet:

Designed for outdoor installation with weatherproof construction.

Panels: Constructed of [steel] [galvanized steel] with baked enamel finish. Furnish access doors or removable access panels.

Insulation: Factory applied to exposed vertical and horizontal panels. [1/2] [one] [2] inch thick [neoprene coated] [aluminum foil faced] glass fiber with edges protected from erosion.

Supply Fan: Forward curved centrifugal type, resiliently mounted with [direct drive] [V-belt drive,] [adjustable variable pitch motor pulley] [high efficiency motor] [premium efficiency motor]. Motor permanently lubricated with built-in thermal overload protection.

Evaporator Coil: Constructed of copper tubes expanded onto aluminum fins. Galvanized drain pan with piping connection. Factory leak tested under water.

*********************************************************************************************************************

Choices in the following paragraphs vary between manufacturers and with unit capacity. Select appropriate items available with unit size.

When project conditions warrant include type of compressor in the following paragraph. This may make specification proprietary as type of compressor differs between manufacturers. Generally, compressor types are scroll although some manufacturers use reciprocating compressors.

Units with multiple compressors generally start at 7-1/2 tons.

*********************************************************************************************************************

Compressor: Hermetically sealed, resiliently mounted with positive lubrication, and internal motor overload protection. Furnish [internal vibration isolators,] [external vibration isolators,] [short cycle protection].

Refrigeration circuit: [Furnish] [Furnish the following for each circuit] [fixed orifice control] [expansion device,] [thermal expansion valve,] [filter-drier,] [suction, discharge, and liquid line service valves with gauge ports,] [high and low pressure safety controls,] [and] [________]. Dehydrate and factory charge [each circuit] with oil and refrigerant.

Condenser:

Coil: Copper tube [aluminum] [copper] fin coil assembly [with subcooling rows] [and coil guard]. Factory leak tested under water.

Condenser Fan: Direct drive propeller fans statically and dynamically balanced. Wired to operate with compressor. Motor permanently lubricated with built-in thermal overload protection. [Furnish high efficiency fan motors.]

Furnish factory installed hail protection coil guard.

*********************************************************************************************************************All Packaged Rooftop Air Conditioning Units shall include at least one of the following heating methods.

*********************************************************************************************************************

Gas-Fired Heating Section:

Fuel: Natural gas.

Heat Exchangers: [Aluminized] [Stainless] steel, welded construction.

Gas Burner: [Atmospheric] [Induced draft] [Forced draft] type burner with adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and [automatic 100 percent shut-off pilot]. Require unit fan operation before allowing gas valve to open.

****** [OR] ******

Electric Heating Coil:

******************************************************************************************************************

Specify single source power connection for units supplied with electric heat. Electric heating coil is only allowed when natural gas and/or steam are not available, as determined by the Mechanical POC.

******************************************************************************************************************

[Finned tube heating elements] [or] [Helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings] easily accessible with automatic reset thermal cut-out, built-in magnetic contactors, galvanized steel frame, [control circuit transformer and fuse,] [manual reset thermal cut-out,] [airflow proving device,] [pilot duty toggle switch,] load fuses. [Single source power connection.] [Number of stages as indicated on Drawings.] [Mercury contactors are not acceptable]

Controls: Start supply fan before electric elements are energized and continue operating until air temperature reaches minimum setting, with switch for continuous fan operation.

****** [OR] ******

Hot Water Heating Coil:

[Factory mounted] Field installed].

Coil: Constructed of copper tubes expanded into aluminum fins. Factory leak tested under water.

Furnish factory installed piping package with [modulating] [two-way] [three-way] control valve.

Air Filters: [1] [2] [4] inch [thick glass fiber disposable media in metal frames.] [25 to 30 percent efficiency based on ASHRAE 52.1.]

Mixed Air Casing:

*********************************************************************************************************************

Based on unit size, choice may not be available for damper leakage. Generally, leakage can be specified in units 15 tons and larger.

*********************************************************************************************************************

Damper Leakage: Furnish dampers with maximum leakage rate of [3] [5] [________] percent at [1] [2] [________] inch water column pressure differential.

*********************************************************************************************************************

Manual outside air damper is only for use on units 5 tons and under without water coils.

*********************************************************************************************************************

Outside Air Damper: Manual, for fixed outside air quantity. [Furnish rain hood with screen.]

****** [OR] ******

Outside Air Damper: Remote controlled with damper operator and remote rheostat for adjusting outside air quantity.

****** [OR] ******

Outside Air Damper: Automatic, two position [spring return]. Interlocked to open when supply fan starts. [Outside air damper normally closed and return air damper normally open.] Furnish rain hood with screen.

*********************************************************************************************************************

Powered exhaust fan is generally available in units above 6 tons

*********************************************************************************************************************

****** [OR] ******

*********************************************************************************************************************

Economizer is required on units over 5 tons.

*********************************************************************************************************************

Economizer: [Factory installed] fully modulating motorized outside air and return air dampers controlled by dry bulb temperature controller [with minimum position setting.] [Outside air damper normally closed and return air damper normally open.] [Furnish barometric relief damper capable of closing by gravity.] [Furnish barometric relief damper with powered exhaust.] [Furnish rain hood with screen.]

*********************************************************************************************************************

Select applicable controls and controls combination. This paragraph deals with standard, factory available controls. More sophisticated controls or those for different types of units may be better specified in control sections and described in Sequences of Operation.

Control features will vary based on size of unit or application to system (i.e. constant volume single zone or changeover bypass).

*********************************************************************************************************************

Controls:

*********************************************************************************************************************

Low ambient control is only used with units less than 5 tons without economizers, based on project requirements.

*********************************************************************************************************************

Furnish control to provide low ambient cooling to [0] [-10] degrees F.

Furnish low limit thermostat in supply air to close outside air damper and stop supply fan.

Furnish terminal strip on unit for connection of operating controls to remote panel.

Thermostat: Furnish space thermostat with [1] [2] stage heating and [1] [2] stage cooling with [manual] [automatic] changeover. Furnish system selector switch [heat-off-cool] [off-heat-auto-cool] [and fan control switch auto-on].

****** [OR] ******

Thermostat: [7 day] programmable electronic space thermostat with [1] [2] stage heating and [1] [2] stage cooling with [manual] [automatic] changeover and heating setback and cooling setup capability. Furnish system selector switch [heat-off-cool] [off-heat-auto-cool] [and fan control switch, auto-on].

Furnish interface to Building Automation and Control System specified in Section 25 5000, Integrated Automated Facility Controls.

Microprocessor Based Controls:

[Factory mounted] [Field installed] with the following features:

Monitor each mode of operation.

Evaporator fan status.

Filter status.

Indoor air quality.

Supply air temperature.

Outdoor air temperature.

Diagnostics for [thermostat] [temperature sensor] commands for staged heating, staged cooling, fan operation, and economizer operation.

Zone space temperature sensor to interface with microprocessor controls with [Manual] [Automatic] programmable with night setback.

Accessories:

Roof Curb Adaptor Package: Furnish duct support hardware to adapt unit to existing roof curb.

Disconnect Switch: Factory mounted, non-fused type, interlocked with access door, accessible from outside unit, with power lockout capability.

[____________________].

Capacity:

See equipment schedule on the drawings.

ROOFTOP AIR CONDITIONING UNITS, 25 TONS TO 60 TONS

Manufacturers:

[Carrier Corp.] Model [________].

[The Trane Company] Model [________].

[York International] Model [________].

[____________________] Model [________].

*********************************************************************************************************************

Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturers specified above.

*********************************************************************************************************************

Product Description: Self-contained, packaged, factory assembled and wired, consisting of [roof curb,] cabinet, supply fan, [variable frequency drive,] evaporator coil, compressor, refrigeration circuit, condenser, [gas-fired heating section,] [electric heating coil,] [hot water heating coil,] [steam heating coil,] air filters, [outdoor air section,] [exhaust-return section,] [return fan,] and controls.

Configuration: [Downflow air delivery.] [Horizontal air delivery.] [As indicated on Drawings].

Roof Mounting Curb: [14] [24] [________] inch high, galvanized steel, channel frame with gaskets, nailer strips. [Full perimeter curb under entire unit.] [Full perimeter curb under unit with separate support curb for condensing section.]

Cabinet:

Designed for outdoor installation with weatherproof construction.

Panels: [Steel] [Galvanized steel] with baked enamel finish. Furnish [removable access panels with handles] [hinged access doors with handles and rubber gaskets at edges].

Insulation: Factory applied to exposed vertical panels, horizontal panels, and access [panels] [doors]. [1/2] [1] [2] inch thick, [0.75] [1.5] pound per cubic foot density, [neoprene coated] [aluminum foil faced] glass fiber with edges protected from erosion.

*********************************************************************************************************************

Interior lined casing may not be available from all manufacturers. When available, generally it will be in 30 ton and larger capacity units. Coordinate availability with selected manufacturer.

*********************************************************************************************************************

Interior Surfaces: Sheet metal lined creating double wall construction.

Supply Fan:

Fan: [Forward curved centrifugal type] [Backward inclined airfoil type], statically and dynamically balanced, resiliently mounted.

Fan Drive: V-Belt type, Cast iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed. Furnish solid shaft construction. Select Variable and adjustable pitch motor sheave to obtain required rpm with sheaves set at mid-position as recommended by manufacturer.

Drive Rating: Minimum [1.5] [________] times nameplate rating of motor.

Fan Sheave: [Fixed.] [Adjustable.]

Motor Sheave: [Fixed.] [Adjustable.]

Fan motor: Three phase, NEMA design B, continuously rated at 40 degrees C, [open drip-proof] [totally enclosed fan cooled] [high efficiency, open drip-proof] [premium efficiency open drip-proof] NEMA T frame, with permanently lubricated bearings and integral overload protection.

Fan Assembly Mounting: Furnish spring-type vibration isolators.

Evaporator Coil:

Constructed of seamless copper tubes mechanically expanded into aluminum fins. Factory leak tested under water.

Galvanized drain pan and piping connection.

Furnish for multiple circuited units [intertwined] [alternate] row circuiting.

*********************************************************************************************************************

Choices in the following paragraphs vary between manufacturers and with unit capacity. Select appropriate items available with unit size.

When project conditions warrant include type of compressor in the following paragraph. This may make specification proprietary as type of compressor differs between manufacturers. Generally, compressor types are scroll or reciprocating.

Compressor type whether hermetic or semi-hermetic varies with manufacturer.

*********************************************************************************************************************

Compressors:

[Hermetically sealed] [Semi-hermetic], resiliently mounted with positive lubrication, and internal motor overload protection.

Furnish each compressor with independent refrigeration circuit.

Furnish [[internal] [external] vibration isolators.

Furnish short cycle protection.

Refrigeration circuit:

Dehydrate and factory charge [each circuit] with oil and refrigerant.

Furnish the following for each circuit:

Thermostatic expansion device.

Filter-drier.

Suction, discharge, and liquid line service valves with gauge ports.

Sight glass.

High and low pressure safety controls.

[________].

*********************************************************************************************************************

Select desired method of capacity control. Not all manufacturers offer this option.

Hot gas bypass is usually used with variable air volume systems and other applications to control capacity at minimum cooling loads.

*********************************************************************************************************************

Furnish capacity control by [hot gas bypass.] [cycling compressors.] [cylinder unloading.] [cycling multi-speed compressors.]

Condenser:

Constructed of copper tubing mechanically bonded to [aluminum] [copper] fins [with sub-cooling rows]. Factory leak tested under water.

Direct drive propeller fans statically and dynamically balanced. Wired to operate with compressor. Motor permanently lubricated with built-in thermal overload protection. [Furnish high efficiency fan motors.]

Furnish factory installed hail protection coil guard.

*********************************************************************************************************************All Packaged Rooftop Air Conditioning Units shall include at least one of the following heating methods.

*********************************************************************************************************************

Gas-Fired Heating Section:

Fuel: Natural gas.

Heat Exchanger: [Aluminized] [Stainless] steel, of welded construction.

Gas Burner: [Induced draft] [____________________] type burner with adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and [automatic 100 percent shut-off pilot].

****** [OR] ******

Electric Heating Coil:

******************************************************************************************************************

Specify single source power connection for units supplied with electric heat. Electric heating coil is only allowed when natural gas and/or steam are not available, as determined by the Mechanical POC.

******************************************************************************************************************

[Finned tube heating elements] [or] [Helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings] easily accessible with automatic reset thermal cut-out, built-in magnetic contactors, galvanized steel frame, [control circuit transformer and fuse,] [manual reset thermal cut-out,] [airflow proving device,] [toggle switch (pilot duty),] load fuses. [Single source power connection.] [Number of stages as indicated on Drawings.] [Mercury contactors are not acceptable]

Controls: Start supply fan before electric elements are energized and continue operating until air temperature reaches minimum setting, with switch for continuous fan operation.

****** [OR] ******

Hot Water Heating Coil:

[Factory mounted] Field installed].

Coil: Constructed of seamless copper tubes mechanically expanded into aluminum fins. Factory leak tested under water.

Furnish factory installed piping package with [modulating] [two-way] [three-way] control valve.

Freezestat: Factory mounted on discharge side of coil.

****** [OR] ******

Steam Heating Coil:

Tube-in-tube non-freeze type. Constructed of seamless copper tubes mechanically expanded into aluminum fins. Factory leak tested under water.

Furnish [modulating] [two-way] control valve.

Freezestat: Factory mounted on discharge side of coil.

Air Filters: [1] [2] [4] inch [thick glass fiber disposable media in metal frames.] [25 to 30 percent efficiency based on ASHRAE 52.1.]

****** [OR] ******

Air Filters: Cartridge type, 12 inch deep, [60 to 65] [90 to 95] percent efficient, based on ASHRAE 52.1. Furnish with 2 inch thick pre-filters.

****** [OR] ******

Air Filters: Bag filters with 90 percent average efficiency based on ASHRAE 52.1. Furnish 2 inch thick pre-filters.

Outdoor Air Section:

Dampers: Furnish with leakage rate not to exceed [0.5] [1] [2.5] percent of nominal airflow based on [1] [1.5] inch water column static pressure.

Outside Air Damper: None. 100 percent return air.

****** [OR] ******

Economizer: [Factory installed] fully modulating from 0 to 100 percent outside air. Motorized outside air and return air dampers controlled by dry bulb controller [with minimum position setting.] [Outside air damper normally closed and return air damper normally open.]

****** [OR] ******

Economizer: Furnish [fully integrated] factory installed fully modulating from 0 to 100 percent outside air economizer. Economizer operation through microprocessor based primary temperature controls automatically modulate dampers to maintain space temperature conditions.

Furnish economizer with dry bulb control.

Furnish adjustable minimum position control located remotely in space.

Furnish spring return motor for outside air damper closure during unit shutdown or power interruption.

Exhaust and Return Section:

No relief air capability.

****** [OR] ******

Barometric relief gravity type dampers to operate in conjunction with economizer. [Furnish barometric relief damper capable of closing by gravity.] [Furnish rain hood with screen.]

****** [OR] ******

Non-modulating exhaust fans: Forward curved centrifugal type, [direct drive] [belt drive], statically and dynamically balanced, [high efficiency motor]. Motor permanently lubricated with built-in thermal overload protection. Furnish barometric dampers at fan outlet to prevent backdraft. Operation of exhaust fans on or off based on economizer outdoor air damper position. [On-off setpoint selectable through remote potentiometer located in return air section.]

Modulating exhaust fans: Forward curved centrifugal type, [direct drive] [belt drive], statically and dynamically balanced, [high efficiency motor]. Motor permanently lubricated with built-in thermal overload protection. Furnish barometric dampers at fan outlet to prevent backdraft. Fans operated with volume control device based on field adjustable interior space pressure setpoint.

Return Fan:

Fan: [Forward curved centrifugal type] [Backward inclined airfoil type], statically and dynamically balanced, resiliently mounted.

Fan Drive: V-Belt type, Cast iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed. Furnish solid shaft construction. Select Variable and adjustable pitch motor sheave to obtain required rpm with sheaves set at mid-position as recommended by manufacturer.

Drive Rating: Minimum [1.5] [________] times nameplate rating of motor.

Fan Sheave: [Fixed.] [Adjustable.]

Motor Sheave: [Fixed.] [Adjustable.]

Fan motor: Three phase, NEMA design B, continuously rated at 40 degrees C, [open drip-proof] [totally enclosed fan cooled] [high efficiency, open drip-proof] [premium open drip-proof efficiency] NEMA T frame, with permanently lubricated bearings and integral overload protection.

Fan Assembly Mounting: Furnish spring-type vibration isolators.

Return Fan Modulation:

Controlled in conjunction with supply fan.

****** [OR] ******

*********************************************************************************************************************

Supply and return fan can be controlled by either individual or single variable frequency drive. Edit the following.

*********************************************************************************************************************

Variable frequency drive: [Controlled from same drive as supply fan.] [Individual drive for return fan.]

Controls: Furnish space thermostat with [1] [2] [________] stage heating and [1] [2] [________] stage cooling with [manual] [automatic] changeover. Furnish system selector switch [heat-off-cool] [off-heat-auto-cool] [and fan control switch, auto-on].

****** [OR] ******

Controls: Furnish [7 day] [________] programmable electronic space thermostat with [4] [________] time periods per day, [1] [2] stage heating, [1] [2] stage cooling, [manual] [automatic] changeover, heating setback, cooling setup, override capability, liquid crystal display, memory storage without batteries, security levels feature, and setpoint limiting. Furnish system selector switch [heat-off-cool] [off-heat-auto-cool] [and fan control switch, auto-on].

****** [OR] ******

*********************************************************************************************************************

Use one of the following two paragraphs when controls are specified in other sections.

*********************************************************************************************************************

Controls: Furnish interface to Building Automation and Control System specified in Section 25 5000, Integrated Automated Facility Controls.

****** [OR] ******

Controls: Microprocessor based controls, factory mounted with the following features:

Constant Volume Controls: To operate rooftop from space temperature sensor, including economizer control.

Furnish space temperature sensor [with setpoint adjustment] for control of unit equipped with override button for timed override of [1] [2] [3] [4] hours.

****** [OR] ******

Furnish space temperature sensor [with setpoint adjustment] for control of unit equipped with override button for timed override of [1] [2] [3] [4] hours. Furnish with space temperature offset of plus or minus 5°F.

****** [OR] ******

Variable Air Volume Controls: To operate VAV rooftop from supply air temperature including supply air sensor, and [inlet guide vanes] [variable frequency drive]. Microprocessor coordinates economizer control and stages of cooling with supply air temperature reset capability based upon outdoor air temperature.

*********************************************************************************************************************

The following is generic list of control functions. Edit or expand list based on project conditions. Coordinate availability with selected manufacturer. Place this information on the drawings.

Control Functions: Furnish the following:

Unit scheduling.

Occupied-unoccupied mode.

Start-up and coast-down modes.

Nighttime free-cool purge mode.

Demand limiting.

Night setback.

Timed override.

Alarm shutdown.

Discharge air set point adjustment.

Static pressure setpoint adjustment.

The following is generic list of setpoints and alarms. Edit or expand list based on project conditions. Coordinate availability with selected manufacturer. Place this information on the drawings.

Furnish the following setpoints and diagnostic functions accessible in unit control panel:

        - Unit operating mode.

Unit failure status.

Supply fan start-stop.

Supply fan status.

Supply fan inlet guide vane position.

Supply fan variable frequency drive percent.

Return fan start-stop.

Return fan status.

Return fan inlet guide vane position.

Return fan variable frequency drive percent.

Exhaust fan start-stop.

Exhaust fan status.

Exhaust fan variable frequency drive percent.

Supply air temperature.

Supply air temperature high-low limit with alarm.

Return air temperature.

Return air temperature high-low limit with alarm.

Mixed air temperature.

Mixed air temperature high-low limit with alarm.

Duct static pressure.

Duct static pressure high-low limit with alarm.

Cooling control.

Cooling status - all stages.

Heating control.

Heating status.

Number of stages activated.

Damper control.

Economizer status.

Requested minimum position.

Damper positions.

Space temperature.

Space temperature high-low limit with alarm.

Filter status.

Smoke detector status.

Outside air temperature.

Outside relative humidity.

The following are specialty control functions furnished by some manufacturers. Coordinate availability with selected manufacturer. Place this information on the drawings.

Ventilation Override: Factory installed. Binary input from independent fire or life safety panel causes unit to override standard operation and assumes one of two factory preset ventilation sequences - purge or pressurization.

Indoor Air Quality Control: Furnish demand ventilation control through economizer with carbon dioxide sensor. Sensor adjustable [duct mounted] [wall mounted] [wall mounted with display of parts per million].

*********************************************************************************************************************

Accessories:

Roof Curb Adaptor Package: Furnish duct support hardware to adapt unit to existing roof curb.

Disconnect Switch: Factory mounted, non-fused type, interlocked with access door, accessible from outside unit, with power lockout capability.

[____________________].

Capacity:

See equipment schedule on the drawings

EXECUTION

INSTALLATION

Roof Curb:

Assemble roof curb.

Install roof curb level.

Install units on roof curb providing watertight enclosure to protect ductwork and utility services.

Install gasket material between unit base and roof curb.

Install units on vibration isolators. Refer to Section ______.

Connect units to supply and return ductwork with flexible connections. Refer to Section 23 3100, HVAC Ducts and Casings.

Install condensate piping with trap and route from drain pan to [splash block on roof] [nearest roof drain.] [condensate drainage system.] [________.] Refer to Section 23 2113, Hydronic Piping.

Install components furnished loose for field mounting.

Install electrical devices furnished loose for field mounting.

Install control wiring between unit and field installed accessories.

INSTALLATION - NATURAL GAS HEATING SECTION

Connect natural gas piping in accordance with NFPA 54.

Connect natural gas piping to unit, full size of unit gas train inlet. Arrange piping with clearances for burner service.

Install the following piping accessories on natural gas piping connections. Refer to Section 23 1123, Facility Natural Gas Piping.

Strainer.

Pressure gage.

Shutoff valve.

Pressure reducing valve.

Install natural gas piping accessories [above roof] [within unit casing] [below roof].

INSTALLATION - HOT WATER HEATING COIL

Make connections to coils with unions or flanges.

Connect water supply to leaving airside of coil (counter flow arrangement).

Locate water supply at bottom of supply header and return water connection at top.

Install water coils to allow draining and install drain connection at low points.

Install valves and piping specialties in accordance with details as indicated on Drawings.

Install [manual] [automatic] air vents at high points complete with shutoff valve. Refer to Section 23 2113, Hydronic Piping.

Install hot water piping accessories [within unit casing] [below roof].

MANUFACTURER'S FIELD SERVICES

Furnish initial start-up and shutdown during first year of operation, including routine servicing and checkout.

Furnish service and maintenance of equipment for [one] [________] year from Date of Substantial Completion. Include maintenance items as shown in manufacturer's operating and maintenance data, including filter replacements, fan belt replacement, and controls checkout and adjustments.

Furnish 24-hour emergency service on breakdowns and malfunctions for this maintenance period.

CLEANING

Vacuum clean coils and inside of unit cabinet.

Install temporary filters during construction period. Replace with permanent filters at Substantial Completion.

DEMONSTRATION

Demonstrate unit operation and maintenance.

Furnish services of manufacturer's technical representative for [one] [________] [8] [________] hour day to instruct LANL personnel in operation and maintenance of units. Schedule training with LANL, provide at least 7 days notice to the LANL Sub-Contractor Technical Representative (STR) Inspector of training date.

SCHEDULES

See the equipment schedule on the drawings.

*********************************************************************************************************************At a minimum, provide the following data in the equipment schedule on the drawings

ROOFTOP UNITS

Drawing Code			HVA-1		HVA-2		HVA-3

Location

Manufacturer

Model

Unit voltage

Minimum Circuit Ampacity

Maximum Overcurrent Protection

Altitude

Unit Sound Rating

Supply Fan

Supply airflow

Outside airflow

External Static Pressure

Fan Motor

Cooling

Total Cooling Capacity

Sensible Cooling Capacity

Entering air temperature (dry bulb)

Entering air temperature (wet bulb)

Leaving air temperature (dry bulb)

Leaving air temperature (wet bulb)

Condenser ambient air temperature

Energy Efficiency Ratio

Number of [compressors] [refrigeration circuits]

Capacity steps: [________].

Gas Heating

Input

Output

Stages

Entering Air Temperature

Leaving Air Temperature

Electric Heating

Electric resistance heating capacity

Capacity steps

Entering Air Temperature

Leaving Air Temperature

Hot Water Heating

Capacity

Water flow

Entering air temperature

Entering water temperature

Leaving water temperature

Entering Air Temperature

Leaving Air Temperature

Coil pressure drop

Nominal Capacity

*********************************************************************************************************************

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 7413 Rev. 0, dated 
October 24, 2007.