SECTION 23 8123

COMPUTER-ROOM AIR-CONDITIONERS

*******************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.   In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This Specification is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*****************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Floor-mounted computer-room air conditioners, 6 tons and larger.

Floor-mounted computer-room air conditioners, 5 tons and smaller.

Ceiling-mounted computer-room air conditioners.

PERFORMANCE REQUIREMENTS

- Supplier-provided control systems, including instruments, signal transmissions, panels, cabinets, and other control and instrumentation requirements shall be coordinated with the Control and Instrumentation Subcontractor.  Some equipment controls are specified in other portions of the subcontract documents.  As part of the work of this section, coordinate with these other suppliers and trades to provide a complete and working equipment controls.

- It is the responsibility of the bidder to read and conform to all articles of this specification, review all subcontract drawings of all divisions, and coordinate with all equipment suppliers of material specified under other sections of the specifications.

- HVAC fans and associated motors shall perform satisfactorily in the following service conditions:

      - Elevation:  7500 feet above sea level.

      - Maximum ambient temperature:  104 degrees F.

      - Minimum ambient temperature:  Minus 20 degrees F.

      - 24-hour average temperature:  not exceeding 86 degrees F.

        - Seismic Protection and Performance:  The seismic protection and performance of HVAC fans shall be in accordance with Section 22 0548, Vibration and Seismic Controls for Plumbing Piping and Equipment.

*******************************************************************************************

Retain subparagraph below if Subcontractor is required to assume responsibility for the design.

*******************************************************************************************

Delegated Design:  Design vibration isolation and seismic-restraint details, including comprehensive engineering analysis by a professional engineer licensed in the State of NM, using performance requirements and design criteria indicated.

REFERENCES

Air Conditioning, Heating, and Refrigeration Institute (AHRI):

AHRI 210/240 – Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment.

AHRI 340/360 – Performance Rating of Commercial and Industrial Unitary Air-Conditioning and Air-Source Heat Pump Equipment.

American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE):

ASHRAE 15 – Safety Standard for Refrigeration Systems.

ASHRAE 52.1 – Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter.

ASHRAE 52.2 – Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size

ASHRAE 62.1 – Ventilation for Acceptable Indoor Air Quality.

ASHRAE/ IESNA 90.1 – Energy Standard for Buildings Except Low-Rise Residential Buildings.

American Society of Mechanical Engineers (ASME):

ASME Section VIII – Boiler and Pressure Vessel Code - Pressure Vessels.

National Electrical Manufacturers Association (NEMA):

NEMA 250 – Enclosures for Electrical Equipment (1000 Volts Maximum).

        - National Fire Protection Association (NFPA):

NFPA 70 – National Electric Code.

SUBMITTALS

Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Shop Drawings:  For computer-room air conditioners.  Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Wiring Diagrams:  For power, signal, and control wiring.

Manufacturer's Installation Instructions:  Submit procedures for rigging and making service connections.

Operation and Maintenance Data:  Submit installation instructions, start-up instructions, operating and maintenance instructions, parts lists, controls, and accessories.

Manufacturer's Certificate:  Certify products meet or exceed specified requirements.

*******************************************************************************************

Retain subparagraphs below for compliance with LEED submittals.

*******************************************************************************************

LEED Submittals:

Product Data for Credit EA 4:  Documentation indicating that equipment and refrigerants comply.

Product Data for Prerequisite IEQ 1:  Documentation indicating that units comply with ASHRAE 62.1.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by any nationally recognized testing laboratory (NRTL) recognized under 29 CFR 1910.7.

ASME Compliance:  Fabricate and label water-cooled condenser shell to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Pressure Vessels, Division 1.

ASHRAE/ IESNA 90.1 Compliance:  Energy Efficiency Rating (EER) not less than prescribed by ASHRAE/ IESNA 90.1 when used in combination with compressors and evaporator coils when tested in accordance with [ARI 340/360] [ARI 210/240].

ASHRAE Compliance:

Fabricate and label refrigeration system to comply with ASHRAE 15, Safety Standard for Refrigeration Systems.

ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1,  Section 4 - Outdoor Air Quality, Section 5 - Systems and Equipment, Section 6 - Ventilation Rate Procedures, and Section 7 - Construction and Startup.

DELIVERY, STORAGE, AND HANDLING

    - Deliver computer room units on site in factory packing.  Inspect for damage.

    - Protect units from damage by storing away from computer room until floor or ceiling are installed.

COORDINATION

Coordinate layout and installation of computer-room air conditioners and suspension system with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

Coordinate installation of computer-room air conditioners with computer-room access flooring Installer.

Coordinate sizes and locations of concrete bases with actual equipment provided.

Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

EXTRA MATERIALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Fan Belts:  Furnish [one] [____] set of belt for each belt-driven fan.

Filters:  Furnish [one] [____] set of filters for each unit.

WARRANTY

Furnish five [___] year manufacturer’s warranty for entire unit.

PRODUCTS

MANUFACTURERS

Subject to compliance with requirements, provide product indicated on Drawings or by one of the following

Carrier Corporation; a United Technologies company.

Compu-Aire, Inc.

Data Aire Inc.

Koldwave, Inc.; a Mestek company.

Liebert Corporation.

McQuay International.

Trane; a business of American Standard Companies.

FLOOR-MOUNTED UNITS, 6 TONS AND LARGER

Description:  Packaged, [water] [glycol] [air] cooled, factory assembled, pre-wired and pre-piped unit, consisting of cabinet, fans filters, humidifier and controls, reheat and heating coils.

Assembly:  [Up-flow] [Down-flow] air delivery, [draw-through] [or] [blow-through] configuration.

Cabinet and Frame:  Welded steel, braced for rigidity, and supporting compressors and other mechanical equipment and fittings.

Doors and Access Panels:  Galvanized steel with polyurethane gaskets, hinges, and concealed fastening devices.

Insulation:  Thermally and acoustically insulate cabinet interior with 1-inch- thick duct liner.

Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Finish of Exterior Surfaces:  Baked-on, textured vinyl enamel; color to match computer equipment.

*******************************************************************************************

Retain subparagraph below for downflow units, delete for upflow units.

*******************************************************************************************

Floor Stand:  Welded tubular steel, with adjustable legs and vibration isolation pads.

Evaporator Fans and Motors:

Double-inlet, forward-curved centrifugal fan(s); statically and dynamically balanced [and with adjustable V-belt drive] [and direct drive.].

Motor:  Drip proof, permanently lubricated ball bearing motor with built-in current and overload protection.

Drive:  V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

**********************************************************************************************

Retain first paragraph below for units with DX refrigerant coils.

**********************************************************************************************

Refrigeration System:

**************************************************************************************

Retain one of the first three subparagraphs below for compressor type.

**************************************************************************************

Compressors:  Semi-hermetic reciprocating; with suction-gas-cooled, 1750-rpm motors; thermal overloads; oil sight glass; suction-line strainer; and reversible oil pumps; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

************OR************

Compressors:  Hermetic reciprocating; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

************OR************

Compressors:  Hermetic scroll; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

Refrigeration Circuits:  Two; each with hot-gas mufflers, thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Refrigerant:  R-407C or R-410A.

Refrigerant Evaporator Coil:  Alternate-row or split-face-circuit, direct-expansion coil of seamless copper tubes expanded into aluminum fins.

Mount coil assembly over stainless-steel drain pan, complying with ASHRAE 62.1.

*******************************************************************************************

Retain one of the first two subparagraphs below for integral, water cooled OR remote air-cooled refrigerant condenser.

*******************************************************************************************

Integral, Water-Cooled Refrigerant Condenser:  [Shell-and-tube type fabricated and labeled according to ASME Boiler and Pressure Vessel Code:  Section VIII] with liquid-line stop valve and head-pressure-actuated, [two] [three]-way regulating valve.  Terminate fluid connections outside cabinet.

Cooling Medium:  [Water] [Glycol solution].

************OR************

Remote Air-Cooled Refrigerant Condenser:  Corrosion-resistant cabinet, copper-tube aluminum-fin coils arranged for two circuits, multiple direct-drive propeller fans with permanently lubricated ball bearings, and single-phase motors with internal overload protection and integral electric control panel and disconnect switch.  Control capacity by [cycling fans] [modulating fan speeds] [three-way refrigerant bypass with receiver and isolation valve].

***********************************************************************************************

Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

***********************************************************************************************

Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

Cooling Medium:  Chilled Water

Control Valve:  Class 125 body

Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

*********************************************************************************************

Retain one of the first two paragraphs below for units with heating.

*********************************************************************************************

Electric-Resistance Heating Coil:  Enclosed finned-tube electric elements arranged for minimum of three stages, with thermal safety switches, manual-reset overload protection, and branch-circuit overcurrent protection.

************OR************

Hot-Water Heating Coil:  Seamless copper tubes expanded into aluminum fins with two-way modulating control valve and strainer.

Control Valve:  Class 125 body.

Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

Disposable, Panel Filter:  Pleated, lofted, nonwoven, reinforced cotton fabric; supported and bonded to welded-wire grid; enclosed in cardboard frame, [2-inch] [4 inch] nominal thickness, disposable, glass-fiber prefilter.

Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity

Recommended Final Resistance:  1.0 inches wg.

Arrestance (ASHRAE 52.1):  90 percent.

MERV (ASHRAE 52.2):  6 (Minimum).

Infrared Humidifier:  High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; pre-piped and using condensate water from cooling coils with stainless-steel or brass float-valve mechanism; located in bypass airstream; with flush-cycle timer and solenoid drain valve.

************OR************

Evaporative Pan Humidifier:  Stainless-steel pan and cover, serviceable without disconnecting water, drain, or electrical connections; pre-piped with stainless-steel or brass float-valve mechanism; electric-resistance heating coil; low-water-cutoff switch; flush-cycle timer; and solenoid drain valve.

Integral Electrical Controls:  Unit-mounted electrical enclosure with piano-hinged door, grounding lug, combination magnetic starters with overload relays, circuit breakers and cover interlock, and fusible control-circuit transformer.

Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Control System:  For control system requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

*******************************************************************************************

Retain one of the first two subparagraphs below for standard Electronic Controls System or Microprocessor Control System.

*******************************************************************************************

Electronic-Control System:  Solid state, with start button, stop button, temporary loss of power indicator, manual-reset circuit breakers, temperature control, humidity control, and monitor panel.

*********** [OR] **********

Microprocessor-Control System:  Continuously monitors operation of process cooling system; continuously displays room temperature and room relative humidity; sounds alarm on system malfunction and simultaneously displays problem.  If more than one malfunction occurs, system displays fault in sequence with room temperature and continues to display fault when malfunction is cleared until system is reset.

Push buttons shall stop and start process cooling system, silence audible alarm, test indicators, and display room's relative humidity.

BAS Interface:  Factory-installed hardware and software to enable the BAS to monitor, control, and display unit status and alarms

FLOOR-MOUNTED UNITS, 5 TONS AND SMALLER

Description:  Self-contained, factory assembled, prewired, and pre-piped; consisting of cabinet, fan, filters, and controls.

Assembly:  [Up-flow] [Down-flow] air delivery, [draw-through] [or] [blow-through] configuration.

Cabinet and Frame:  Welded tubular-steel frame with removable steel panels with baked-enamel finish, insulated with 1-inch thick duct liner.

*******************************************************************************************

Retain subparagraph below for downflow units, delete for upflow units.

*******************************************************************************************

Floor Stand:  Welded tubular steel, with adjustable legs and vibration isolation pads.

Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Evaporator Fans and Motors:

Forward-curved centrifugal fan(s); statically and dynamically balanced.

Motor:  Drip proof, permanently lubricated ball bearing motor with built-in current and overload protection.

Drive:  V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

**********************************************************************************************

Retain first paragraph below for units with DX refrigerant coils.

**************************************************************************************************

Refrigeration System:

Compressor:  Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

Refrigeration Circuit:  Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Refrigerant:  R-407C or R-410A.

Refrigerant Evaporator Coil:  Direct-expansion coil of seamless copper tubes expanded into aluminum fins, with two circuits, each with solenoid valve.

Mount coil assembly over stainless-steel drain pan complying with ASHRAE 62.1.

Remote Air-Cooled Refrigerant Condenser:  Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, [direct] [belt] driven.

Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

***********************************************************************************************

Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

***********************************************************************************************

Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

Cooling Medium:  Chilled Water

Control Valve:  Class 125 body

Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

**************************************************************************************************

Retain first paragraph below for units with heating.

**************************************************************************************************

        - Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor and high-temperature-limit switches.

Filter:  2-inch thick, disposable, glass-fiber media.

Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity.

Recommended Final Resistance:  1.0 inches wg.

Arrestance (ASHRAE 52.1):  90 percent.

MERV (ASHRAE 52.2):   6 (Minimum).

Infrared Humidifier:  High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; pre-piped and located in bypass airstream; with flush-cycle timer and solenoid drain valve.

Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Control System:

Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature [and humidity] control modules, [humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat].  Provide solid-state, wall-mounted control panel with start-stop switch, [adjustable humidity set point,] and adjustable temperature set point.

For additional control requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

CEILING-MOUNTED UNITS

Description:  Self-contained, [water] [glycol] [air] cooled, factory assembled, prewired, and pre-piped; consisting of cabinet, fan, filters, [humidifier,] and controls.

Assembly:  For horizontal ceiling mounting to fit T-bar ceiling opening of 24 by 48 inches.

Cabinet:  Galvanized steel with baked-enamel finish, insulated with 1/2-inch thick acoustic duct liner.

Integral factory-supplied supply and return grille to fit ceiling grid kit of 24 by 48 inches, with filter.

Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Supply-Air Fan:  Forward curved, centrifugal, and directly driven by two-speed motor.

**********************************************************************************************

Retain first paragraph below for units with DX refrigerant coils.

**************************************************************************************************

Refrigeration System:

Compressor:  Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

Refrigeration Circuit:  Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Refrigerant:  R-407C or R-410A.

Refrigerant Evaporator Coil:  Direct-expansion coil of seamless copper tubes expanded into aluminum fins.

Mount coil assembly over stainless-steel drain pan complying with ASHRAE 62.1.

*******************************************************************************************

Retain one of the first two subparagraphs below for integral, water cooled OR remote air-cooled refrigerant condenser.

*******************************************************************************************

Integral, Water-Cooled Refrigerant Condenser:  [Coaxial, counterflow, tube-in-tube] [Brazed-plate] type with liquid-line stop valve and head-pressure-actuated, water-regulating valve.

Cooling Medium:  [Water] [Glycol solution].

*********** [OR] **********

Remote Air-Cooled Refrigerant Condenser:  Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, direct driven.

Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

***********************************************************************************************

Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

***********************************************************************************************

Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

Cooling Medium:  Chilled Water

Control Valve:  Class 125 body

Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

*********************************************************************************************

Retain first paragraph below for units with heating.

*********************************************************************************************

Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor, dehumidification relay, and high-temperature-limit switches.

Filter:  1-inch- thick, disposable, glass-fiber media.

Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity

Recommended Final Resistance:  1.0 inches wg.

Arrestance (ASHRAE 52.1):  90 percent.

MERV (ASHRAE 52.2):  6 Minimum.

*********************************************************************************************

Retain first paragraph below for units with humidifier.

*********************************************************************************************

Atomizing Humidifier:  Centrifugal atomizer with stainless-steel pan, demister pad, and solenoid valve.

Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Control System:

Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature [and humidity] control modules, [humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat].  Provide solid-state, wall-mounted control panel with start-stop switch, [adjustable humidity set point,] and adjustable temperature set point.

For additional control requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

FAN MOTORS

Refer to Section 26 0700, Induction Motors – 500 HP and Smaller, for motor requirements.

Motor Sizes:  Minimum size as indicated on Drawings.  If not indicated, large enough so driven loads will not require motor to operate in service factor range above 1.0.

CAPACITIES AND CHARACTERISTICS

See the Equipment Schedule on the Design Drawings.

***************************************************************************************************

As a minimum, the following information and performance characteristics shall be shown on the drawings as part of the equipment schedule.

***************************************************************************************************

    - Manufacturer

    - Model Number

**********************************************************************************************

Retain first paragraph below for floor mounted units; delete for ceiling mounted units.

**************************************************************************************************

        - Unit Configuration:

[Upflow] [Downflow].

[Draw] [Blow] through.

Supply-Air Fan:

Number of Fans:  [One] [Two].

Airflow:  [       ] cfm.

Minimum Static Pressure:  [    ] inches wg.

Motor Size:  [    ] hp.

**********************************************************************************************

Retain first paragraph below for units with DX refrigerant coils and retain subparagraphs as applicable.

**************************************************************************************************

Refrigeration System:

Unit Energy Efficiency:  [    ] COP or EER.

Refrigerant Compressor:

Total Unit Cooling Capacity:  [       ] Btu/h.

Sensible Unit Cooling Capacity:  [       ] Btu/h.

Number of Compressors:  [One] [Two].

Motor Size:  [    ] hp.

Refrigerant Evaporator Coil:

Cooling Capacity:  [        ] Btu/h.

Entering-Air Dry-Bulb Temperature:  [    ] deg F.

Entering-Air Wet-Bulb Temperature:  [    ] deg F.

Leaving-Air Dry-Bulb Temperature:  [    ] deg F.

Leaving-Air Wet-Bulb Temperature:  [    ] deg F.

Water-Cooled Refrigerant Condenser:

Cooling Capacity:  [        ] Btu/h.

Condenser Water Flow:  [    ] gpm.

Cooling Medium:  [Water] [       ].

Entering-Water Temperature:  [    ] deg F.

Fluid Pressure Drop:  [    ] feet of head.

Air-Cooled Refrigerant Condenser:

Cooling Capacity:  [        ] Btu/h.

Entering-Air Temperature:  [    ] deg F.

Number of Condenser Fan Motors:  [    ].

Condenser Fan Motors:  [    ] hp.

Hydronic Heating Coil:

Cooling Coil Capacity:  [         ] Btu/h.

Entering-Air Dry-Bulb Temperature:  [     ] deg F.

Entering-Air Wet-Bulb Temperature:  [     ] deg F.

Leaving-Air Dry-Bulb Temperature:  [     ] deg F.

Leaving-Air Wet-Bulb Temperature:  [     ] deg F.

Fluid Flow:  [      ] gpm.

Entering-Fluid Temperature:  [     ] deg F.

Fluid Pressure Drop:  [     ] feet of head.

Cooling Medium:  Chilled Water

Hydronic Heating Coil:

Total:  [         ] Btu/h.

Entering-Air Dry-Bulb Temperature:  [    ] deg F.

Leaving-Air Dry-Bulb Temperature:  [    ] deg F.

Water Flow:  [      ] gpm.

Entering-Water Temperature:  [    ] deg F.

Leaving-Water Temperature:  [    ] deg F.

Fluid Pressure Drop:  [    ] feet of head.

Electric-Resistance Heating Coil:

Total Capacity:  [    ] kW>.

Stages of Heating:  [1] [2].

Humidifier:

Total:  [        ] lb/h.

Input:  [        ] Btu/h.

Electrical Characteristics:

Volts:  [120] [208] [240] [277] [480].

Phase:  [Single] [Three].

Hertz:  60.

Full-Load Amperes:  [     ].

Minimum Circuit Ampacity:  [     ].

Maximum Overcurrent Protection:  [      ].

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Examine walls, floors, and roofs for suitable conditions where computer-room air conditioners will be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install computer-room air conditioners level and plumb, maintaining manufacturer's recommended clearances.

Computer-Room Air-Conditioner Mounting:  Install using [elastomeric pads] [elastomeric mounts] [restrained spring isolators].  Comply with requirements for vibration isolation devices specified in Section 22 0548, Vibration and Seismic Controls for HVAC Piping and Equipment.

Suspended Computer-Room Air Conditioners:  Install using continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of computer-room air conditioner.

Comply with requirements for vibration isolation devices specified in Section 22 0548, Vibration and Seismic Controls for HVAC Piping and Equipment.

Fabricate brackets or supports as required.  Comply with requirements for hangers and supports specified in Section 22 0529, Hangers and Supports for HVAC Piping and Equipment.

CONNECTIONS

Drawings indicate general arrangement of piping, fittings, and specialties.

Install piping adjacent to machine to allow service and maintenance.

Water and Drainage Connections:  Comply with applicable requirements Section 22 1100 Facility Water Distribution.  Provide adequate connections for water-cooled units, condensate drain, and humidifier flushing system.

Hot-Water Heating Piping:  Comply with applicable requirements in Section 23 2113, Hydronic Piping.  Provide shutoff valves in inlet and outlet piping to heating coils.

Condenser-Water Piping:  Comply with applicable requirements in Section 23 2113, Hydronic Piping.   Provide shutoff valves in water inlet and outlet piping on water-cooled units.

Refrigerant Piping:  Comply with applicable requirements in Section 23 2300, Refrigerant Piping.  Provide shutoff valves and piping.

FIELD QUALITY CONTROL

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Tests and Inspections:

Inspect for and remove shipping bolts, blocks, and tie-down straps.

After installing computer-room air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Adjust initial temperature and humidity set points.

Set field-adjustable switches and circuit-breaker trip ranges as indicated.

Test and record for maintenance of room conditions over continuous 24-hour period.

Computer-room air conditioners will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

After startup service and performance test, change filters and flush humidifier.

END OF SECTION

****************************************************************

Do not delete the following reference information.

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 8123 Rev. 0, dated November 23, 2010.