SECTION 23 8123

COMPUTER-ROOM AIR-CONDITIONERS

- *************************************************************************************************************

- LANL MASTER SPECIFICATION

- This template must be edited for each project.   In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification items for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  This specification template is tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM). To seek a variance from requirements of the ESM that are applicable, contact the ESM Mechanical POC. Please contact POC with suggestions for improvement as well.

- When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

- This Specification is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

- Seismic:  If all CRAC units are not exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this Section to be Project-specific, refer to Sections 22 0548.23, Vibration and Seismic Controls for Mechanical Systems, and 01 8734, Seismic Qualification of Nonstructural Components (IBC), as applicable. In order to edit this section for job-specific seismic requirements, refer to author notes that begin with “Seismic.”  Also, see the Seismic Specification Guide for Mechanical Non-Structural Components for guidance on properly editing this section.

- *************************************************************************************************************

- GENERAL

      - SUMMARY

        - Section Includes:

          - Floor-mounted computer-room air conditioners, 6 tons and larger.

          - Floor-mounted computer-room air conditioners, 5 tons and smaller.

          - Ceiling-mounted computer-room air conditioners.

*************************************************************************************************************

Seismic: If the CRACs are exempt from seismic design then delete both 1.2A and 1.2B

- Otherwise, see the seismic portion of the previous author note.

- *************************************************************************************************************

- 1.2		RELATED SECTIONS

    - Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements.

    - Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

      - PERFORMANCE REQUIREMENTS

- Supplier-provided control systems, including instruments, signal transmissions, panels, cabinets, and other control and instrumentation requirements shall be coordinated with the Control and Instrumentation Subcontractor.  Some equipment controls are specified in other portions of the subcontract documents.  As part of the work of this section, coordinate with these other suppliers and trades to provide a complete and working equipment controls.

- It is the responsibility of the bidder to read and conform to all articles of this specification, review all subcontract drawings of all divisions, and coordinate with all equipment suppliers of material specified under other sections of the specifications.

- HVAC fans and associated motors shall perform satisfactorily in the following service conditions:

      - Elevation:  7500 feet above sea level.

      - Maximum ambient temperature:  104 degrees F.

      - Minimum ambient temperature:  Minus 20 degrees F.

      - 24-hour average temperature:  not exceeding 86 degrees F.

- *************************************************************************************************************

Seismic: Delete D if CRAC(s) is/are exempt from seismic design.  However, if paragraph applies:

- edit it in accordance with content of 22 0548.23 and/or 01 8734

- the “E” drawings for the controller shall also state that the controller is a Designated Seismic System

- *************************************************************************************************************

- Seismic Performance Requirements

  - The unit(s) shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the Drawings] [in Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems]].

      - REFERENCES

    - Air Conditioning, Heating, and Refrigeration Institute (AHRI):

      - AHRI 210/240 – Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment.

      - AHRI 340/360 – Performance Rating of Commercial and Industrial Unitary Air-Conditioning and Air-Source Heat Pump Equipment.

    - American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE):

      - ASHRAE 15 – Safety Standard for Refrigeration Systems.

      - ASHRAE 52.2 – Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size

      - ASHRAE 62.1-[2013] – Ventilation for Acceptable Indoor Air Quality.

      - ASHRAE/ IESNA 90.1-[2013] – Energy Standard for Buildings Except Low-Rise Residential Buildings.

    - American Society of Mechanical Engineers (ASME):

      - ASME Section VIII – Boiler and Pressure Vessel Code - Pressure Vessels.

      - ASME B31.9-[2014] – Building Services Piping

    - National Electrical Manufacturers Association (NEMA):

          - NEMA 250 – Enclosures for Electrical Equipment (1000 Volts Maximum).

        - National Fire Protection Association (NFPA):

          - NFPA 70 – National Electric Code.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include material descriptions, dimensions of individual components and profiles, and finishes for computer-room air-conditioning units.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

- *******************************************************************************************

- Retain subparagraphs below for compliance with LEED submittals.

- *******************************************************************************************

        - Sustainable Design Submittals:

          - Product Data for Credit EA 4:  Documentation indicating that equipment and refrigerants comply.

          - Product Data for Prerequisite IEQ 1:  Documentation indicating that units comply with ASHRAE 62.1.

        - Shop Drawings: For computer-room air conditioners.

          - Include plans, elevations, sections, and attachment details.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

        - Color Samples: For unit cabinet, discharge grille, and exterior louver and for each color and texture specified.

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Plans, elevations, and other details, drawn to scale, using input from installers of the items involved.

Retain "Field quality-control reports" Paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Sample Warranty: For special warranty.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For computer-room air conditioners to include in emergency, operation, and maintenance manuals.

        - Refrigeration Appliance Inventory Form: Complete form as required by LANL (e.g., procedure ENV-ES-QP-311.8).

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by any nationally recognized testing laboratory (NRTL) recognized under 29 CFR 1910.7.

        - ASME Compliance:  Fabricate and label water-cooled condenser shell to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Pressure Vessels, Division 1.

        - ASHRAE/ IESNA 90.1 Compliance:  Energy Efficiency Rating (EER) not less than prescribed by ASHRAE/ IESNA 90.1 when used in combination with compressors and evaporator coils when tested in accordance with [AHRI 340/360] [AHRI 210/240].

        - ASHRAE Compliance:

          - Fabricate refrigeration system to comply with ASHRAE 15, Safety Standard for Refrigeration Systems.

          - ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1,  Section 4–Outdoor Air Quality, Section 5–Systems and Equipment, Section 6–Ventilation Rate Procedures, and Section 7– Construction and Startup.

      - DELIVERY, STORAGE, AND HANDLING

    - Deliver computer room units on site in factory packing.  Inspect for damage.

    - Protect units from damage by storing away from computer room until floor or ceiling is installed.

      - COORDINATION

        - Coordinate layout and installation of computer-room air conditioners and suspension system with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

        - Coordinate installation of computer-room air conditioners with computer-room access flooring installer.

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

        - Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

      - EXTRA MATERIALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Fan Belts:  Furnish [one] [____] set of belt for each belt-driven fan.

          - Filters:  Furnish [one] [____] set of filters for each unit.

      - WARRANTY

        - Furnish five [___] year manufacturer’s warranty for entire unit.

- PRODUCTS

      - MANUFACTURERS

*************************************************************************************************************

For CRACs that are not exempt from seismic, if Project Spec includes 22 0548.23, and if mounting and/or anchorage devices are to be used that differ from those specified in 22 0548.23, they must be described herein (in PART 2).

*************************************************************************************************************

        - Subject to compliance with requirements, provide product indicated on Drawings or by one of the following

          - Compu-Aire, Inc.

          - Data Aire Inc.

          - Liebert Corporation.

          - Trane; an Ingersoll Rand brand.

      - FLOOR-MOUNTED UNITS, 6 TONS AND LARGER

        - Description:  Packaged, [water] [glycol] [air] cooled, factory assembled, pre-wired and pre-piped unit, consisting of cabinet, fans filters, humidifier and controls, reheat and heating coils.

        - Assembly:  [Up-flow] [Down-flow] air delivery, [draw-through] [or] [blow-through] configuration.

        - Cabinet and Frame:  Welded steel, braced for rigidity, and supporting compressors and other mechanical equipment and fittings.

          - Doors and Access Panels:  Galvanized steel with polyurethane gaskets, hinges, and concealed fastening devices.

          - Insulation:  Thermally and acoustically insulate cabinet interior with 1-inch- thick duct liner.

          - Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

          - Finish of Exterior Surfaces:  Baked-on, textured vinyl enamel; color to match computer equipment.

- *******************************************************************************************

- Retain subparagraph below for downflow units, delete for upflow units installed on structural floor.

- *******************************************************************************************

          - Floor Stand:  Welded tubular steel, with adjustable legs and vibration isolation pads.

        - Evaporator Fans and Motors:

          - Double-inlet, forward-curved centrifugal fan(s); statically and dynamically balanced [and with adjustable V-belt drive] [and direct drive.].

          - Motor:  Drip proof, permanently lubricated ball bearing motor with built-in current and overload protection.

          - Drive:  V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

- **********************************************************************************************

- Retain first paragraph below for units with DX refrigerant coils.

- **********************************************************************************************

        - Refrigeration System:

- **************************************************************************************

- Retain one of the first three subparagraphs below for compressor type.

- **************************************************************************************

          - Compressors:  Semi-hermetic reciprocating; with suction-gas-cooled, 1750-rpm motors; thermal overloads; oil sight glass; suction-line strainer; and reversible oil pumps; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

- ************OR************

          - Compressors:  Hermetic reciprocating; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

************OR************

          - Compressors:  Hermetic scroll; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

          - Refrigeration Circuits:  Two; each with hot-gas mufflers, thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

          - Refrigerant:  [R-407C] [R-410A].

          - Refrigerant Evaporator Coil:  Alternate-row or split-face-circuit, direct-expansion coil of seamless copper tubes expanded into aluminum fins.

            - Mount coil assembly over stainless-steel drain pan, complying with ASHRAE 62.1.

- *******************************************************************************************

- Retain one of the first two subparagraphs below for integral, water cooled OR remote air-cooled refrigerant condenser.

- *******************************************************************************************

          - Integral, Water-Cooled Refrigerant Condenser:  [Shell-and-tube type fabricated and labeled according to ASME Boiler and Pressure Vessel Code:  Section VIII] with liquid-line stop valve and head-pressure-actuated, [two] [three]-way regulating valve.  Terminate fluid connections outside cabinet.

            - Cooling Medium:  [Water] [Glycol solution].

- ************OR************

          - Remote Air-Cooled Refrigerant Condenser:  Corrosion-resistant cabinet, copper-tube aluminum-fin coils arranged for two circuits, multiple direct-drive propeller fans with permanently lubricated ball bearings, and single-phase motors with internal overload protection and integral electric control panel and disconnect switch.  Control capacity by [cycling fans] [modulating fan speeds] [three-way refrigerant bypass with receiver and isolation valve].

- ****************************************************************************************************

- Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

- ****************************************************************************************************

        - Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

          - Cooling Medium:  Chilled Water

          - Control Valve:  Class 125 body

            - Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

            - Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

- *********************************************************************************************

- Retain one of the first two paragraphs below for units with heating.

- *********************************************************************************************

        - Electric-Resistance Heating Coil:  Enclosed finned-tube electric elements arranged for minimum of three stages, with thermal safety switches, manual-reset overload protection, and branch-circuit overcurrent protection.

- ************OR************

        - Hot-Water Heating Coil:  Seamless copper tubes expanded into aluminum fins with two-way modulating control valve and strainer.

          - Control Valve:  Class 125 body.

            - Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

            - Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

            - Listed item per ASME B31.9.

        - Disposable, Panel Filter:  Pleated, lofted, nonwoven, reinforced cotton fabric; supported and bonded to welded-wire grid; enclosed in cardboard frame, [2-inch] [4 inch] nominal thickness, disposable, glass-fiber prefilter.

          - Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity

          - Recommended Final Resistance:  1.0 inches wg.

          - MERV (ASHRAE 52.2):  8 (Minimum).

        - Infrared Humidifier:  High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; pre-piped and using condensate water from cooling coils with stainless-steel or brass float-valve mechanism; located in bypass airstream; with flush-cycle timer and solenoid drain valve.

- ************OR************

        - Evaporative Pan Humidifier:  Stainless-steel pan and cover, serviceable without disconnecting water, drain, or electrical connections; pre-piped with stainless-steel or brass float-valve mechanism; electric-resistance heating coil; low-water-cutoff switch; flush-cycle timer; and solenoid drain valve.

        - Economizer: Provide economizer for free cooling, per ASHRAE 90.1-[2013], Section 6.5.1

        - Integral Electrical Controls:  Unit-mounted electrical enclosure with piano-hinged door, grounding lug, combination magnetic starters with overload relays, circuit breakers and cover interlock, and fusible control-circuit transformer.

        - Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

        - Control System:  For control system requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

- *******************************************************************************************

- Retain one of the first two subparagraphs below for standard Electronic Controls System or Microprocessor Control System.

- *******************************************************************************************

          - Electronic-Control System:  Solid state, with start button, stop button, temporary loss of power indicator, manual-reset circuit breakers, temperature control, humidity control, and monitor panel.

- *********** [OR] **********

          - Microprocessor-Control System:  Continuously monitors operation of process cooling system; continuously displays room temperature and room relative humidity; sounds alarm on system malfunction and simultaneously displays problem.  If more than one malfunction occurs, system displays fault in sequence with room temperature and continues to display fault when malfunction is cleared until system is reset.

            - Push buttons shall stop and start process cooling system, silence audible alarm, test indicators, and display room's relative humidity.

            - BAS Interface:  Factory-installed hardware and software to enable the BAS to monitor, control, and display unit status and alarms

      - FLOOR-MOUNTED UNITS, 5 TONS AND SMALLER

        - Description:  Self-contained, factory assembled, prewired, and pre-piped; consisting of cabinet, fan, filters, and controls.

        - Assembly:  [Up-flow] [Down-flow] air delivery, [draw-through] [or] [blow-through] configuration.

        - Cabinet and Frame:  Welded tubular-steel frame with removable steel panels with baked-enamel finish, insulated with 1-inch thick duct liner.

- *******************************************************************************************

- Retain subparagraph below for downflow units, delete for upflow units installed on structural floor.

- *******************************************************************************************

          - Floor Stand:  Welded tubular steel, with adjustable legs and vibration isolation pads.

          - Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

        - Evaporator Fans and Motors:

          - Forward-curved centrifugal fan(s); statically and dynamically balanced.

          - Motor:  Drip proof, permanently lubricated ball bearing motor with built-in current and overload protection. Meet the requirements of IEEE 841.

          - Drive:  V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

- **********************************************************************************************

- Retain first paragraph below for units with DX refrigerant coils.

- **************************************************************************************************

        - Refrigeration System:

          - Compressor:  Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

          - Refrigeration Circuit:  Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

          - Refrigerant:  [R-407C] [R-410A].

          - Refrigerant Evaporator Coil:  Direct-expansion coil of seamless copper tubes expanded into aluminum fins, with two circuits, each with solenoid valve.

            - Mount coil assembly over stainless-steel drain pan complying with ASHRAE 62.1.

          - Remote Air-Cooled Refrigerant Condenser:  Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, [direct] [belt] driven.

            - Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

- ***********************************************************************************************

- Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

- ***********************************************************************************************

        - Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

          - Cooling Medium:  Chilled Water

          - Control Valve:  Class 125 body

            - Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

            - Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

            - Listed item per ASME B31.9.

- **************************************************************************************************

- Retain first paragraph below for units with heating.

- **************************************************************************************************

        - Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor and high-temperature-limit switches.

        - Filter:  2-inch thick, disposable, glass-fiber media.

          - Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity.

          - Recommended Final Resistance:  1.0 inches wg.

          - MERV (ASHRAE 52.2):   8 (Minimum).

        - Infrared Humidifier:  High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; pre-piped and located in bypass airstream; with flush-cycle timer and solenoid drain valve.

        - Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

        - Control System:

          - Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature [and humidity] control modules, [humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat].  Provide solid-state, wall-mounted control panel with start-stop switch, [adjustable humidity set point,] and adjustable temperature set point.

          - For additional control requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

      - CEILING-MOUNTED UNITS

        - Description:  Self-contained, [water] [glycol] [air] cooled, factory assembled, prewired, and pre-piped; consisting of cabinet, fan, filters, [humidifier,] and controls.

        - Assembly:  For horizontal ceiling mounting to fit T-bar ceiling opening of 24 by 48 inches.

        - Cabinet:  Galvanized steel with baked-enamel finish, insulated with 1/2-inch thick acoustic duct liner.

          - Integral factory-supplied supply and return grille to fit ceiling grid kit of 24 by 48 inches, with filter.

          - Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

        - Supply-Air Fan:  Forward curved, centrifugal, and directly driven by two-speed motor.

- **********************************************************************************************

- Retain first paragraph below for units with DX refrigerant coils.

- **************************************************************************************************

        - Refrigeration System:

          - Compressor:  Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

          - Refrigeration Circuit:  Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

          - Refrigerant:  [R-407C] [R-410A].

          - Refrigerant Evaporator Coil:  Direct-expansion coil of seamless copper tubes expanded into aluminum fins.

            - Mount coil assembly over stainless-steel drain pan complying with ASHRAE 62.1.

- ********************************************************************************************

- Retain one of the first two subparagraphs below for integral, water cooled OR remote air-cooled refrigerant condenser.

- ********************************************************************************************

          - Integral, Water-Cooled Refrigerant Condenser:  [Coaxial, counterflow, tube-in-tube] [Brazed-plate] type with liquid-line stop valve and head-pressure-actuated, water-regulating valve.

            - Cooling Medium:  [Water] [Glycol solution].

- *********** [OR] **********

          - Remote Air-Cooled Refrigerant Condenser:  Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, direct driven.

          - Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

- ****************************************************************************************************

- Retain paragraph below for units with chilled water coil and delete Refrigeration System paragraph above with DX refrigerant coil.

- ****************************************************************************************************

        - Hydronic Cooling Coil:  Seamless copper tubes expanded into aluminum fins with modulating [two] [three]-way control valve.

          - Cooling Medium:  Chilled Water

          - Control Valve:  Class 125 body

            - Maximum Pressure Drop:  [3 psig] [5 psig] at design flow rate.

            - Close-Off (Differential) Pressure Rating:  100 percent of pressure differential across valve or 100 percent of total system (pump) head.

- *********************************************************************************************

- Retain first paragraph below for units with heating.

- *********************************************************************************************

        - Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor, dehumidification relay, and high-temperature-limit switches.

        - Filter:  1-inch- thick, disposable, glass-fiber media.

          - Initial Resistance:  [0.30] [___] inches wg. at 500 fpm face velocity

          - Recommended Final Resistance:  1.0 inches wg.

          - MERV (ASHRAE 52.2):  8 Minimum.

- *********************************************************************************************

- Retain first paragraph below for units with humidifier.

- *********************************************************************************************

        - Atomizing Humidifier:  Centrifugal atomizer with stainless-steel pan, demister pad, and solenoid valve.

        - Disconnect Switch:  Non-automatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

        - Control System:

          - Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature [and humidity] control modules, [humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat].  Provide solid-state, wall-mounted control panel with start-stop switch, [adjustable humidity set point,] and adjustable temperature set point.

          - For additional control requirements, see Article 1.2.A.  Refer to Section 25 5000, Integrated Automated Facility Controls.  All necessary controls shall be factory installed and wired.

      - FAN MOTORS

        - Meet the requirements of IEEE 841.

        - Motor Sizes:  Minimum size as indicated on Drawings.  If not indicated, large enough so driven loads will not require motor to operate in service factor range above 1.0.

      - CAPACITIES AND CHARACTERISTICS

See the Equipment Schedule on the Design Drawings.

***************************************************************************************************

As a minimum, the following information and performance characteristics shall be shown on the drawings as part of the equipment schedule.

    - Manufacturer

    - Model Number

- **********************************************************************************************

- Retain first paragraph below for floor mounted units; delete for ceiling mounted units.

- **************************************************************************************************

        - Unit Configuration:

          - [Upflow] [Downflow].

          - [Draw] [Blow] through.

        - Supply-Air Fan:

          - Number of Fans:  [One] [Two].

          - Airflow:  [       ] cfm.

          - Minimum Static Pressure:  [    ] inches wg.

          - Motor Size:  [    ] hp.

- ****************************************************************************************************

- Retain first paragraph below for units with DX refrigerant coils and retain subparagraphs as applicable.

- ****************************************************************************************************

        - Refrigeration System:

          - Unit Energy Efficiency:  [    ] COP or EER.

          - Refrigerant Compressor:

            - Total Unit Cooling Capacity:  [       ] Btu/h.

            - Sensible Unit Cooling Capacity:  [       ] Btu/h.

            - Number of Compressors:  [One] [Two].

            - Motor Size:  [    ] hp.

          - Refrigerant Evaporator Coil:

            - Cooling Capacity:  [        ] Btu/h.

            - Entering-Air Dry-Bulb Temperature:  [    ] deg F.

            - Entering-Air Wet-Bulb Temperature:  [    ] deg F.

            - Leaving-Air Dry-Bulb Temperature:  [    ] deg F.

            - Leaving-Air Wet-Bulb Temperature:  [    ] deg F.

          - Water-Cooled Refrigerant Condenser:

            - Cooling Capacity:  [        ] Btu/h.

            - Condenser Water Flow:  [    ] gpm.

            - Cooling Medium:  [Water] [       ].

            - Entering-Water Temperature:  [    ] deg F.

            - Fluid Pressure Drop:  [    ] feet of head.

          - Air-Cooled Refrigerant Condenser:

            - Cooling Capacity:  [        ] Btu/h.

            - Entering-Air Temperature:  [    ] deg F.

            - Number of Condenser Fan Motors:  [    ].

            - Condenser Fan Motors:  [    ] hp.

        - Hydronic Heating Coil:

          - Cooling Coil Capacity:  [         ] Btu/h.

          - Entering-Air Dry-Bulb Temperature:  [     ] deg F.

          - Entering-Air Wet-Bulb Temperature:  [     ] deg F.

          - Leaving-Air Dry-Bulb Temperature:  [     ] deg F.

          - Leaving-Air Wet-Bulb Temperature:  [     ] deg F.

          - Fluid Flow:  [      ] gpm.

          - Entering-Fluid Temperature:  [     ] deg F.

          - Fluid Pressure Drop:  [     ] feet of head.

          - Cooling Medium:  Chilled Water

        - Hydronic Heating Coil:

          - Total:  [         ] Btu/h.

          - Entering-Air Dry-Bulb Temperature:  [    ] deg F.

          - Leaving-Air Dry-Bulb Temperature:  [    ] deg F.

          - Water Flow:  [      ] gpm.

          - Entering-Water Temperature:  [    ] deg F.

          - Leaving-Water Temperature:  [    ] deg F.

          - Fluid Pressure Drop:  [    ] feet of head.

        - Electric-Resistance Heating Coil:

          - Total Capacity:  [    ] kW>.

          - Stages of Heating:  [1] [2].

        - Humidifier:

          - Total:  [        ] lb/h.

          - Input:  [        ] Btu/h.

        - Electrical Characteristics:

          - Volts:  [120] [208] [240] [277] [480].

          - Phase:  [Single] [Three].

          - Hertz:  60.

          - Full-Load Amperes:  [     ].

          - Minimum Circuit Ampacity:  [     ].

          - Maximum Overcurrent Protection:  [      ].

********************************************************************************************************

- EXECUTION

*************************************************************************************************************

For CRACs that are not exempt from seismic, if Project Spec includes 22 0548.23, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 22 0548.23, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine walls, floors, and roofs for suitable conditions where computer-room air conditioners will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install computer-room air conditioners level and plumb, maintaining manufacturer's recommended clearances. [Coordinate with the computer room access floor installer].

        - Computer-Room Air-Conditioner Mounting:  Install using [elastomeric pads] [elastomeric mounts] [restrained spring isolators].  Suspended Computer-Room Air Conditioners:  Install using continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of computer-room air conditioner.

          - Fabricate brackets or supports as required.  Comply with requirements for hangers and supports specified in 22 0548.23, Vibration and Seismic Controls for Mechanical Systems.

      - CONNECTIONS

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to machine to allow service and maintenance.

        - Water and Drainage Connections:  Comply with applicable requirements Section 22 1100, Facility Water Distribution.  Provide adequate connections for water-cooled units, condensate drain, and humidifier flushing system.

        - Chilled- and Hot-Water Heating Piping:  Comply with applicable requirements in Section 23 2113, Hydronic Piping.  Provide shutoff valves in inlet and outlet piping to heating coils.

        - Condenser-Water Piping:  Comply with applicable requirements in Section 23 2113, Hydronic Piping.   Provide shutoff valves in water inlet and outlet piping on water-cooled units.

        - Refrigerant Piping:  Comply with applicable requirements in Section 23 2300, Refrigerant Piping.  Provide shutoff valves and piping.

*************************************************************************************************************

Seismic:  Flexible connections (between the CRACs and other nonstructural components it’s associated with) are one of the requirements for the exemption from seismic design.  Ensure such connections are indicated on the drawings in the applicable location(s).

*************************************************************************************************************

        - Install flexible connections where shown on drawings.

      - FIELD QUALITY CONTROL

        - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

        - Tests and Inspections:

          - Inspect for and remove shipping bolts, blocks, and tie-down straps.

          - After installing computer-room air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

          - Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

          - Adjust initial temperature and humidity set points.

          - Set field-adjustable switches and circuit-breaker trip ranges as indicated.

          - Test and record for maintenance of room conditions over continuous 24-hour period.

        - Computer-room air conditioners will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

        - After startup service and performance test, change filters and flush humidifier.

END OF SECTION

***************************************************************

Do not delete the following reference information.

***************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 23 8123 Rev. 1, dated November 21, 2017.