SECTION 26 0519

LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

*******************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*******************************************************************************************************

GENERAL

SECTION INCLUDES

*************************************************************************************************************

Edit article to match Project requirements. Delete items not applicable to Project.

*************************************************************************************************************

Building wire (600 V)

Metal-clad cable (600 V)

Wire and cable connectors

Insulating tape and tubing

Wire pulling lubricant

LANL Performed Work

None

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for components and installation.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application and environment in which installed.

*************************************************************************************************************

Edit the following article to match project conditions. Delete if there are no critical systems.

*************************************************************************************************************

Definitions

Critical System. The following are critical systems:

Safety Class systems

Safety Significant systems

Fire pump systems covered in NEC Article 695

Emergency power systems covered in NEC Article 700

Legally required standby power systems covered in NEC Article 701

Critical operations power systems covered in NEC Article 708

*************************************************************************************************************

Edit the following article to match project conditions.

*************************************************************************************************************

SUBMITTALS

Submit the following in accordance with the provisions of Section 01 3300 Submittal Procedures:

Catalog Data: Compression connectors; indicate installation tools and dies that will be used.

*************************************************************************************************************

Edit the following article to match project conditions.

*************************************************************************************************************

Project record Documents

Submit the following in accordance with the provisions of Section 01 7839 Project Record Documents:

Field Test Records:

Cable pulling records required in Building Wire Installation.

Inspections and tests required in Field Quality Control.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500 Substitution Procedures.

  - BUILDING WIRE

Provide NRTL-listed building wire as shown on the Drawings with the following characteristics:

Description: Single conductor 600 V insulated wire.

Conductor:

*************************************************************************************************************

Edit the following two articles to match project conditions. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger. If aluminum conductors will not be used, delete the information within brackets. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] 98% conductivity, annealed, uncoated copper, ASTM B 3 Standard Specification for Soft or Annealed Copper Wire, solid or stranded as specified in Part 3 of this Section.

[Where indicated on the Drawings for conductors 1/0 AWG and larger: AA 8000 series aluminum alloy registered in ASTM B 800 Standard Specification for 8000 Series Aluminum Alloy Wire for Electrical Purposes—Annealed and Intermediate Tempers, compact stranded in accordance with ASTM B 801 Standard Specification for Concentric-Lay-Stranded Conductors of 8000 Series Aluminum Alloy for Subsequent Covering or Insulation.]

Insulation: The following types, rated 600 volts:

*************************************************************************************************************

Edit the following two articles to match project conditions. Use thermoset (XHHW-2) conductor insulation for all branch circuits and feeders for Safety Class, Safety Significant, NEC Article 695, NEC Article 700, NEC Article 701, and NEC Article 708 systems. Thermoset insulation may also be needed for wiring in high temperature or high radiation environments. If these systems or conditions do not exist on this Project, delete the information within brackets. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] 1 AWG and smaller, Type THHN/THWN-2 per UL Standard 83, “Thermoplastic-Insulated Wires and Cables.”

[Where indicated on the Drawings: 1 AWG and smaller, Type XHHW-2 per UL Standard 44, “Thermoset-Insulated Wires and Cables.”]

1/0 AWG and larger, Type XHHW-2 per UL Standard 44, “Thermoset-Insulated Wires and Cables.”

Color code conductors as follows:

Use colored insulation for color coding conductors 6 AWG and smaller.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.  Manufacturer: 3M “Scotch 35"

Provide black conductor insulation where colored tape is used for color coding.

Use the following color codes for AC power system conductors:

| System Voltage: Conductor: | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground | 120/240V |
| --- | --- | --- | --- | --- |
| Phase A: | Brown | Black | Black | Black |
| Phase B: | Orange | Red | Red | Red |
| Phase C: | Yellow | Blue | Blue | --- |
| Grounded (Neutral): | Gray | White | White White/Red* | White White/Blue* |
| Equipment Grounding: | Green | Green | Green | Green |
| Isolated Ground: | --- | --- | Green/Yellow | --- |
| Switched: | Purple | Pink | --- | Blue |

* Provide grounded conductor insulation with colored stripe when installed in any raceway, box, or enclosure with wiring of another system voltage.

Use the following color codes for DC power system conductors:

Positive:	Red

Negative:	Black

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

In existing facilities, change color coding of existing service, feeder, and major branch circuits (50 amps and larger) to match the above color code.

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

*************************************************************************************************************

Type MC cable may be used in IBC Business Group B occupancies for branch circuit wiring systems. Refer to Section D5020 in the LANL Engineering Standards for additional information. Delete this article when metal-clad cable is not used.

*************************************************************************************************************

  - METAL-CLAD CABLE

Provide metal-clad cable (Type MC) that complies with UL Standard 1569 – Metal-Clad Cables, the NEC, and this Section.

Metal-clad cable shall consist of 600 V THHN insulated solid copper circuit conductors, an insulated solid copper equipment grounding conductor, a Mylar wrapping around the conductor bundle, and a close fitting aluminum or galvanized steel outer sheath.

Provide MC cables with quantities and sizes (minimum 12 AWG) of conductors as indicated on the Drawings.

Provide larger conductor sizes as required to limit branch circuit voltage drop to 3 percent at the full connected load.

Use larger conductor sizes to adjust allowable ampacity if there are more than 3 current-carrying conductors in a cable.

For isolated ground power circuits provide Type MC cables with a separate neutral conductor and isolated ground conductor for each circuit; uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.

Provide MC cables with the same conductor color coding as specified for BUILDING WIRE.

Metal-clad cable manufacturer: AFC Cable Systems Inc.

Provide NRTL listed, insulated throat or insulating bushing, connectors for Type MC cables. Manufacturers: Arlington Industries “SNAP2IT.” O-Z/Gedney ETP “Speed-Lock,” “AMC,” “KC,” or PK as appropriate for MC cable diameter.

  - WIRING CONNECTORS

For splices and taps on copper wire, sizes 20 to 12 AWG solid and 16 to 14 AWG stranded, use push-on, insulated, spring type connectors, rated 600 V and 105 ºC that are NRTL-listed to UL 486C Splicing Wire Connectors and provide a means of visual inspection of the connection. Manufacturer: IDEAL “In-Sure.”

For splices and taps on copper wire, sizes 8 AWG and smaller, use insulated, spring type connectors, rated 600 volts and 105 ºC that are NRTL-listed to UL 486C, Splicing Wire Connectors. Manufacturer: 3M “Scotchlok.”

For splices and taps on copper wire, sizes 6 AWG through 1 AWG, use the following materials:

Tin-plated copper split-bolt connectors that meet the requirements in UL 486A-486B, Wire Connectors; provide with matching 600-volt snap-on insulating cover. Manufacturer: FCI Burndy “Type KSA” with “Type SC” insulating cover.

Multi-tap connectors that meet the requirements of UL 486A-466B that have two or more range-taking mechanical lugs and matching 600-volt insulated cover. Manufacturers: Burndy ‘POLYTAP” or “UNITAP”, Ilsco “Type PCT”, Blackburn “AMT”.

For copper wire, sizes 1/0 AWG and larger, use UL 486A-486B listed circumferential or hexagonal crimp compression terminals, splices, or adapters.

Provide compression terminals and splices made from electro-tin plated seamless copper tubing and marked with wire size, die index / color code, and number / locations of crimps. Manufacturers: FCI Burndy Types “YA”, “YA-L”, “YA-L-NT”, “YS”, and “YC-C.” Thomas & Betts “Color-Keyed.”

Provide straight and offset compression adapters made from electro-tin plated aluminum, NRTL listed for use on copper conductors, and marked with wire size, die index / color code, and number / locations of crimps. Each adapter shall include a 600 V, 90 degree C rated insulating cover. Manufacturer: FCI Burndy Types “AYP” and “AYPO.”

Range-taking, die-less, or indenter-applied terminals are not acceptable.

*************************************************************************************************************

Edit the following two article to match project conditions. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger. If aluminum conductors will not be used, delete the information within brackets. *************************************************************************************************************

[For aluminum wire, sizes 1/0 AWG and larger, use UL 486A-486B listed circumferential or hexagonal crimp compression terminals, splices, or adapters.

Provide compression terminals and splices made from electro-tin plated wrought aluminum, filled with oxide inhibiting compound, and marked with wire size, die index / color code, and number / locations of crimps. Manufacturer: FCI Burndy Types “YA-A,” “YS-A,” and “YRB.” Thomas & Betts “Color-Keyed.”

Provide straight and offset compression adapters made from electro-tin plated aluminum, NRTL listed for use on aluminum conductors, and marked wire size, die index / color code, and number / locations of crimps. Each adapter shall include a 600 V, 90 degree C rated insulating cover. Manufacturer: FCI Burndy Types “AYP” and “AYPO.” Thomas & Betts “Color-Keyed.”

Range-taking, die-less, or indenter-applied terminals are not acceptable.]

For control wiring use nylon insulated crimp-on terminals with insulation grip that meet the requirements of UL 486A-486B. Manufacturer: 3M “Scotchlok MNG,” Thomas & Betts “Sta-Kon.”

Use ring tongue terminals for nutted studs.

Use flanged fork terminals for barrier terminal blocks.

Use pin terminals or ferrules for DIN type terminal blocks.

Insulation-piercing type connectors are not acceptable for power or control wiring.

  - INSULATING TAPE AND TUBING

For making re-enterable tape-insulated splices and connections, provide varnished cambric electrical insulating tape made of cotton cambric fabric that is oil primed and coated with electrical insulating varnish. Manufacturer: 3M “Scotch 2510” (no adhesive) and Scotch 2520” (pressure-sensitive adhesive).

Insulate taped splices and connections using ethylene propylene rubber (EPR) tape that meets the requirements of UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and is rated for 90 ºC continuous operation and   130 ºC short-term overload service. Manufacturer: 3M “Scotch 130C”

For the outer covering of tape-insulated splices and connections use vinyl plastic tape that meets the requirements of UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and has the following characteristics:

8.5 mil minimum thickness,

ASTM D-3005, “Standard Specification for Low-Temperature Resistant Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape – Type 1.”

Rated 600 volts and 105 ºC, suitable for indoor and outdoor applications.

Retains flexibility, adhesion, and applicable at temperature ranges from 0 through 100 ºF without loss of physical or electrical properties.

Resistant to abrasion, moisture, alkalis, acid, corrosion, and sunlight.

Manufacturer: 3M “Scotch Super 88”

Provide heat shrinkable tubing that meets the requirements of UL 486D – Sealed Wire Connector Systems and has the following characteristics:

Rated 600 volts

Factory applied adhesive/sealant

Split resistant

Manufacturer: 3M “ITCSN”

Use motor lead splicing kits to insulate and seal connections to leads for motors rated 480V and less. Manufacturer: 3M “5300 Series”

WIRE PULLING LUBRICANT

Provide NRTL-listed wire pulling lubricant that is compatible with the conductor insulation or jacket, has a maximum coefficient of dynamic friction of 0.25, and leaves no flammable residue. For cold weather installations, provide wire pulling lubricant suitable for conduit temperature.

Compatibility with conductor insulation shall be determined in accordance with IEEE Std 1210, Standard Tests for Determining Compatibility of Cable-Pulling Lubricants with Wire and Cable.

Manufacturer:

For conduit temperature above freezing: Polywater “Lubricant J.”

For conduit temperature below freezing: Polywater “Lubricant WJ.”

EXECUTION

  - EXAMINATION

Verify interior of building has been protected from weather.

Verify that work of other trades likely to damage wire and cable is completed.

Verify raceway installation is complete and supported.

Verify that field measurements are as shown on Drawings.

Wire and cable routing shown on Drawings is approximate unless dimensioned.

Route wire and cable as required meeting project conditions.

Where cable routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet Project conditions.

PREPARATION

Examine raceways and building finishes that are to receive wires and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.

Completely and thoroughly swab raceway before installing wire.

Do not handle or pull cables that are colder than +14 degrees F. Store cold cables for at least 24 hours in a heated building prior to installation.

*************************************************************************************************************

Delete the following article when existing construction is not affected.

*************************************************************************************************************

EXISTING WORK

Remove abandoned wire and cable, including abandoned wire and cable above accessible ceiling finishes. Patch surfaces where removed cables pass through building finishes.

Disconnect abandoned circuits and remove circuit wire and cable. Remove abandoned boxes when wire and cable servicing boxes are abandoned and removed. Install blank cover for abandoned boxes not removed.

Provide access to existing wiring connections remaining active and requiring access. Modify installation or install access panel.

Extend existing circuits using materials and methods as specified.

Building Wire Installation

Install building wire according to, the NEC, the requirements in this Section, and the following NECA installation standards as applicable:

NECA 1 Standard for Good Workmanship in Electrical Construction (ANSI).

*************************************************************************************************************

Delete the following article if aluminum building wire is not used. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger.

*************************************************************************************************************

NECA/AA 104 Recommended Practice for Installing Aluminum Building Wire and Cable (ANSI).

Do not damage conductor, insulation, or jacket by excessive installation pulling tension or sidewall bearing pressure.

Calculate expected cable pulling tension and sidewall bearing pressures for each set of conductors being pulled into a conduit run where any of the following combinations of bends and raceway length is exceeded between accessible pull points:

4 equivalent 90-degree bends and 10 feet of raceway.

3 equivalent 90-degree bends and 40 feet of raceway.

2 equivalent 90-degree bends and 80 feet of raceway.

1 equivalent 90-degree bend and 150 feet of raceway.

Straight pull with more than 250 feet of raceway.

For cable pulling tension and sidewall bearing pressure calculations use formulas and factors described in IEEE Std 422, IEEE Guide for the Design and Installation of Cable Systems in Power Generating Stations.

Obtain recommended maximum conductor or cable pulling tension and sidewall bearing pressure values from the manufacturer, or use the following maximum allowable values:

Maximum sidewall bearing pressure: 500 lb/ft.

Maximum tension, pulling directly on conductor: 0.008 lb/cmil

Maximum tension, pulling on basket grip over insulation jacket: 2000 lb, not to exceed 0.008 lb/cmil of conductor.

Use a tension measuring device to monitor pulling force on runs where cable pulling calculations indicate installation stresses may exceed 80 percent of allowable pulling tension or sidewall bearing pressure.

Record the maximum measured pulling tension for each monitored cable pull.

Submit the recorded cable pulling tension for each monitored cable pull and the corresponding calculated allowable pulling tension.

*************************************************************************************************************

Edit the following Article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

Use a tension measuring device to monitor pulling force on each pull of conductors for critical systems where a pulling winch is used. Record and submit the maximum measured pulling tension for each cable pull.

Use solid copper conductors for power circuits 10 AWG and smaller except use stranded conductors in flexible conduits.

Use stranded conductors for power circuits 8 AWG and larger.

Use copper conductors not smaller than 12 AWG for power and lighting branch circuits.

Use stranded copper conductors not smaller than 14 AWG for 120V control circuits.

Use minimum 10 AWG copper conductors from panelboard to first outlet for 20-ampere, 120-volt branch circuits longer than 75 feet; use larger conductors as indicated on the Drawings.

Use minimum 10 AWG copper conductors from panelboard to first outlet for 20-ampere, 277-volt branch circuits longer than 150 feet; use larger conductors as indicated on the Drawings.

*************************************************************************************************************

Delete the following two articles if aluminum building wire is not used on the Project. There may be cases where the required compression connectors are not compatible with the termination point or there is insufficient wire bending space to use the connectors.

*************************************************************************************************************

Use AA8000 aluminum conductors 1/0 AWG and larger only at locations indicated on the Drawings. Use copper conductors for all critical systems.

Where it is necessary to use copper conductors instead of the aluminum conductors indicated on the Drawings, provide copper conductors with equal or greater ampacity based on the 75°C column in NEC Table 310.16.

Do not “through-pull” conductors at boxes, fittings or cabinets where a change of raceway alignment occurs.

Install wiring at outlets with at least 6 inches of slack conductor at each outlet.

*************************************************************************************************************

Delete the following article when Type MC Cable is not used. Note that use of Type MC Cable at LANL is restricted to International Building Code “Business Group B” occupancy. Refer to Section D5020 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

TYPE MC CABLE INSTALLATION

Install MC cables according to NECA 120, Standard for Installing Armored Cable (AC) and Metal-Clad Cable (MC) (ANSI), the NEC, and requirements in this Section.

Route MC cables to meet Project conditions.

For branch circuits serving multiple outlets use conduit for the “homerun” from the first outlet or junction box to the branch circuit panelboard; use Type MC cables for branch circuit wiring beyond the first outlet or junction box.

Use Type MC cables in interior, dry locations that are classified by the International Building Code as “Business Group B” occupancy where they will be concealed above ceilings, in dry-wall partitions, in equipment enclosures, or below raised floors. Type MC cables may be installed exposed in dedicated electrical rooms and mechanical rooms if they will not be exposed to physical damage or deteriorating agents.

Install and support Type MC cables as required in Article 330 of the NEC. Use NRTL listed spring steel MC cable supports or UV resistant plastic tie wraps to support Type MC cables; do not use wire to support Type MC cables.

Connector Installation

Install conductors in terminals, splices, adapters, and connectors in accordance with the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Make splices, taps, and terminations to carry full ampacity of conductors with no perceptible temperature rise above the conductor temperature.

Do not nick conductors when removing insulation.

Do not cut conductor strands to fit into connectors, splices, adapters, or terminals.

Make connections using clean connection surfaces. Wire brush conductors immediately before installing lugs, terminals, splices, or adapters.

Connect conductors 1/0 AWG and larger using compression terminals at the locations described below where there is adequate wire bending space to accommodate compression terminals. Select compression terminals suitable for the conductor sizes, materials, and termination point configurations. Install compression terminals using the manufacturer’s recommended dies and minimum 12-ton force compression tools.

Circuit breakers with frame size greater than 100 amperes that are NRTL listed for with compression terminals. Use compression adapters where the circuit breaker is not listed for compression terminals.

Safety switches and fused switches rated more than 100 amperes.

Transformers; refer to Section 26 2213, “Low-voltage Distribution Transformers.”

Switchgear, switchboards, panelboards, busway, motor control centers, and similar service and distribution equipment.

Utilization equipment connections that are NRTL listed for with compression terminals.

Install copper conductors, 1/0 AWG and larger, connected using mechanical lugs, in the locations or conditions described below.

Connection points not NRTL-listed for either compression terminals or compression adapters.

Where there is insufficient wire bending space to accommodate either compression terminals or compression adapters.

100 ampere frame circuit breakers.

30, 60, and 100 ampere safety switches.

Terminate power conductors smaller than 1/0 AWG using mechanical lugs.

Terminate control conductors using crimp-on terminals or ferrules. Do not place stranded conductors directly under terminal screws. Install terminals or ferrules on conductors using ratchet-type compression tools.

Connect outlets and components to wiring and to ground as indicated and instructed by manufacturer. Tighten connectors and terminals, including screws and bolts, according to equipment manufacturer's published torque-tightening values for equipment connectors. Where manufacturer's torque requirements are not indicated, tighten connectors and terminals according to tightening torques specified in UL Standard 486A-486B.

INSULATING TAPE AND TUBING Installation

Install insulating tape and tubing in accordance with the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Insulate splices and taps of irregular shapes with manufactured insulating covers or insulating tape built up to not less than 150 percent of insulation rating of conductor.

Apply varnished cambric tape over connections where re-entry is likely, such as motor lead connections.

Use rubber insulating tape in half-lapped layers to develop the basic insulation over splices and taps.

Use vinyl plastic tape in half-lapped layers to provide the outer protective covering over splices and taps.

Insulate cylinder shaped splices and taps, connector barrels and adapter barrels using heat shrinkable insulating tubing, insulating covers manufactured for the connector, or tape insulation as described above.

Identification

Identify wire and cable under provisions of Section 26 0553, Identification for Electrical Systems.

Identify each conductor with its circuit number or other designation indicated on Drawings.

Apply color coding tape on conductors at each termination, splice, junction, and pull box.

Post conductor color code on each panelboard, switchboard, switchgear assembly, motor control center, dry-type transformer, safety switch, and separate motor controller. Use type-written, adhesive-backed labels

FIELD QUALITY CONTROl

Observe conductors and cables during the installation process.

Reject and replace entire reels, rolls, or boxes containing conductors or cables with material or manufacturing defects.

Reject and replace cable or conductor segments that have been kinked, dented, or otherwise damaged during handling or installation.

After installation of wires and cables and before electrical circuit is energized, show product capability and compliance with requirements and verify by documented inspections and tests.

Perform the following inspections:

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type,

Correct color coding and identification.

Inspect connections for:

Correct connector size and type according to the Specifications,

The use of the correct compression dies and the correct number of crimps on compression connectors in accordance with the connector manufacturer’s instructions.

Perform the following tests:

Before connecting conductors to equipment, use a megohm meter in a 1-minute test to verify the insulation integrity of each service conductor, feeder conductor, critical system branch circuit conductor, and critical system control conductor with respect to ground and other conductors in the same raceway.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms notify the LANL Subcontract Technical Representative and investigate the conductor installation.

After connecting conductors to equipment, test continuity and correct connection of each power circuit conductor and each control circuit conductor.

Measure and record the tightness of not less than 10% of each size and type of mechanical or bolted connection using a calibrated torque wrench or torque screwdriver.

Compare measured torque with torque recommended by the connector manufacturer or UL Standard 486A-486B.

If any connection is found to be less than 90% of the recommended torque, notify the LANL Subcontract Technical Representative and re-torque all bolted connections on the Project.

Remove and replace defective, incorrect, or improperly installed conductors and connectors. Re-inspect and re-test replacement conductors and connectors.

Submit test and inspection records to the LANL Subcontract Technical Representative.

*************************************************************************************************************

Delete the following article if formal electrical acceptance testing is not required. Refer to Section D5000 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

Refer to Section 26 0813, Electrical Acceptance Testing for other inspections and tests that are required before conductors may be energized.

END OF SECTION

*********************************************************

Do not delete the following reference information:

http://engstandards.lanl.gov/

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0519, Rev. 4, dated May 6, 2009.