SECTION 26 0519

LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

*******************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*******************************************************************************************************

GENERAL

SECTION INCLUDES

*************************************************************************************************************

Edit article to match Project requirements. Delete items not applicable to Project.

*************************************************************************************************************

Building wire (600 V)

Metal-clad cable (600 V)

Wire and cable connectors

Insulating tape and tubing

Wire pulling lubricant

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for components and installation.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).  If listed products are unavailable, contact LANL Electrical Safety Office via STR for instructions.

Calibrated tools and test instruments used shall be maintained and calibrated in accordance with NETA ATS.

*************************************************************************************************************

Edit the following article to match project conditions. Delete if there are no critical systems.

*************************************************************************************************************

Definitions

Critical System. The following are critical systems:

Safety Class systems

Safety Significant systems

Fire pump systems covered in NEC Article 695

Emergency power systems covered in NEC Article 700

Legally required standby power systems covered in NEC Article 701

Critical operations power systems covered in NEC Article 708

*************************************************************************************************************

Edit the following article to match project conditions.

*************************************************************************************************************

ACTION SUBMITTALS

Certification of the Subcontractor’s tool and instrument calibration program.

*************************************************************************************************************

Edit the following article to match project conditions.

*************************************************************************************************************

CLOSEOUT SUBMITTALS

Submit the following in accordance with the provisions of Section 01 7839 Project Record Documents:

Field Test Records:

Tool and instrument calibration records.

Termination torque records.

Cable pulling records.

Field Quality Control inspection reports and tests results.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500 Substitution Procedures.

  - BUILDING WIRE

Provide NRTL-listed building wire as shown on the Drawings with the following characteristics:

Description: Single conductor 600 V insulated wire.

Conductor:

*************************************************************************************************************

Edit the following two articles to match project conditions. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger. If aluminum conductors will not be used, delete the information within brackets. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] 98% conductivity, annealed, uncoated copper, ASTM B 3 Standard Specification for Soft or Annealed Copper Wire, solid or stranded as specified in Part 3 of this Section.

[Where indicated on the Drawings for conductors 1/0 AWG and larger: AA 8000 series aluminum alloy registered in ASTM B 800 Standard Specification for 8000 Series Aluminum Alloy Wire for Electrical Purposes—Annealed and Intermediate Tempers, compact stranded in accordance with ASTM B 801 Standard Specification for Concentric-Lay-Stranded Conductors of 8000 Series Aluminum Alloy for Subsequent Covering or Insulation.]

Insulation: The following types, rated 600 volts:

*************************************************************************************************************

Edit the following two articles to match project conditions. Use thermoset (XHHW-2) conductor insulation for all branch circuits and feeders for Safety Class, Safety Significant, NEC Article 695, NEC Article 700, NEC Article 701, and NEC Article 708 systems. Thermoset insulation may also be needed for wiring in high temperature or high radiation environments. If these systems or conditions do not exist on this Project, delete the information within brackets. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] Type THHN/THWN-2 per UL Standard 83, “Thermoplastic-Insulated Wires and Cables.”]

[Where indicated on the Drawings: Type XHHW-2 per UL Standard 44, “Thermoset-Insulated Wires and Cables.”]

*************************************************************************************************************

Edit the following Article to match Project requirements. If the project is construction of a new facility the following applies.  Delete if not applicable to Project.

*************************************************************************************************************

Color-code conductors in facilities as follows:

Use colored insulation for color coding conductors 6 AWG and smaller.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.  Manufacturer: 3M “Scotch 35"

Provide black conductor insulation where colored tape is used for color coding.

Use the following color codes for AC power system conductors:

|  | System Type |
| --- | --- |
| Conductor | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground | 120/240V |
| Phase A | Brown | Black | Black | Black |
| Phase B | Orange | Red | Red | Red |
| Phase C | Yellow | Blue | Blue | --- |
| Grounded (Neutral) | Gray | White | White White/Red* | White White/Blue* |
| Equipment Grounding | Green | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow | --- |
| Switched | Purple or color of feeding circuit with labels: S1, S2… | Pink or color of feeding circuit with labels: S1, S2… | --- | Blue |

* Provide grounded conductor insulation with colored stripe when installed in any raceway, box, or enclosure with wiring of another system voltage.

** Caution:  The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom; color-code the conductors by phase as noted in the table.

Use the following color codes for DC power system conductors:

Positive:	Red

Negative:	Black

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

*************************************************************************************************************

If Project is an addition or modification to an existing facility, then the following applies.  Delete if not applicable.

*************************************************************************************************************

Color-code conductors in existing facilities as follows:

Use colored insulation for color coding conductors 6 AWG and smaller.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.

Manufacturer: 3M “Scotch 35"

Provide black conductor insulation where colored tape is used for color-coding.

Use the following color codes for AC power system conductors:

*************************************************************************************************************

Edit the following: Design engineer shall complete the following table to identify the existing facility's color code requirements. Delete if not applicable to Project.

*************************************************************************************************************

|  | System Type |
| --- | --- |
| Conductor | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground | 120/240V |
| Phase A |  |  |  |  |
| Phase B |  |  |  |  |
| Phase C |  |  |  |  |
| Grounded (Neutral) |  |  |  |  |
| Equipment Grounding | Green | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow | --- |
| Switched |  |  |  |  |

* Provide grounded conductor insulation with colored stripe when installed in any raceway, box, or enclosure with wiring of another system voltage.

** Caution:  The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom; color-code the conductors by phase as noted in the table.

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

Note: In existing facilities, in order to maintain rotation, it is sometimes necessary to swap two conductors in a three-phase feeder.  In this situation, the color code of the line side of the conductors will be different from the color code on the load side of the conductors.

*************************************************************************************************************

Type MC cable may be used in IBC Business Group B occupancies for branch circuit wiring systems. Refer to Section D5020 in the LANL Engineering Standards for additional information. Delete this article when metal-clad cable is not used.

*************************************************************************************************************

  - METAL-CLAD CABLE

Provide metal-clad cable (Type MC) that complies with UL Standard 1569 – Metal-Clad Cables, the NEC, and this Section.

Provide MC cables with quantities and sizes (minimum 12 AWG, maximum 2 AWG) of conductors as indicated on the Drawings.

Metal-clad cable shall consist of 600 V THHN insulated copper circuit conductors, an insulated copper equipment grounding conductor, a Mylar wrapping around the conductor bundle, and a close-fitting aluminum or galvanized steel outer sheath.

Provide metal-clad cables with conductors solid or stranded as specified in Part 3 of this Section.

Provide metal-clad cables with conductors colored to match the color codes for AC power system conductors as specified in Part 2 of this Section.

Metal-clad cables used to supply isolated-ground branch circuits shall have a neutral conductor, isolated ground conductor and equipment grounding conductor.  Identify each isolated ground conductor with a yellow-colored stripe on the green insulation.

Metal-clad cables used to supply multiple branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral conductor for each circuit, and one equipment ground conductor per cable.  Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.

Metal-clad cables used to supply multiple isolated-ground branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral and isolated ground conductor for each circuit, and one equipment ground conductor per cable.  Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.  Uniquely identify each isolated-ground conductor with one or more yellow-colored stripes on the green insulation.

Manufacturer: AFC Cable Systems Inc.

Provide NRTL-listed, insulated-throat or insulating-bushing connectors for Type MC cables.

Manufacturers:  Arlington Industries “SNAP2IT” or O-Z/Gedney ETP “Speed-Lock,” “AMC,” “KC,” or “PK” as appropriate for MC cable diameter.

  - WIRING CONNECTORS

For splices and taps on copper wire, sizes 12 to 10 AWG solid and 12 to 6 AWG stranded, use push-on, insulated, spring type connectors, or twist on connectors with helical coiled spring rated 600 V and 105 ºC that are NRTL-listed to UL 486C Splicing Wire Connectors and provide a means of visual inspection of the connection.

Manufacturer:

IDEAL “In-Sure.”

IDEAL “Twister Series”

3M “Scotchlock”

Wago “773 Series”

For splices and taps on copper wire, sizes 6 AWG through 1 AWG, use the following materials:

Tin-plated copper split-bolt connectors that meet the requirements in UL 486A-486B, Wire Connectors; provide with matching 600-volt snap-on insulating cover.

Manufacturer: FCI Burndy “Type KSA” with “Type SC” insulating cover.

Multi-tap connectors that meet the requirements of UL 486A-466B that have two or more range-taking mechanical lugs and matching 600-volt insulated cover.

Manufacturers: Burndy ‘POLYTAP” or “UNITAP”, Ilsco “Type PCT”, Blackburn “AMT.”

For wire, sizes 12 AWG and larger, use UL 486A-486B listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, copper or a copper alloy, and marked “CU”, “AL-CU” or “CU-AL” Manufacturers: FCI Burndy, Ilsco, or Thomas & Betts.

*************************************************************************************************************

Edit the following article to match project conditions. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger. If aluminum conductors will not be used, delete the information within brackets. *************************************************************************************************************

For aluminum wire, sizes 1/0 AWG and larger, use UL 486A-486B listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, and marked “AL”, “AL-CU” or “CU-AL”. Manufacturer: FCI Burndy, Ilsco, or Thomas & Betts.

For control wiring use nylon insulated crimp-on terminals with insulation grip that meet the requirements of UL 486A-486B. Manufacturer: 3M “Scotchlok MNG,” Thomas & Betts “Sta-Kon.”

Use ring tongue terminals for nutted studs.

Use flanged fork terminals for barrier terminal blocks.

Use pin terminals or ferrules for DIN type terminal blocks.

Insulation-piercing type connectors are not acceptable for power or control wiring.

  - INSULATING TAPE AND TUBING

Insulate taped splices and connections using ethylene propylene rubber (EPR) tape that meets the requirements of UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and is rated for 90ºC continuous operation and 130ºC short-term overload service. Manufacturer: 3M “Scotch 130C”

For the outer covering of tape-insulated splices and connections use vinyl plastic tape that meets the requirements of UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and has the following characteristics:

8.5 mil minimum thickness,

ASTM D-3005, “Standard Specification for Low-Temperature Resistant Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape – Type 1.”

Rated 600 volts and 105ºC, suitable for indoor and outdoor applications.

Retains flexibility, adhesion, and applicable at temperature ranges from 0 through 100ºF without loss of physical or electrical properties.

Resistant to abrasion, moisture, alkalis, acid, corrosion, and sunlight.

Manufacturer: 3M “Scotch Super 88”

Provide heat shrinkable tubing that meets the requirements of UL 486D – Sealed Wire Connector Systems and has the following characteristics:

Rated 600 volts

Factory applied adhesive/sealant

Split resistant

Manufacturer: 3M “ITCSN”

Use motor lead splicing kits to insulate and seal connections to leads for motors rated 480V and less. Manufacturer: 3M “5300 Series”

WIRE PULLING LUBRICANT

Provide NRTL-listed wire pulling lubricant that is compatible with the conductor insulation or jacket, has a maximum coefficient of dynamic friction of 0.25, and leaves no flammable residue. For cold weather installations, provide wire pulling lubricant suitable for conduit temperature.

Compatibility with conductor insulation shall be determined in accordance with IEEE Standard 1210, Standard Tests for Determining Compatibility of Cable-Pulling Lubricants with Wire and Cable.

Manufacturer:

For conduit temperature above freezing: Polywater “Lubricant J.”

For conduit temperature below freezing: Polywater “Lubricant WJ.”

EXECUTION

  - EXAMINATION

Verify interior of building has been protected from weather.

Verify that work of other trades likely to damage wire and cable is completed.

Verify raceway installation is complete and supported.

Field verify dimensions shown on Drawings.

Wire and cable routing shown on Drawings is approximate unless dimensioned.

Route wire and cable as required meeting project conditions.

Where cable routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet Project conditions.

PREPARATION

Examine raceways and building finishes that are to receive wires and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.

Swab raceway before installing wire.

Do not handle or pull cables that are colder than +14 degrees F. Store cold cables for at least 24 hours in a heated building prior to installation.

*************************************************************************************************************

Delete the following article when existing construction is not affected.

*************************************************************************************************************

EXISTING WORK

Remove abandoned wire and cable, including abandoned wire and cable above accessible ceiling finishes. Patch surfaces where removed cables pass through building finishes.

Disconnect abandoned circuits and remove circuit wire and cable. Remove abandoned boxes when wire and cable servicing boxes are abandoned and removed. Install blank cover for abandoned boxes not removed.

Provide access to existing wiring connections remaining active and requiring access. Modify installation or install access panel.

Extend existing circuits using materials and methods as specified.

Determine and record the existing power distribution system phase rotation, ABC clockwise or ABC counterclockwise.  Maintain the existing phase rotation throughout the new installation.

Building Wire Installation

Install building wire according to, the NEC, the requirements in this Section, and the following NECA installation standards as applicable:

NECA 1 Standard for Good Workmanship in Electrical Construction (ANSI).

*************************************************************************************************************

Delete the following article if aluminum building wire is not used. Refer to LANL ESM Chapter 7 Section D5010 paragraph 2.10.2 for conditions under which aluminum conductors may be used for services and feeders 1/0 AWG and larger.

*************************************************************************************************************

NECA/AA 104 Recommended Practice for Installing Aluminum Building Wire and Cable (ANSI).

Do not “through-pull” conductors at boxes, fittings or cabinets where a change of raceway alignment occurs.

Do not damage conductor, insulation, or jacket by excessive installation pulling tension or sidewall bearing pressure.

Use a tension measuring device to monitor pulling force on conductors 1/0 AWG and larger where any of the following combinations of bends and raceway length is exceeded between accessible pull points:

4 equivalent 90-degree bends and 10 feet of raceway.

3 equivalent 90-degree bends and 40 feet of raceway.

2 equivalent 90-degree bends and 80 feet of raceway.

1 equivalent 90-degree bend and 150 feet of raceway.

Straight pull with more than 250 feet of raceway.

*************************************************************************************************************

Edit the following paragraph to match Project requirements. Delete if not applicable.

*************************************************************************************************************

Use a tension measuring device to monitor pulling force on each pull of conductors for critical systems where a pulling winch is used. Record and submit the maximum measured pulling tension for each cable pull.

Record the maximum measured pulling tension for each monitored cable pull.

Obtain recommended maximum conductor or cable pulling tension and sidewall bearing pressure values from the manufacturer, or use the following maximum allowable values:

Maximum sidewall bearing pressure: 500 lb/ft.

Maximum tension, pulling directly on conductor: 0.008 lb/cmil

Maximum tension, pulling on basket grip over insulation jacket: 2000 lb, not to exceed 0.008 lb/cmil of conductor.

Submit the recorded cable pulling tension for each monitored cable pull and the corresponding maximum allowable pulling tension.

Notify the LANL Subcontract Technical Representative of any conductor pull where the maximum measured pulling tension exceeded 80 percent of maximum allowable pulling tension or sidewall bearing pressure Replace the conductors where the maximum measured pulling tension exceeded 100 percent of maximum allowable pulling tension or sidewall bearing pressure.

Use solid copper conductors for power circuits 10 AWG and smaller except use stranded conductors in flexible conduits.

Use stranded conductors for power circuits 8 AWG and larger.

Use copper conductors not smaller than 12 AWG for power and lighting branch circuits.

Use stranded copper conductors not smaller than 14 AWG for 120V control circuits.

For 20-ampere, 120-volt branch circuits longer than 75 feet use minimum 10 AWG copper conductors from panelboard to first outlet. Use larger conductors as indicated on the Drawings.

For 20-ampere, 277-volt branch circuits longer than 150 feet, use minimum 10 AWG copper conductors from panelboard to first outlet. Use larger conductors as indicated on the Drawings.

Install wiring at outlets with at least 6 inches of slack conductor at each outlet.

*************************************************************************************************************

Delete the following two articles if aluminum building wire is not used on the Project. There may be cases where the required compression connectors are not compatible with the termination point or there is insufficient wire bending space to use the connectors.

*************************************************************************************************************

Use AA8000 aluminum conductors 1/0 AWG and larger only at locations indicated on the Drawings. Use copper conductors for all critical systems.

Where it is necessary to use copper conductors instead of the aluminum conductors indicated on the Drawings, provide copper conductors with equal or greater ampacity based on the 75°C column in NEC Table 310.16.

*************************************************************************************************************

Delete the following article when Type MC Cable is not used. Note that use of Type MC Cable at LANL is restricted to International Building Code “Business Group B” occupancy. Refer to Section D5020 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

TYPE MC CABLE INSTALLATION

Install MC cables according to NECA/NEIS 120, Standard for Installing Armored Cable (AC) and Metal-Clad Cable (MC) (ANSI), the NEC, and requirements in this Section.

Route MC cables to meet Project conditions.

For branch circuits serving multiple outlets use conduit for the “homerun” from the branch circuit panelboard to the first outlet or junction box. Use Type MC cables for branch circuit wiring beyond the first outlet or junction box.

Use Type MC cables in interior, dry locations where they will be concealed above ceilings, in dry-wall partitions, in equipment enclosures, or below raised floors. Type MC cables may be installed exposed in dedicated electrical rooms and mechanical rooms if they will not be exposed to physical damage or deteriorating agents.

Install and support Type MC cables as required in Article 330 of the NEC. Use NRTL listed spring steel MC cable supports or UV resistant tie wraps to support Type MC cables; do not use wire to support Type MC cables.

Connector Installation

Install conductors in terminals, splices, adapters, and connectors in accordance with the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Make splices, taps, and terminations to carry full ampacity of conductors with no perceptible temperature rise above the conductor temperature.

Do not nick conductors when removing insulation.

Do not cut conductor strands to fit into connectors, splices, adapters, or terminals.

Make connections using clean connection surfaces. Wire brush conductors immediately before installing lugs, terminals, splices, or adapters.

Terminate all power conductors using mechanical lugs.

Terminate control conductors using crimp-on terminals or ferrules. Do not place stranded conductors directly under terminal screws. Install terminals or ferrules on conductors using ratchet-type compression tools.

*************************************************************************************************************

Edit the following paragraph to match Project requirements. Delete if not applicable.

*************************************************************************************************************

In new facilities the power distribution system’s phase rotation shall be ABC clockwise.  This phase rotation shall be maintained throughout the power distribution system.  Make or correct connections at rotating equipment input terminal to ensure proper equipment rotation.

*************************************************************************************************************

Edit the following paragraph to match Project requirements. Delete if not applicable.

*************************************************************************************************************

In existing facilities the power distribution system’s phase rotation shall match the existing phase rotation.  This phase rotation shall be maintained throughout the additions to the power distribution system.  Make or correct connections at rotating equipment’s input terminals to ensure proper equipment rotation.

Terminate wiring on outlets and components as indicated on the drawings or per the manufacturer’s instructions.

The LANL STR shall be given 2 weeks written, advance-notice of the date and time when the torqueing of connectors and terminals, including screws and bolts in major electrical distribution equipment will be performed. Major electrical distribution equipment includes: transformers, switchgear, switchboards, MCCs, panelboards, disconnect switches, motors greater than 10HP, receptacles sized greater than 50A.  The LANL STR or his /her representative shall witness the torqueing.

Tighten connectors and terminals, including screws and bolts, to manufacturers published torque-tightening values using a calibrated torque wrench or torque screwdriver.

Where manufacturer's torque-tightening values are not indicated, tighten connectors and terminals to torque-tightening values specified in UL Standard 486A-486B.

Provide a tabulated torqueing record.  This shall include as a minimum:

      - The torque values applied to all connectors and terminals,

      - The identification of the torque tools used,

      - The torque tools next calibration due date,

      - The person making each termination,

      - Signing and dating by the person(s) performing the torqueing.

      - The report will be signed and dated by the STR or STR representative witnessing the torqueing.

INSULATING TAPE AND TUBING Installation

Install insulating tape and tubing in accordance with the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Insulate splices and taps of irregular shapes with manufactured insulating covers or insulating tape built up to not less than 150 percent of insulation rating of conductor.

Use rubber insulating tape in half-lapped layers to develop the basic insulation over splices and taps.

Use vinyl plastic tape in half-lapped layers to provide the outer protective covering over splices and taps.

Insulate cylinder shaped splices and taps, connector barrels and adapter barrels using heat shrinkable insulating tubing, insulating covers manufactured for the connector, or tape insulation as described above.

Identification

Identify wire and cable under provisions of Section 26 0553, Identification for Electrical Systems.

Identify each conductor with its circuit number or other designation indicated on Drawings.

Apply color coding tape on conductors at each termination, splice, junction, and pull box.

Post conductor color code on each panelboard, switchboard, switchgear assembly, motor control center, dry-type transformer, safety switch, and separate motor controller. Use type-written, adhesive-backed labels

FIELD QUALITY CONTROl

The LANL STR shall be given 2 weeks, written advance-notice of the date and time when inspection and testing required by this section will be conducted. At the discretion of the LANL STR, any of the following tests or inspections may be witnessed by the STR or STR representative.

Pre-installation Inspection and Tests

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type,

For conductors 1/0 and larger, use a megohm meter in a 1-minute test to verify the insulation integrity of the conductors while still on the reel. Record all test results.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms consult the LANL Subcontract Technical Representative for further direction.

Reject and replace entire reels, rolls, or boxes containing conductors or cables with material or manufacturing defects.

Observe conductors and cables during the installation process.

Reject and replace cable or conductor segments that have been kinked, dented, or otherwise damaged during handling or installation.

After installation of wires and cables, perform the following inspections and tests:

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type,

Correct color coding and identification.

Before energizing the circuit, perform the following and tests:

Before connecting conductors to equipment, use a megohm meter in a 1-minute test to verify the insulation integrity of each service conductor, feeder conductor, critical system branch circuit conductor, and critical system control conductor with respect to ground and other associated conductors in the same cable or raceway.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms consult the LANL STR for further direction.

After connecting conductors to equipment, inspect connections for correct connector size and type.

Measure and record torque pass/fail of not less than 10% of each size and type of connector and terminal using a calibrated torque wrench or torque screwdriver.

Compare measured torque with torque with the torque-tightening values indicated by the manufacturer or specified in UL Standard 486A-486B.

If any connection is found to be less than the recommended torque, notify the LANL STR and re-torque the connection.  Record the torque-tightening values for connections that were re-torqued.

If more than 50% of the tested connections are found to be less than the recommended values the LANL STR shall require all bolted connections on the Project to be redone.

Remove and replace defective, incorrect, or improperly installed conductors and connectors. Re-inspect and re-test replacement conductors and connectors.

Submit test and inspection records to the LANL STR.

*************************************************************************************************************

Delete the following paragraph if formal electrical acceptance testing is not required. Refer to Section D5000 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

Refer to Section 26 0813, Electrical Acceptance Testing for other inspections and tests that are required before conductors may be energized.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

THIS REFERENCE FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0519 Rev. 5, dated June 22, 2015.