SECTION 26 0529

Hangers and supports for electrical systems

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

*************************************************************************************************************

*************************************************************************************************************

Hangers and supports addressed in this Section are “non-structural’ and are intended support very light loads and are typically exempt from being “designed anchors.” To be exempt from requiring a designed anchor, an electrical component must meet one of the following criteria:

1.	It is a PC-0 electrical component.

2	It is a PC-1 electrical component with flexible connections between the component and associated conduit, busway, wireway, etc. and also meets any of the following conditions:

a.	Component is mounted at 4 ft or less above a floor level and weighs 400 lb or less, or

b.	Component weighs 20 lb or less, or

c.		Is a distribution system (e.g. conduit) that weighs 5 lb/ft or less.

3.	It is a PC-1 or PC-2 conduit that is 2-1/2” trade size or smaller.

4.	It is a trapeze-supported assembly of PC-1 or PC-2 conduits with a total weight (including conductors) of 10 lb/ft or less.

If the project includes electrical components exceeding the above criteria, a designed anchor is required for each such component. The anchors must be designed for the seismic forces and relative displacements defined in ASCE 7, and construction details for each anchorage must be shown on the Drawings and specified in Section 26 0548 - Vibration and Seismic Controls for Electrical Systems.

All post-installed concrete and masonry anchors for use in non-structural applications must be chosen from qualified anchors in compliance with the IBC and ESM Chapter 16, IBC Program.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

    - Furnish and install, hangers, supports, anchors, concrete bases, and other positive fastenings for non-structural electrical components such that gravity loads are safely transferred to the structure.

*************************************************************************************************************

Edit the following article to match project requirements; delete if no electrical systems or components on the Project require vibration or seismic controls (designed anchors).  Electrical components that require designed anchors include the following:

Battery racks and battery cabinets: All

Cable trays: All

Conduits:

All PC-4 and PC-3 conduits.

Individually supported PC-2 and PC-1 conduits larger than 2-1/2 inches.

Trapeze supported PC-2 and PC-1 conduits with and aggregate weight exceeding 10 lb/ft.

Enclosed bus assemblies: All

Enclosed circuit breakers and safety switches:

All PC-4, PC-3, and PC-2 enclosed circuit breakers and safety switches.

All PC-1 enclosed circuit breakers and safety switches weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 enclosed circuit breakers and safety switches weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Enclosed controllers:

All PC-4, PC-3, and PC-2 enclosed controllers.

All PC-1 enclosed controllers weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 enclosed controllers weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Engine-generators: All

Luminaires:

All luminaires that weigh more than 20 lb.

All luminaires mounted above designated exit pathways.

All emergency luminaires and exit signs.

Motor control centers: All

Motors:

All PC-4, PC-3, and PC-2 motors.

All PC-1 motors weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 motors weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Paging system speaker assemblies:

All PC-4, PC-3, and PC-2 paging system speaker assemblies.

All PC-1 paging system speaker assemblies that weigh more than 20 lb.

All paging system speaker assemblies mounted above designated exit pathways.

Panelboards:

All PC-4, PC-3, and PC-2 panelboards.

All PC-1 panelboards weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 panelboards weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Switchboards: All

Switchgear: All

Transformers:

All PC-4, PC-3, and PC-2 transformers.

All PC-1 transformers weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 transformers weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Uninterruptible power supplies: All

Unit substations: All

Variable frequency motor controllers:

All PC-4, PC-3, and PC-2 variable frequency motor controllers.

All PC-1 variable frequency motor controllers weighing more than 20 lb that are mounted more than 4 ft above a floor level.

All PC-1 variable frequency motor controllers weighing more than 400 lb that are mounted 4 ft or less above a floor level.

Wireways: All

In addition, ASCE-7 requires designed anchors for:

Supports that are cantilevered up from the floor.

Supports that include bracing to limit deflection.

Supports that are constructed as rigid welded frames.

Attachments into concrete using nonexpanding inserts.

Attachments into concrete using power-actuated fasteners.

Attachments into concrete using cast iron embedments.

Attachments using spot welds, plug welds, or minimum size welds as defined by AISC.

*************************************************************************************************************

Vibration and Seismic Controls

    - Refer to Section 26 0548 - Vibration and Seismic Controls for Electrical Systems for hangers, supports, vibration isolation, concrete bases, and seismic control for electrical components identified on the Drawings as having vibration isolators or seismic designed anchors or braces.

QUALITY ASSURANCE

    - Furnish and install hangers and supports that conform to the requirements of the following codes and standards:

NFPA 70, National Electric Code (NEC)

IBC, International Building Code

NECA 1, Standard Practices for Good Workmanship in Electrical Contracting

Metal Framing Manufacturers Association

MFMA-4, Metal Framing Standards Publication

MFMA-102, Guidelines for the Use of Metal Framing

    - Where a Nationally Recognized Testing Laboratory (NRTL) has requirements for such products, provide products that are NRTL listed and labeled for the application, installation condition, and the environment in which installed.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

SUBMITTALS

    - Submit the following in accordance with the provisions of Section 01 3300 Submittal Procedures.

Catalog Data: Submit catalog data for each type of product specified.  Include information substantiating equivalent corrosion resistance to zinc coated steel of alternative treatment, finish, or inherent material characteristic.

Test reports: Submit ICC Evaluation Service, Inc evaluation report for each post-installed concrete or masonry anchor product showing that it complies with the current edition of the IBC and the intended conditions of use.

Receiving, Storing and Protecting

    - Receive, store, and protect, and handle products according to NECA 1.

PRODUCTS

  - Substitutions

    - Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

COATINGS and Materials

    - Furnish products for use indoors protected with zinc coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic.

    - Furnish products for use outdoors or in damp or corrosive indoor locations with hot-dip galvanized coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or material such as stainless steel with inherent corrosion resistant characteristics.

RACEWAY SUPPORTING DEVICES

    - Furnish supports as described below for the installation of raceway systems.

    - Use pressed steel, single bolt hangers to support individual RGS, IMC or EMT conduits from threaded rods or beam clamps.  Manufacturer:  Steel City “6H Series”.

    - For individual runs of EMT up to 1-inch trade size above accessible ceilings, use spring steel conduit clips with positive snap closure.  Manufacturer: ERICO CADDY “M Series”.

    - Use malleable iron conduit clamps to secure individual RGS, IMC or EMT conduit runs across, parallel, or perpendicular to beams, channels and angle supports.  Manufacturer: Steel City “RC, EC, and PC Series”.

    - Use two-piece carbon steel riser clamps for individual vertical conduits passing through floors.  Manufacturer: Kindorf “C-210 Series”.

    - Use snap-on type one-hole steel straps to secure individual conduits up to 2-inch trade size to flat, dry interior surfaces.  Manufacturer: T&B “1210 Series” for RGS and IMC and “4100 Series” for EMT.

    - Use one-hole malleable iron straps to secure individual conduits up to 4-inch trade size to flat, dry interior surfaces.  Manufacturer: T&B “1275 Series”.

    - Use one-hole malleable iron straps and conduit spacers to secure individual conduits to flat exterior or damp flat interior surfaces.  Manufacturer: T&B “1275 Series” straps with 1350 Series” spacers.

    - Support multiple parallel horizontal conduits with trapeze hangers fabricated from framing channel materials specified below.

OUTLET BOX SUPPORTING DEVICES

    - Furnish pre-fabricated sheet steel brackets to support outlet boxes from metal studs in dry-wall construction.

    - Single outlet boxes: Provide brackets that are inset to allow for dry-wall ring and have a far-side support leg.  Manufacturer: ERICO CADDY “H Series” or “MEB1” attached with “SMS8” low-profile self-tapping screws.

    - Multiple outlet boxes: Provide brackets that are inset to allow for dry-wall rings and span from stud to stud.  Manufacturer: ERICO CADDY “RBS Series”  attached with “SMS8” low-profile self-tapping screws

HANGER RODS

    - Furnish mild steel rods that conform to ASTM A 307, Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength.

    - Furnish rods that are threaded on both ends, threaded on one end, or continuous threaded with UNC (coarse) thread pitch.

## Fasteners

    - Pre-set Concrete Inserts

Furnish pre-set concrete inserts as shown on the Drawings.

Manufacturers:

Continuous inserts for wood forms: B-Line “B22I-12” or longer.

Spot inserts for wood forms or metal decks: B-Line “B2500” with “N2500” nut, “B2501”

    - Post-installed Concrete Anchors

Furnish post-installed concrete anchors as shown on the Drawings.

Each post-installed anchor shall have an ICC-ES evaluation report stating that the product is compliant with the current edition of the IBC and the intended conditions of use.

For applications in outdoor, damp, or corrosive locations furnish stainless steel post installed anchors.

Furnish post-installed expansion, adhesive, and undercut anchors specified in Section 03 1534 Post Installed Concrete Anchor Purchase – Normal Confidence.

Powder-actuated threaded studs: Use zinc-plated carbon steel or stainless steel suitable for the intended service:

        - 1/4-20 threaded stud: Manufacturer: Hilti X-W6

        - 3/8-16 threaded stud: Manufacturer: Hilti W10

Concrete and masonry screw anchors: Heat-treated carbon steel. Manufacturer: Simpson Strong-Tie “Titen HD”.

    - Beam Clamps: NRTL-listed, or compliant with Federal Specification WW-H-171E, or compliant with Manufacturers’ Standardization Society SP-69 and SP-58.

    - Hollow Wall Anchors: All steel-spring head type toggle bolts.

FRAMING CHANNEL SYSTEMS

    - Furnish U-channel framing systems that conform to MFMA-4 and are fabricated using minimum 12-gage steel, with 9/16-inch-diameter holes, from 1-1/2 to 1-7/8 inches on center, in the surface opposite the “U” opening.

    - Furnish fittings and accessories that mate and match with U-channel and are of the same manufacturer. Use two-piece, single bolt type conduit straps on U-channel supports.

    - Manufacturers: Unistrut, B-Line, Superstrut.

FABRICATED SUPPORTING DEVICES

    - Furnish shop- or field-fabricated supports or manufactured supports assembled from U-channel components.

    - Furnish steel brackets fabricated from angles, channels, and other standard structural shapes.  Connect with welds and machine bolts to form rigid supports.

EXECUTION

  - GENERAL

    - Install hangers and supports according to the NEC, IBC, NECA 1, the requirements in this Section, and specific supporting requirements in other Sections.

    - Conform to manufacturer's instructions and recommendations for selection and installation of hangers and supports.

    - Do not use wire or perforated strap for permanent supports.

    - Install flexible sections in electrical conduits and raceways where they cross expansion joints and where they connect to equipment with seismic controls or vibration isolators. Refer to Section 26 0533 - Raceways and Boxes for Electrical Systems.

    - Do not support conduits, boxes, raceways, etc. from ceiling suspension wires.

EXAMINATION

    - Examine surfaces to receive hangers and supports for compliance with installation tolerances and other conditions affecting performance of the system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

FASTENERS

    - Pre-set inserts: Install pre-set inserts for anchoring to reinforced concrete slabs, sides of reinforced concrete beams, and reinforced concrete walls.

    - Post-installed concrete expansion anchors: Install in accordance with Section 03 1550, Post Installed Concrete Anchors - Installation and Testing and the product’s ICC-ES report conditions of use.

    - Masonry screw anchors: Use in accordance with NECA 1 and the product’s ICC-ES report conditions of use.

    - Powder-actuated threaded studs:

      - Use only to fasten individual conduits 2-1/2 inches trade size and smaller.

      - Install in accordance with the product’s ICC-ES report conditions of use and the manufacturer’s instructions using recommended tools and loads.

      - Use only in uncracked concrete or concrete masonry units.

      - Install to provide embedment as indicated on the Drawings.

    - Hollow wall anchors: Use toggle bolts in accordance with NECA 1.

    - Use wood screws for fastening to wood construction.

    - Use beam clamps or machine bolts, nuts, and washers for fastening to metal.

    - The use of lead-cinch drop in anchors is not allowed.

    - Torque threaded fasteners as recommended by the manufacturer’s instructions.

RACEWAY SUPPORTS.

    - Install individual and multiple (trapeze) raceway hangers and riser clamps as necessary to support raceways.  Provide U-bolts, clamps, attachments, and other hardware necessary for hanger assembly and for securing hanger rods and conduits.

    - Support three or more parallel runs of horizontal raceways together on trapeze hangers.

    - Support individual horizontal raceways by separate pipe hangers.

    - Do not support conduits from ceiling suspension wires.

BOXES AND CABINETS

    - Support sheet metal boxes directly from the building structure, or by approved brackets or bar hangers, as shown on the Drawings or as required.  Where bar hangers are used, attach the bar to structure on opposite sides of the box.

    - In open overhead spaces, cast boxes threaded to raceways need not be supported separately except where used for fixture support.

    - Install surface-mounted cabinets and panelboards as shown on the Drawings or as required.

Framing Channel Systems

    - Select and install framing channel systems in accordance with MFMA-103.

    - Use framing channel to support electrical equipment that is mounted free of walls.

    - Use framing channel to support equipment mounted on walls that do not have sufficient strength to resist pull-out or wallowing out of equipment mounting bolts.

*************************************************************************************************************

Edit the following article to match project conditions; delete if there is no floor-mounted electrical equipment, Concrete bases must be designed by the Engineer of Record based on the properties of the load to be supported, the properties of the supporting structure, the required anchor bolt embedment lengths, etc. Construction details and dimensions for concrete bases must be shown on the Drawings.

*************************************************************************************************************

CONCRETE BASES

    - Install a reinforced concrete base for each piece of floor-mounted electrical equipment. Refer to Section 03 3001, Reinforced Concrete, for materials and installation requirements.

Form concrete equipment bases using framing lumber with form release compounds.

Construct concrete bases as shown on the Drawings and not less than 3.5 inches high and not less than 4 inches larger in both directions than the supported equipment.

Place pre-set anchors, conduits, and sleeves using the equipment manufacturer's installation template or instructions. Install post-installed anchors in accordance with FASTENERS article above.

Place concrete and provide a steel trowel finish on top; chamfer top edges and corners.

    - Cure concrete not less than seven days before installing equipment.

HANGER RODS

*************************************************************************************************************

Coordinate the following article with the Drawings.  Delete if there is no suspended equipment.

*************************************************************************************************************

    - Use minimum 3/8-inch diameter threaded rod; use larger diameter rod as indicated on the Drawings, in other Sections, or in the supported equipment manufacturer’s installation instructions.

PAINTING

*************************************************************************************************************

Coordinate the following article with the Drawings; delete if there is no requirement for painting. Coordinate painting with project architect.

*************************************************************************************************************

    - Paint hangers and supports to match finish of adjacent surfaces.

    - Refer to Section 09 9100 Painting for materials and installation requirements.

END OF SECTION

*************************************************************************************************************

Do not delete the following reference information.

*************************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0529 Rev. 2, dated June 4, 2009.