SECTION 26 0536

Cable Trays for electrical systems

*******************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

*******************************************************************************************************

GENERAL

Section Includes

Metal cable tray and fittings.

Firestopping and sealing of cable tray through-penetrations.

LANL PERFORMED WORK

None

SUBMITTALS

Submit the following in accordance with Project submittal procedures:

Catalog Data:

Submit manufacturer's data on cable tray including, but not limited to, types, materials, finishes, rung spacing, inside depths and fitting radii.

Submit manufacturer's data on fire stop products.

Test Reports: Provide results of tests performed or witnessed by an independent testing laboratory of the "worst case" loading conditions outlined in this specification and performed in accordance with the latest revision of NEMA VE-1; including test reports verifying rung load capacity in accordance with NEMA VE-1 Section 5.4.

********************************************************************************************************

Edit list match project requirements. Shop drawings may not be warranted for simple cable tray installations. Shop drawings are necessary when access to cable tray must be coordinated with adjacent architectural, structural, mechanical and electrical elements.

*******************************************************************************************************

Shop Drawings:  Detail fabrication and installation of cable tray, including plans and sections of components and attachments to other construction elements.  Designate components and accessories, including clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings.  Include floor plans and sections drawn to scale.  Include scaled cable tray layout and relationships between components and adjacent architectural, structural, mechanical and electrical elements.

Installation Instructions:  Indicate application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements.  Include instructions for storage, handling, protection, examination, preparation, and installation of Product.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if no cable tray on the Project is designated with an Ip greater than 1.0.

*************************************************************************************************************

Certification: Submit certification and backup information that cable tray systems with Ip greater than 1.0 can perform required functions after a design earthquake as specified in "SERVICE CONDITIONS" below. Refer to Section 26 0548 – Vibration and Seismic Controls for Electrical Systems.

REGULATORY REQUIREMENTS

Conform to requirements of the National Electrical Code (NEC) for components and installation.

Conform to applicable requirements of NEMA VE1 – Metal Cable Tray Systems and NEMA VE2 – Metal Cable Tray Installation Guidelines.

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) as suitable for purposes specified and shown.

  - SERVICE CONDITIONS

Provide metal cable tray and accessories that will perform satisfactorily in any combination the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

International Building Code seismic criteria:

Seismic Design Category = D

SDS = spectral acceleration, short period = 0.75 g

SD1 = spectral acceleration, 1-second period = 0.64g

ap = component amplification factor = 1.0 for rigidly mounted cable trays and 2.5 for suspended cable trays.

Rp = component response modification factor = 2.5 for rigidly nounted cable trays and 6.0 for suspended cable trays.

Ip = Component importance factor
Ip = 1.5 for life safety related components such as emergency systems
Ip = 1.5 for safety class or safety significant systems
Ip = 1.0 for all other applications

COORDINATION

Coordinate cable tray, hangers, and accessories with other construction that penetrates ceilings or floors or is supported by them, including light fixtures, HVAC equipment and ductwork, fire-suppression system, and partition assemblies.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction and NECA/NEMA 105 Recommended Practice for Installing Metal Cable Tray Systems.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500 –Substitution Procedures.

  - Metal CABLE TRAY

Provide metal cable tray and accessories conforming to NEMA VE-1, the NEC, and this Section.

Cable trays shall be of types, classes and sizes indicated on the Drawings or specified, complete with splice plates, bolts, nuts and washers for connecting units.

**********************************************************************************************************

Edit the following article to match project conditions.

**********************************************************************************************************

Cable tray shall be capable of carrying not less than the following uniformly distributed and concentrated loads at the rated support span with a safety factor of 1.5 when supported as a simple span and tested per NEMA VE1 Section 5.2.  Load and safety factors are applicable to both side rails and rung capacities.

6 and 12 inch widths: 50 lb. per linear foot plus a 200 lb. load at mid-span.

18 and 24 inch widths: 75 lb. per linear foot plus a 200 lb. load at mid-span.

30 and 36 inch widths: 100 lb. per linear foot plus a 200 lb. load at mid-span.

**********************************************************************************************************

Edit the following article to match project conditions. Delete materials not used on the project. If more than one material is needed, the Drawings should clearly indicate material requirements. Aluminum alloy cable tray can be used for most indoor and outdoor applications. Use pre-galvanized steel cable tray for indoor, non-corrosive environments where greater strength or longer spans are required. Use hot-dip galvanized cable tray for non-chemical industrial outdoor and indoor applications. Use stainless steel cable tray for severe chemical environments.

***********************************************************************************************************

Materials and finish:

Aluminum: Straight section and fitting side rails and rungs extruded from aluminum alloy.

Pre-galvanized Steel: Straight sections, fitting side rails, rungs, and covers made from steel meeting the minimum structural properties and mill galvanized in accordance with ASTM A653 coating designation G90.

Hot-dip Galvanized Steel: Straight section and fitting side rails and rungs made from steel meeting the minimum structural properties and hot-dip galvanized after fabrication in accordance with ASTM A123.  All covers and splice plates must also be hot-dip galvanized after fabrication; mill galvanized covers are not acceptable for hot-dipped galvanized cable tray.  Inspect hot-dip galvanized after fabrication steel cable trays after coating and remove excess zinc.

Stainless Steel: Straight section and fitting side rails and rungs made of AISI Type 304 or Type 316 stainless steel. Transverse members (rungs) or corrugated bottoms welded to the side rails with Type 316 stainless steel welding wire.

***********************************************************************************************************

Edit the following article to match project conditions. Delete cable tray types not used. If more than one cable tray type is needed, clearly indicate requirements on the Drawings.

***********************************************************************************************************

Type of tray system:

***********************************************************************************************************

Edit the following article to match project conditions. Delete rung spacings not used on the project. If more than one rung spacing is needed, the Drawings should clearly indicate material requirements. Use 6-inch rung spacing for small telecommunications and control cables. Use 9 inches or greater rung spacing for power cables.

**********************************************************************************************************

Ladder type trays shall consist of two longitudinal members (side rails) with transverse members (rungs) welded to the side rails. Rung spacing shall be [6] [9] [12] [18] inches on center. Spacing in radiused fittings shall not exceed 9 inches measured at the center of the tray's width.

Ventilated trough type trays shall consist of two longitudinal members (side rails) with a corrugated bottom welded to the side rails. To provide ventilation in the tray, the valleys of the corrugated bottom shall have rectangular holes punched along the width of the bottom.

Solid bottom trough type trays shall consist of two longitudinal members (side rails) with a corrugated bottom welded to the side rails.

**********************************************************************************************************

Edit the following article to match project conditions. Delete cable tray sizes not used on the project. If more than one cable size type is needed, the Drawings should clearly indicate requirements.

**********************************************************************************************************

Tray dimensions:

Cable tray usable load depth shall be [3] [4] [5] [6] inches minimum, or as noted on the Drawings.

Straight tray sections shall have side rails fabricated as I-beams or C-sections. Supply straight sections in standard [10] [12] [20] [24] feet lengths, except where shorter lengths are needed to facilitate tray assembly lengths shown on Drawings.

Cable tray width shall be [6] [9] [12] [18] [24] [30] [36] inches or as shown on Drawings.

Fittings shall have a minimum inside radius of [12] [24] [36] inches.

***********************************************************************************************************

Edit the following article to match project conditions. Delete materials not used on the project. ***********************************************************************************************************

Use bolted type splice plates made as indicated below for each tray type. The resistance of fixed splice connections between adjacent sections of tray shall not exceed 0.00033 ohms. Splice plate construction shall be such that a splice may be located anywhere within the support span without diminishing rated loading capacity of the cable tray.

Aluminum Tray: Splice plates shall be made of aluminum alloy with four square neck carriage bolts and serrated flange locknuts.  Hardware shall be zinc plated in accordance with ASTM B633, SC1.  If aluminum cable tray is to be used outdoors then hardware shall be Type 316 stainless steel.

Steel (including Pre-galvanized and Hot-dip galvanized):  Splice plates shall be manufactured of high strength steel, meeting the minimum mechanical properties of ASTM A1011 HSLAS, Grade 50, Class 1.  Attach each splice plate with four ribbed neck carriage bolts with serrated flange locknuts.  Hardware shall be zinc plated in accordance with ASTM B633 SC1 for pre-galvanized cable trays, or Chromium Zinc in accordance with ASTM F-1136 for hot-dip galvanized cable trays.

Place cable tray supports so that the support spans do not exceed span ratings of cable tray sections.

Construct trapeze supports from 12 gauge steel formed shape channel members 1-5/8 inches by 1-5/8 inches with necessary hardware.

Support cable trays installed adjacent to walls on wall mounted brackets.

Center hung supports shall be manufactured of 12 gauge, 1-5/8 inches by 1-5/8 inches steel strut with a pipe welded at the middle of the support to provide eccentric loading stability. Support shall withstand 700 pounds in a 60 percent vs. 40 percent eccentric loading condition with a safety factor of 3.

Use 1/2 inch (minimum) diameter threaded rods to support trapeze hangers and center-hung supports.

Install a warning label with the following message on each cable tray section and fitting:

WARNING: DO NOT USE CABLE TRAY AS A WALKWAY LADDER OR SUPPORT. USE ONLY AS MECHANICAL SUPPORT FOR CABLES AND TUBING.

Provide barrier strips as indicated on the Drawings. Fasten barrier strips into the tray with self-drilling screws.

Furnish accessories as shown on the Drawings and as required to protect, support, and install a cable tray system and associated cables. Accessories include section splice plates, expansion plates, blind-end plates, ladder dropouts, and barriers.

Manufacturers: Chalfant, Cooper B-Line, Cope, MP Husky

  - CABLE TRAY GROUND CLAMPS

Use NRTL listed cable tray ground clamps suitable for use with aluminum cable tray and copper equipment grounding conductor.

Manufacturer: O-Z/Gedney “Type CTGC”, Crouse-Hinds “TGC40”

  - CABLE TRAY/CONDUIT BONDING CLAMPS

Use NRTL listed clamps suitable for mechanically connecting and electrically bonding conduit to steel or aluminum cable tray.

Manufacturer: Thomas & Betts “6200 Series”, Crouse-Hinds “LCC Series”

*************************************************************************************************************

Edit the following article to match project conditions. Coordinate with LANL Construction Specification Section 07 8400 – Firestopping. Delete materials not used on the project. *************************************************************************************************************

  - Cable Tray Firestop

Provide cable tray firestop products, materials, and systems to perform the following functions:

Restore the integrity of all fire resistive walls or floor-ceiling assemblies that are penetrated by cable tray and cables to prevent the spread of heat, fire, gasses, and smoke.

*************************************************************************************************************

Edit the following two articles to match project conditions. These are for cable penetrations through walls or floor-ceiling assemblies where a seal must be established in addition to firestopping. Uses include:

- Seal boundaries of radiological areas that are penetrated by cable tray and cables to prevent the spread radiological contamination.

- Seal penetrations where cable trays and cables pass between areas where air pressure differential must be maintained.

Delete article(s) if not applicable to the project.

*************************************************************************************************************

Seal boundaries of radiological areas that are penetrated by cable tray and cables to prevent the spread radiological contamination.

Seal penetrations where cable trays and cables pass between areas where air pressure differential must be maintained.

Cable tray firestop products, materials, and systems shall meet the following performance and quality assurance requirements:

Conform to both flame and temperature ratings as required by nationally recognized testing laboratories per ASTM E814 or UL 1479 – Fire Tests of Through-Penetration Fire Stops a configuration that is representative of installation condition on this Project.

Be listed in the UL Fire Resistance Directory with a UL 1479 “F-rating” equal to the corresponding rating of the penetrated wall or floor-ceiling assembly.

Be capable of closing or filling through-openings created by the burning of combustible cable jacketing or movement of cable tray due to thermal expansion.

Be compatible with and appropriate for:

The cable tray dimensions and materials,

The cable sizes and jacket materials,

The materials and construction of the penetrated wall or floor, and

The environment at the installation location.

Allow future cable changes without damaging existing cables.

Not affect the electrical properties of power or communications cables

*************************************************************************************************************

Edit the following article to match project conditions. This system is for cable tray penetrations through framed walls. Delete if not applicable to the project.

*************************************************************************************************************

Cable Tray Firestop System for Framed Walls:

Cable tray firestop system shall be listed in the UL Fire Resistance Directory for use with fire-resistive framed walls consisting of drywall applied on metal studs.

Provide cable tray / multi-cable sealing system consisting of a two-piece steel enclosure, fixation plate, intumescent rubber sponge void fillers, fire-resistant gaskets, and fireproof sealant.

Provide metal housing suitable for the cable tray size and installation location environment: enameled steel for non-corrosive indoor environments, galvanized steel for wet or outdoor environments, stainless steel for corrosive environments.

Provide manufacturer’s weather shield fitting for each sealing system exposed to weather.

Manufacturer: CSD “FIRSTO.”

*************************************************************************************************************

Edit the following article to match project conditions. This system is for cable tray penetrations through concrete or masonry walls or through concrete floors. Delete if not applicable to the project.

*************************************************************************************************************

Cable Tray Firestop System for Concrete Floors and Concrete or Masonry Walls:

Cable tray firestop system shall be listed in the UL Fire Resistance Directory for use with fire-resistive concrete floor-ceiling assemblies and concrete or masonry walls.

Intumescent flexible blocks shall be based on two-component polyurethane foam that is free from dust, fibers, halogen, and solvents.

Blocks shall be soft, flexible, and reuseable,

Nominal dimensions shall be 8 inches x 5 inches x 2 inches.

It shall be possible to cut and shape blocks to suit irregular openings.

Intumescent firestop putty shall be non-hardening, re-useable, and shall contain no volatile solvents.

Manufacturer: Hilti “FS 657” fire block and “CP 618” or “CP 619” putty.

*************************************************************************************************************

Edit the following article to match project conditions. This system is for cable tray penetrations through walls or floor-ceiling assemblies where a seal must be established in addition to firestopping. Uses include:

- Seal boundaries of radiological areas that are penetrated by cable tray and cables to prevent the spread radiological contamination.

- Seal penetrations where cable trays and cables pass between areas where air pressure differential must be maintained.

Delete article if not applicable to the project.

*************************************************************************************************************

Multi-cable transit system firestop system shall be listed in the UL Fire Resistance Directory for use with fire-resistive floor-ceiling assemblies and walls.

System shall provide a penetration seal to contain conditioned air and to restrict the entrance of contaminants into clean areas.

System shall consist of the required number and size mounting frames, elastomer sealing modules to fit around each cable and close openings, plus accessories required for a complete system.

Manufacturer: Nelson “MCT” or “MPS”, Crouse-Hinds “TW Series”

Provide red and white self-adhesive labels, or plastic or metal plates stating as a minimum that the installation is a “through-penetration fire stop system,” and installation data (UL-Listed or FM-Approved configuration number, date installed, installer and organization).  Also state “Modify/remove only with LANL Fire Group approval” if space permits.  Examples of acceptable products:

Hilti sticker P/N 00339611

Hilti plate P/N 00306219

EXECUTION

  - EXISTING WORK

**********************************************************************************************************

Delete this article when existing construction is not affected.

**********************************************************************************************************

Remove abandoned cable tray, including associated hangers and accessories.

Maintain access to existing cable trays and other installations remaining active and requiring access. Modify installation or provide access panels.

Clean and repair existing cable trays and accessories to remain or to be reinstalled.

EXAMINATION

Examine spaces to receive cable tray for compliance with installation tolerances and other conditions affecting performance of the raceway system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

Cable Tray INSTALLATION

Install cable tray where indicated on the Drawings and according to manufacturer's instructions, NECA/NEMA 105 – Recommended Practice for Installing Metal Cable Tray Systems, and the NEC. Have the manufacturer’s instructions available at the construction site.

    - Provide not less than 12 inches of clear space above and to one side of cable trays to permit access for installing and maintaining cables.

    - Align cable trays to be parallel to column lines unless specifically shown otherwise on the Drawings.

*************************************************************************************************************

Cable tray requires designed anchors that comply with International Building Code and ASCE 7. Show locations and installation details of cable tray supports and anchors on the Drawings.

*************************************************************************************************************

    - Install supports and seismic anchorage for cable tray as shown on the Drawings.

      - Comply with the manufacturer’s installation instructions and the requirements of Section 26 0548 – Vibration and Seismic Controls for Electrical Systems.

      - Support cable tray independent of supports for other elements such as pipes, conduits, ceilings, ducts, and equipment enclosures.

Use minimum 1/2-inch threaded rods to support cable tray.

Locate cable tray fitting supports so they meet the strength requirements of straight sections. Install fitting supports per NECA/NEMA 105 and in accordance with manufacturer's instructions.

    - Install expansion splice plates and flexible bonding jumpers at locations where cable trays cross building expansion joints. Install at other locations so distance between expansion fittings does not exceed manufacturer's recommended distance between fittings.

    - Install a waterproof concrete curb at least 4 inches high around floor penetrations.

Grounding and Bonding

Ground and bond cable tray under provisions of Section 26 0526 – Grounding and Bonding for Electrical Systems.

Provide electrical continuity between tray components.

Use anti-oxidant compound to prepare aluminum contact surfaces before assembly.

Install not smaller than 6 AWG bare copper equipment grounding conductor along the entire length of tray; bond to each component using cable tray ground clamps. Place grounding conductor on the outside of one cable tray side rail and complete all bonds before placing any cables in the cable tray.

Make mechanical and electrical bond connection between conduits and cable tray using NRTL- listed cable tray/conduit bonding clamps.

FireStop Installation

Install firestop products in accordance with manufacturer’s instructions, the UL Fire Resistance Directory, and Section 07 8400 – Fire Stopping.

Install firestop products to restore the integrity of all fire-resistive walls or floor-ceiling assemblies that are penetrated by cable trays to prevent the spread of heat, fire, gasses, and smoke.

*************************************************************************************************************

Edit the following two articles to match project conditions. This system is for cable tray penetrations through walls or floor-ceiling assemblies where a seal must be established in addition to firestopping. Uses include:

- Seal boundaries of radiological areas that are penetrated by cable tray and cables to prevent the spread radiological contamination.

- Seal penetrations where cable trays and cables pass between areas where air pressure differential must be maintained.

Delete articles if not applicable to the project.

*************************************************************************************************************

Install firestop products to seal boundaries of radiological areas that are penetrated by cable tray cables to prevent the spread radiological contamination.

Install firestop products to seal penetrations where cable tray cables pass between areas where air pressure differential must be maintained.

LABELING

Install red warning labels with 1/2-inch white letters and the following message at visible locations 50 foot on centers on all cable trays in environmental or return air plenums:

USE ONLY PLENUM RATED CABLES IN THIS CABLE TRAY

Install white labels with 1/2-inch black letters and the following information at visible locations 50 foot on centers on all cable trays:

Maximum cable tray loading depth

Allowable cable load in pounds per foot based on the as-installed support span spacing and structural support capability.

Label fire barrier penetration seals on both sides of the penetrated fire barrier. Use labels per Part 2.

FIELD QUALITY CONTROL

Inspect accessible components for cleanliness, mechanical, and electrical integrity, and for presence of damage or deterioration before energizing.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

END OF SECTION

**********************************************************************************************************

Do not delete the following reference information.

**********************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0536 Rev. 2, dated October 1, 2009.