SECTION 26 2713

ELECTRICITY Metering

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

GENERAL

Section Includes

*************************************************************************************************************

Edit list match project requirements. Use the single-phase watt-hour meter for 120/240 V single phase services up to 200 amperes. Use the digital electrical power meter, test switches, and instrument transformers for three-phase services rated 800 amperes or less. Use the multi-function, digital electrical meter, test switches, and instrument transformers for three-phase services rated more than 800 amperes. Use the meter cabinets where the instrument transformers will not be installed within the service entrance switchboard or switchgear.

Coordinate the communications interface for digital electronic meters with the ES-DE Process and Automation Team. There are at least three different communications situations:

(1) A facility smaller than 10,000 sq ft with no foreseeable need for metering other utility services: specify Ethernet communications over the telecommunications system to the utility-maintained server.

(2) A facility larger than 10,000 sq ft that has no “building automation system” (BAS): specify an RS-485 connection to a LANL-furnished “LANL utilities standard meter/BAS interface” box.

(3) A facility that has a BAS: specify RS-485 connection to the BAS “building global controller.”

*************************************************************************************************************

Single-phase watt-hour meter and socket.

Digital electrical power meter

Multi-function, digital electrical meter

Test switches.

Instrument transformers.

Meter cabinets.

*************************************************************************************************************

Edit the following article match project requirements.

************************************************************************************************************

LANL PERFORMED WORK

LANL Utilities will inspect, test, program, and adjust the meter, meter wiring, Ethernet communication wiring, and Ethernet communications interface.

LANL ES-DE Process and Automation Team will inspect and test the RS-485 communication wiring and communications interface.

SUBMITTALS

Submit the following in accordance with project submittal procedures:

Catalog data and manufacturer's technical data, including data proving that materials comply with specified requirements.  Provide catalog sheets showing ratings, dimensions, and enclosure details.

Installation instructions indicating application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.

*************************************************************************************************************

Edit the following article match project requirements.

*************************************************************************************************************

Shop drawing of installation in [meter cabinets] [switchboard] [switchgear].

Wiring diagram showing connection of meter and display modules, instrument transformers, test switches, potential fuses, and communications circuits.

Operation and maintenance instructions.

REGULATORY REQUIREMENTS

Conform to requirements of the National Electrical Code (NEC).

Conform to requirements of ANSI C12.1 American National Standard Code for Electricity Metering.

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) as suitable for purposes specified and shown.

COORDINATION

*************************************************************************************************************

Edit the following article match project requirements. Delete A if metering will be installed in metering cabinets.

*************************************************************************************************************

Coordinate installation of metering components in the service entrance [switchboard][switchgear assembly].

Coordinate the features of the meter and associated instrument transformers with the ratings and characteristics of the circuit to be metered.

*************************************************************************************************************

Edit the following article match project requirements. Delete C socket-mounted single-phase watt-hour meter is installed.

*************************************************************************************************************

Coordinate connection of meter KYZ pulse output with the Integrated Automated Facility Controls described in Section 25 5000 with the controls Subcontractor.

Provide not less than 14 working days notice to LANL STR to arrange for LANL Utilities to inspect, program, and test the meter prior to Project final inspection.

EXTRA MATERIALS

Furnish one spare for every five installed fuses, but not less than one set of three of each size and type.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500, Substitution Procedures.

*************************************************************************************************************

Use the meter specified in the following article for 120/240 V single phase services up to 200 Amps. Delete article if there is no single-phase metering.

*************************************************************************************************************

Single-Phase WATT-HOUR METER and Socket

Provide a self-contained, electro-mechanical watt-hour meter that meets the requirements of ANSI C12.10 American National Standard for Electromechanical Watthour Meters and has the following characteristics:

Form: 2S

*************************************************************************************************************

Use Class 100 for 100 A services and Class 200 for 200 A services.

*************************************************************************************************************

Class: [100] [200]

*************************************************************************************************************

Use 15 A test current for Class 100 meters and 30 A test current for Class 200 meters.

*************************************************************************************************************

Test current: [15] [30] amps

Voltage: 240 volts, single phase.

Wires: 3

Register: 5 dial clock type.

Cover: Polycarbonate

Provide ringless-type meter socket for single-phase watt-hour meter.

Provide socket to accommodate [overhead] [underground] service.

Socket shall be suitable for outdoor installation.

Socket shall be rated 200 amps, 600 volts.

Socket shall have an integral lever bypass and jaw release.

Socket shall be NRTL listed to UL 414 Standard for Meter Sockets.

Manufacturers:

Meter: ABB “Type AB1".

Socket: Square D “Class 4131”

*************************************************************************************************************

Use the meter specified in the following article for Projects with three-phase services rated 800 amperes or less. Delete article if not applicable to the Project.

*************************************************************************************************************

DIGITAL ELECTRICAL Power METER

Provide a digital electrical power meter as indicated on the Drawings.  Meter shall meet the following standards:

Be NRTL listed to UL 508 Standard for Safety - Industrial Control Equipment.

Meet requirements of ANSI C12.16, American National Standard for Solid-State Electricity Meters.

Meet NEMA C12.20, Electricity Meters 0.2 and 0.5 Accuracy Classes, class 0.5S for energy revenue metering.

The meter shall sample current and voltage signals at a rate high enough to provide true-RMS metering accurate beyond the 30th harmonic.

The meter shall be rated for an operating temperature range of -25 degrees C to 70 degrees C

Meter shall have a current input withstand rating of 15 amperes continuous, 50 amperes for 10 seconds per hour and 500 amperes for 1 second per hour.

Setup parameters required for the meter shall be stored in non-volatile memory and retained in the event of a control power interruption.  Any battery used to provide non-volatile memory must be serviceable from the front of the meter.

The meter shall display the following metered values on a faceplate alphanumeric readout and shall auto range between Units, Kilo-Units, and Mega-Units.  The information shall be also available at a remote computer through a communications network:

Real-time readings (accuracy expressed as percent of reading):

Current: (±0.075 percent accuracy + 0.025% full scale) true RMS

Phases A, B, C

Voltage: (±0.075 percent accuracy + 0.025% full scale) true RMS

Phases A-B, B-C, C-A

Phases A-N, B-N, C-N

Power: (±0.15 percent accuracy + 0.025% full scale) true RMS

Real (watts)

Reactive (vars)

Apparent (VA)

Phases A, B, C, 3-phase total

Frequency: (±0.01 Hz) 45 to 67 Hz

Power Factor: (±0.002 percent accuracy)

3-phase total

Individual harmonics: magnitude and angle

% THD - Current:

Phases A, B, C

% THD - Voltage:

Phases A-B, B-C, C-A

Phases A-N, B-N, C-N

Energy Readings (accuracy expressed as percent of reading):

Real (kWh): (±0.5 percent accuracy)

3-phase total

Apparent (kVAh): ±0.5 percent accuracy

3-phase total

Demand readings:

Current (amperes):

Present

Peak

Real power (kW):

Present

Peak

Reactive power (kvar):

Present

Peak

Apparent power (kVA):

Present

Peak

Meter shall be capable of power demand calculations using either of the following user-selectable methods:

Thermal demand using a sliding window updated every 15 seconds with window length field selectable from 5 to 60 minutes in 5 minute increments.

Block interval with or without sub-intervals. Window length field selectable from 5 to 60 minutes in 5 minute increments. Sub-interval length field selectable from 5 to 60 minutes in 5 minute increments.

The meter shall maintain a user selectable combination of trend and event logging information in non-volatile memory. The information shall be available at a remote computer through a communications network. Minimum trend and logging capabilities shall be as follows:

1 billing log.

1 custom data log

Event log date and time stamped to seconds

Minimum and maximum of worst phase date and time stamped.

Alarm and maintenance logs.

The meter shall accept inputs from industry standard instrument transformers.

The meter shall allow potential connection to circuits up to 600 volts AC without the use of external potential transformers. External potential transformer ratios up to 500,000:120 VAC shall be supported.

Meter shall operate with AC or DC control power

115 to 415 Vac, 45 – 67 Hz.

125 to 250 Vdc

The meter shall be equipped with the following digital communications ports.

An RS-485 port that is capable of communicating over a twisted pair network using Modbus protocol.

Meter shall provide ANSI C12.1 KYZ output pulses that can be user-programmed for kWH, kVARH or kVAH. The value of a pulse shall be programmable, allowing control of the maximum pulse rate to meet the requirements of the receiving equipment.

Provide a separately mounted display with the following features:

High visibility alpha-numeric display to show metering data, min/max values, alarms, and inputs,

Pushbuttons to scroll through menus and select information to display.

Cable connection to the meter.

*************************************************************************************************************

Edit the following three articles to match project requirements. Coordinate communications requirements with the ES-DE Process and Automation Team. There are at least three different communications situations:

(1) A facility smaller than 10,000 sq ft with no foreseeable need for metering other utility services: retain the Ethernet communications module specification article below; in Part 3 specify connection of the meter’s Ethernet card to a telecommunications outlet.

(2) A facility larger than 10,000 sq ft that has no “building automation system” (BAS): delete the Ethernet communications module specification article below; in Part 3 specify connection of the meter’s RS-485 port to a LANL-furnished “LANL utilities standard meter/BAS interface” box.

(3) A facility that has a BAS: delete the Ethernet module specification article below; in Part 3 specify connection of the meter’s RS-485 port to the BAS “building global controller.”

*************************************************************************************************************

[Ethernet communications module capable of at least 10 Base T communications to TCP/IP networks using embedded HTML pages. Communications module shall have an available RS-485 port.]

Manufacturer:  Square D PM820RD Power Meter [and PM8ECC Ethernet  communications module]. No substitution.

*************************************************************************************************************

Use the meter specified in the following article for Projects with three-phase services rated greater than 800 amperes. Delete article if not applicable to the Project.

*************************************************************************************************************

MULTI-FUNCTION DIGITAL ELECTRICAL METER

Provide addressable multi-function, microprocessor-based, digital electrical meter(s) as indicated on the Drawings.  Meter shall meet the following standards:

Be NRTL listed to UL 508 Standard for Safety Industrial Control Equipment.

Meet requirements of ANSI C12.16, American National Standard for Solid-State Electricity Meters.

Meet NEMA C12.20, Electricity Meters 0.2 and 0.5 Accuracy Classes, class 0.5S for energy revenue metering.

The meter shall sample current and voltage signals at a rate high enough to provide true-RMS metering accurate beyond the 60th harmonic.

The meter shall be rated for an operating temperature range of -25 degrees C to 70 degrees C and have a current input withstand rating of 300 amps for 1 second.

Setup parameters required for the meter shall be stored in non-volatile memory and retained in the event of a control power interruption.  Any battery used to provide non-volatile memory must be serviceable from the front of the meter.

The meter shall display the following metered values on a faceplate alphanumeric readout and shall auto range between Units, Kilo-Units, and Mega-Units.  The information shall be also available at a remote computer through a communications network:

Real-time readings (accuracy expressed as percent of reading):

Current: ±0.20 percent accuracy, true RMS

Phases A, B, C, 3-phase average

Voltage: ±0.20 percent accuracy, true RMS

Phases A-B, B-C, C-A

3-phase average line-to-line

Phases A-N, B-N, C-N

3-phase average line-to-neutral

Power: ±0.40 percent accuracy, true RMS

Real (watts)

Reactive (vars)

Apparent (VA)

Phases A, B, C, 3-phase total

Frequency: ±0.04 percent accuracy

Power Factor: ±0.80 percent accuracy

Displacement

Apparent

Phases A, B, C, 3-phase total

% THD - Current: ±1.00 percent accuracy

Phases A, B, C, Neutral

% THD - Voltage: ±1.00% accuracy

Phases A-B, B-C, C-A

Phases A-N, B-N, C-N

K-Factor - Current: ±1.00% accuracy

Phases A, B, C, 3-phase total

Energy Readings (accuracy expressed as percent of reading):

Real (kWh): ±0.4% accuracy

Phases A, B, C, 3-phase total

Forward, reverse, net

Reactive (kvarh): ±0.4% accuracy

Phases A, B, C, 3-phase total

Forward, reverse, net

Apparent (kVAh): ±0.4% accuracy

Phases A, B, C, 3-phase total

Demand readings (accuracy expressed as percent of reading):

Current (amperes): ±0.4% accuracy

3-phase average

Last completed interval, peak

Real power (kW): ±0.4% accuracy

3-phase total

Last completed interval, peak

Reactive power (kvar): ±0.4% accuracy

3-phase total

Last completed interval, peak

Apparent power (kVA): ±0.4% accuracy

3-phase total

Last completed interval, peak

Meter shall be capable of power demand calculations using either of the following user-selectable methods:

Thermal demand using a sliding window updated every 15 seconds with window length field selectable from 5 to 60 minutes in 5 minute increments.

Block interval with or without sub-intervals. Window length field selectable from 5 to 60 minutes in 5 minute increments. Sub-interval length field selectable from 5 to 60 minutes in 5 minute increments.

The meter shall have disturbance detection and disturbance waveform capture and shall provide waveform captures of steady state voltage and current waveforms that can be transmitted to a remote PC for display and analysis using appropriate software.

Meter shall be capable of storing in non-volatile memory up to 30 cycles of each phase voltage and current sampled at a rate of 128 samples per cycle.

Meter shall initiate waveform capture either on manual command from a remote PC or by self-triggering due to an over/under condition.

The meter shall maintain a user selectable combination of trend and event logging information in non-volatile memory.  The information shall be available for local downloading or available at a remote computer through a communications network. Minimum trend and logging capabilities shall be as follows:

4 trend log files each capable of logging 24 parameters.

User selectable sampling rate for each log file

Internal storage capacity of 89000 date and time stamped logged data points.

Logging triggered by user-defined event or new maximum or minimum of metered value.

Minimum and maximum of each measured parameter with date and time.

Alarm and event log of 500 events.

The meter shall accept inputs from industry standard instrument transformers.

The meter shall allow potential connection to circuits up to 600 volts AC without the use of external potential transformers. External potential transformer ratios up to 500,000:120 VAC shall be supported.

Current transformer ratios up to 10,000:5 A shall be supported.

Meter shall operate with control power input from 110 to 240 VAC, 45 – 66 Hz.

Meter shall provide ANSI C12.1 KYZ output pulses that can be user-programmed for kWH, kVARH or kVAH. The value of a pulse shall be programmable, allowing control of the maximum pulse rate to meet the requirements of the receiving equipment.

Provide a separately mounted display with the following features:

High visibility alpha-numeric display to show metering data, min/max values, alarms, and inputs.

Pushbuttons to scroll through menus and select information to display.

An infrared data port with proximity sensor for use with an optical communications interface connected to a laptop computer.

Cable connection to the meter.

*************************************************************************************************************

Edit the following two articles to match project requirements. Coordinate communications requirements with the ES-DE Process and Automation Team. There are at least three different communications situations:

(1) A facility smaller than 10,000 sq ft with no foreseeable need for metering other utility services: retain the Ethernet port specification article below; in Part 3 specify connection of the meter’s Ethernet gateway to a telecommunications outlet.

(2) A facility larger than 10,000 sq ft that has no “building automation system” (BAS): delete the Ethernet port specification article below; in Part 3 connection of the meter’s RS-485 port to a LANL-furnished “LANL utilities standard meter/BAS interface” box.

(3) A facility that has a BAS: delete the Ethernet port specification article below; in Part 3 specify connection of the meter’s RS-485 port to the BAS “building global controller.”

*************************************************************************************************************

The meter shall be equipped with the following digital communications port[s].

An RS-485 port that is capable of communicating over a twisted pair network using Modbus or Jbus protocol.

[An RJ-45 Ethernet port that is capable of at least 10 Base T communications to TCP/IP-based networks using embedded HTML pages.]

Manufacturer:  Square D CM3350 meter with CMDVF display [and ECC21 communications module]. No substitution.

*************************************************************************************************************

Edit the following article to match Project requirements.  Adequate instrument transformers may exist in retrofit applications. Instrument transformers are not used with the specified single-phase meter. Delete this article if not needed.

*************************************************************************************************************

INSTRUMENT TRANSFORMERS

Provide current and potential transformers, conforming to NEMA EI 21.1 and ANSI C57.13, metering accuracy class 0.3, of suitable ratio and burden for specified metering.

Provide current transformers having 5 Amp secondary and a continuous current rating factor of not less than 1.33.

Provide two current transformers for 3-phase, 3-wire delta circuits.  Select current transformer primary to match circuit overcurrent device trip rating.

Provide three current transformers for 3-phase, 4-wire wye circuits.  Select current transformer primary to match circuit overcurrent device trip rating.

Current transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Current transformers for 13.8 kV circuits shall have 110 kV BIL.

Provide with window opening adequate for the conductors or bus bars.

*************************************************************************************************************

Edit the following articles to match Project requirements.  Select CT to match system voltage and current.

*************************************************************************************************************

Manufacturer: ABB

Type CMS, through 200:5 at 600 V or less.

Type CMF, through 1200:5 at 600 V or less.

Type CMV, through 3000:5 at 600 V or less.

Type CLC, through 4000:5 at 600 V or less.

Type CLE, through 5000:5 at 600 V or less.

Type KIR-11, indoors at 13.8 kV.

Type KOR-11, outdoors at 13.8 kV.

Type KON-11, outdoors at 13.8 kV.

*************************************************************************************************************

Edit the following article to match Project requirements.  The specified multi-function digital meter does not require potential transformers when connected to a 480Y/277 V system.

*************************************************************************************************************

Provide potential transformers having 120 VAC secondary.

Provide two potential transformers for 3-phase, 3-wire delta circuits.  Select potential transformer primary to match system line-to-line voltage.

Provide three potential transformers for 3-phase, 4-wire wye circuits. Select potential transformer primary to match system line-to-line voltage.

Potential transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Potential transformers for 13.8 kV circuits shall have 110 kV BIL.

*************************************************************************************************************

Edit the following article to match Project requirements.  Select PT to match system voltage.

*************************************************************************************************************

Manufacturer: ABB

Type VIZ-11 with 2 primary fuses for 13.8 kV system indoors

Type VOY-11 for 13.8 kV system outdoors

Type PPW for 480 V system

*************************************************************************************************************

Edit the following article to match Project requirements.  Adequate test switches and plugs may exist in retrofit applications. Test switches and plugs are not required with the specified single-phase meter. Delete this article if not needed.

*************************************************************************************************************

TEST SWITCHES AND PLUGS

Provide semi-flush mounted test switches in meter potential and current circuits to facilitate testing of the meter installation and also external connection of additional portable metering equipment.

Provide test switches that comply with ANSI C12.9 and automatically short circuit current transformer circuits when the switches are opened preparatory to inserting the test plug.

Test switch shall have potential and shorting type current poles as follows:

3 wire delta systems: 3 potential poles and 4 shorting type current poles.

4 wire wye systems: 4 potential poles and 6 shorting type current poles.

Provide plastic cover for each test switch.

Provide matching test plugs designed for in-service testing.

Manufacturers: States “Type FMS”.

3 wire delta systems: States FMS-07C

4 wire wye systems: States FMS-10C

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete if there is no three-phase metering.

*************************************************************************************************************

POTENTIAL CIRCUIT FUSES

Provide UL Class CC, time-delay, 600 V, 3-ampere fuses to protect each potential lead to the meter.

Provide each fuse with a cover having a blown-fuse indicator.

Manufacturer: Bussman “Type FNQ-R fuses, BC Series fuse blocks, and SAMI-7I fuse covers.”

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete on low-voltage systems.

*************************************************************************************************************

For indoor medium-voltage metering installations, protect the primary of each potential transformer with indoor, current-limiting, 1/2 Amp, 14,400 V fuses having blown fuse indication.  Manufacturer: S&C “Fusistor.”

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete on low-voltage systems.

*************************************************************************************************************

For outdoor medium-voltage metering installations, protect the primary of each potential transformer with outdoor, 1 Amp, 14,400 V power fuses.  Manufacturer: S&C “SMD-20 with SMU-20 fuse unit”.

WIRING AND TERMINATIONS

Use 12 AWG, THHN-THWN stranded copper, for current transformer secondary circuits that are less than 50 ft. Use 10 AWG, THHN-THWN stranded copper, for current transformer secondary circuits that are more than 50 ft.

Use 12 AWG, Type THHN-THWN, stranded copper, for potential transformer secondary circuits.

Use crimp-on, nylon insulated, insulation grip, brazed seam terminals for instrument wiring as follows:

Use ring tongue terminals for nutted studs.  Manufacturer: Burndy “Type TN”

Use flanged fork terminals for barrier terminal strips.  Manufacturer: Burndy “YAE-Z”.

Use pin terminals for DIN type terminal blocks.  Manufacturer: 3M “MNG-P”.

Use 18 AWG shielded, twisted pair, type CMP cable for RS-485 connections.

*************************************************************************************************************

Edit the following article to match Project requirements.  Use meter cabinets for retrofit applications or where there is insufficient space to mount the meter and test switches in the service entrance panelboard or switchgear.  Meter cabinet is not needed for a single-phase, socket-mounted meter. Delete article if not needed.

*************************************************************************************************************

METER CABINETS

Provide a metal current transformer (CT) cabinet with hinged door to house the meter test switches, fuse blocks, [potential transformers,] and current transformers.

Minimum cabinet size: 36” high, 30” wide, 11” deep.

Manufacturer: Hoffman A-363011HCT

Provide a meter cabinet with hinged door to house the meter module, display module, communications interfaces, and accessories.

Minimum cabinet size: 12” high, 12” wide, 6” deep.

Manufacturer: Hoffman A-12R126HCLO.

EXECUTION

*************************************************************************************************************

Delete the following article when existing construction is not affected.

*************************************************************************************************************

  - EXISTING WORK

Remove abandoned meters, including associated cabinets, instrument transformers and test blocks.

Maintain access to existing meters and other installations remaining active and requiring access. Modify installation or provide access panel.

Clean and repair existing meters and associated cabinets, instrument transformers and test blocks to remain or to be reinstalled.

EXAMINATION

Examine surfaces to receive meters and associated cabinets, instrument transformers and test blocks for compliance with installation tolerances and other conditions affecting performance of the raceway system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install metering equipment according to manufacturer's instructions.  Have the manufacturer’s installation instructions available at the construction site.

Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  Where manufacturer's torque values are not furnished, use those specified in UL 486A.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Identify meter, [test switches,] [instrument transformers,] and meter wiring according to Section 26 0553, Identification for Electrical Systems. [Install voltage and arc-flash warning labels on cover of instrument transformer cabinet.]

Ground meter and enclosure according to manufacturer’s instructions and Section 26 0526, Grounding and Bonding for Electrical Systems.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Support meter, [meter base,] [meter cabinet,] [instrument transformers] in accordance with Section 26 0529, Hangers and Supports for Electrical Systems, and the NEC.

*************************************************************************************************************

Use the following article when instrument transformers will NOT be installed within a service entrance switchboard or switchgear assembly. Provide sufficient space adjacent to the service entrance equipment for the CT cabinet and meter cabinet. Delete this article if not required.

*************************************************************************************************************

Install CT cabinet and meter cabinet adjacent to service entrance equipment.

Install 3/4” plywood backboard painted with two coats of fire-retardant paint in the CT cabinet.

Mount current transformers on plywood backboard in the CT cabinet; position transformers to minimize stress from power conductors.

Mount potential circuit fuse blocks on plywood backboard in the CT cabinet.

Recess mount meter test switches in current transformer CT cabinet door.

Locate meter cabinet so display is approximately 60 inches above the floor.

Install meter module, communications interfaces, and accessories on DIN rail in meter cabinet.

Mount meter display on meter cabinet door.

Interconnect metering components as indicated on the Drawings.

*************************************************************************************************************

Use the following article when instrument transformers will be installed within a service entrance switchboard or switchgear assembly. Coordinate this article with Section 26 2300 – Low-Voltage Switchgear or Section 26 2413 – Switchboards as applicable. Delete this article if not required.

*************************************************************************************************************

Install metering components within the electrical service entrance switchgear. Refer to [Section 26 2300 – Low-Voltage Switchgear][Section 26 2413 – Switchboards].

Install potential transformers and associated potential fuses in dedicated potential transformer compartment.

Install current transformers on main bus in accordance with switchgear manufacturer’s standard details.

Install meter in a dedicated metering compartment.

Recess mount meter test switches in switchgear metering compartment door.

Locate meter display on switchgear metering compartment door approximately 60 inches above the floor.

Interconnect metering components as indicated on the Drawings.

*************************************************************************************************************

Delete the following four articles if a single-phase, socket-mounted meter is used.

*************************************************************************************************************

Provide control power to meter in accordance with the manufacturer’s instructions.

Use a dedicated, fuse-protected, 120 volt circuit or a dedicated, fuse-protected, control power transformer if potential transformers are required for the metering voltage inputs.

Control power may be derived from the fuse-protected metering voltage inputs when potential transformers are not required.

Wire current and potential leads through test switch.

Install fuse protection in the potential leads on the line side of the test switch.

Use shorting-type switches for the current transformer leads.

*************************************************************************************************************

Edit the following articles to match project requirements. Coordinate communications requirements with the ES-DE Process and Automation Team. There are at least three different communications situations:

(1) A facility smaller than 10,000 sq ft with no foreseeable need for metering other utility services: specify connection of the meter’s Ethernet gateway to a telecommunications outlet.

(2) A facility larger than 10,000 sq ft that has no “building automation system” (BAS): specify connection of the meter’s RS-485 port to a LANL-furnished “LANL utilities standard meter/BAS interface” box using RS-485 cable in conduit.

(3) A facility that has a BAS: specify connection of the meter’s RS-485 port to the BAS “building global controller” using RS-485 cable in conduit.

*************************************************************************************************************

[Provide communications connection between the building telecommunications system and the Ethernet port associated with the meter.

Provide telecommunications outlet within the electrical room and as close as practical to the metering equipment or enclosure.

Install conduit pathway for communications cables from the [meter cabinet][switchboard or switchgear metering cubicle] to within 1 ft of the telecommunications outlet.

Install suitable communications cables and terminations.

Connect meter to telecommunications outlet using a CAT-6 cord.]

[Provide Modbus protocol communications connection between the building automation system and the RS-485 port on the meter.

Install conduit pathway for an RS485 cable from the [meter cabinet][switchboard or switchgear metering cubicle] to the [LANL-furnished “LANL utilities standard meter/BAS interface” box] [appropriate BAS cabinet]. Coordinate with the [controls subcontractor] [ES-DE Process and Automation Team].

Install an RS-485 cable from the RS-485 port on the meter to the [LANL-furnished “LANL utilities standard meter/BAS interface” box] [BAS cabinet].

Label the RS-485 cable and leave at least 6 ft of slack at both ends of the RS-485 cable for termination by the [controls Subcontractor] [ES-DE Process and Automation Team].]

FIELD QUALITY CONTROL

Inspect accessible components for cleanliness, mechanical, and electrical integrity, and for presence of damage or deterioration before energizing.

LANL Utilities will inspect, test, program, and adjust the meter, meter wiring, Ethernet communication wiring, and Ethernet communications interface.

LANL ES-DE Process and Automation Team will inspect and test the RS-485 communication wiring and communications interface.

Correct deficiencies in material, wiring, or installation that may be discovered.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

END OF SECTION

************************************************************************************

Do not delete the following reference information.

************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2713 Rev. 3, dated January 11, 2010.