SECTION 26 5100

iNTERIOR lIGHTING

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic:  In order to edit this section for job-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the Seismic Specification Guide for Nonstructural Components: Electrical Components (“Guide,” posted on LANL specs webpage) for guidance on properly editing this section.
*************************************************************************************************************

- GENERAL

  - SUMMARY

    - SECTION INCLUDES

*************************************************************************************************************

Edit to suit project requirements

*************************************************************************************************************

      - Interior luminaires and accessories

      - Lamps

      - Ballasts

    - DEFINITIONS:

      - Luminaire: A luminaire is a complete lighting unit including light source(s) and parts required to distribute the light, position and protect the light source(s), and connect the light source(s) to the power supply.

      - Average Life:  The time after which 50 percent will have failed and 50 percent will have survived under specified operating and starting condition.

      - Total harmonic distortion (THD): The root mean square (RMS) of all the harmonic components divided by the fundamental current.

  - RELATED SECTIONS

*************************************************************************************************************

Seismic: Refer to Guide for editing guidance.

- *************************************************************************************************************

    - Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements pertaining to [manufacturer’s certification] [and] [special certification].

    - Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

  - ACTION SUBMITTALS

    - Submit the following in accordance with project submittal procedures:

      - Catalog Data: Submit catalog data describing luminaires, including lamps and ballasts where applicable. Include data substantiating that materials comply with specified requirements.  Arrange data for luminaires in the order of fixture designation.

      - Performance Curves/Data:

        - Submit certified photometric data for each type of luminaire.

        - Submit supply-air, return-air, heat-removal, and sound performance data for air handling luminaires.

*************************************************************************************************************

Edit extra materials as necessary.  Delete items that do not apply to the project.

- *************************************************************************************************************

  - EXTRA MATERIALS

    - Furnish the following extra materials matching products installed.  Package with protective covering for storage and identify with labels describing contents.

      - Five (5) percent of quantity of fluorescent lamps of each type, but no fewer than two lamps of each type.

      - Five (5) percent of quantity of high intensity discharge (HID) lamps of each type, but no fewer than two lamps of each type.

      - One (1) percent of quantity of louvers and lenses of each type, but not less than one of each type.

      - One (1) percent of quantity of ballasts of each type, but not less than one of each type.

  - QUALITY ASSURANCE

    - Comply with the National Electrical Code (NEC) and the International Building Code (IBC) for installation requirements.

    - Provide luminaires listed and labeled by a nationally recognized testing laboratory (NRTL)

    - Use manufacturers that are experienced in manufacturing luminaires, lamps and ballasts similar to those indicated for this Project and have a record of successful in-service performance.

    - Coordinate luminaires, mounting hardware and trim with the ceiling system.

  - Service Conditions

    - Luminaires shall perform satisfactorily in the following service conditions:

      - Elevation: 7500 feet above sea level.

      - Ambient temperature limits: 32 to 104 degrees F unless indicated otherwise for specific products in Part 2.

  - Receiving, Storing and Protecting

    - Receive, store, and protect, and handle products according to the following NECA National Electrical Installation Standards:

      - NECA/IESNA 500, Recommended Practice for Installing Indoor Commercial Lighting Systems (ANSI).

      - NECA/IESNA 502, Recommended Practice for Installing Industrial Lighting Systems (ANSI).

- PRODUCTS

*************************************************************************************************************

Seismic: If Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).  If this applies, use the same terminology for these devices in PART 3 in order to identify the type of devices required for each application.

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

    - Refer to Section 01 2500, Substitution Procedures.

- *************************************************************************************************************

Seismic:  For either paragraph 2.2.A or 2.2.B, if there are too many systems/components to list here, then list them in an appendix to this section, and then merely refer to that appendix in the paragraph

- *************************************************************************************************************

  - SEismic Performance requirements

    - The luminaires shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

    - The luminaire is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

  - INTERIOR LUMINAIRES

    - Furnish interior luminaires that comply with requirements specified below, indicated on the Drawings, and as required to meet conditions of installation.

    - Metal parts shall be free from burrs and sharp corners and edges

    - Metal components shall be formed and supported to prevent sagging and warping

    - Steel parts shall be finished with manufacturer's standard finish applied over a corrosion-resistant primer.  Finish shall be free from runs, streaks, stains, holidays or defects.

    - Doors and frames shall be smooth operating and free from light leakage under operating conditions.  Relamping, if applicable, shall be possible without the use of tools.  Doors, frames, lenses and diffusers shall be designed to prevent accidental falling during relamping and when secured in the operating position.

    - Pulse-start metal-halide luminaires shall be sufficiently enclosed to prevent escape of lamp parts in the event of catastrophic lamp failure.

    - Luminaires, if applicable, shall have minimum reflecting surface reflectance as follows unless specified otherwise on the Drawings:

      - White Surfaces:  85 percent

      - Specular Surfaces:  83 percent

      - Diffusing Specular Surfaces:  75 percent

    - Lenses, diffusers, covers and globes shall be 100 percent virgin acrylic unless specified otherwise on the Drawings.  Lenses shall have 0.125 inches minimum thickness.  Lenses for fluorescent troffers shall be injection molded.

    - Luminaires shall conform to UL 1598 - Luminaires. Provide product with damp location listing or wet location listing as required by installation location.

    - Light diffusers, other than those made of metal or glass, used in air-handling light fixtures shall be listed and marked “Fixture Light Diffusers for Air-Handling Fixtures.”

*************************************************************************************************************

Note to designer:  Typically, an LED with a CRI of 80 should be chosen.  CRI is a measure of how close the lamp is to an incandescent.  Incandescent lamps are high in the yellow part of the spectrum and low in the blue part of the spectrum.  In order to get an even spectrum, the CRI, by definition, must be low.  CREE labels their CRI 80 lamp as “high definition” because it has a more even spectrum than their CRI 90+

Because of the hazard that 277 volt lighting poses to maintenance personnel, whenever possible use 120 volt circuits to power luminaires.  The lower current draw of LEDs reduces the need for 277 volt lighting circuits.

*************************************************************************************************************

  - LED LUMINAIRES

    - For LED lighting in interior spaces, use 120V [or 277V] luminaires with the performance characteristics listed below:

      - Minimum luminaire efficacy per IES LM-79, Approved Method: Electrical and Photometric Measurement of Solid-State Lighting Products:

        - 90 lumens/watt for general lighting,

        - 50 lumens/watt for accent and display lighting, down-lighting, and special purpose lighting.

      - Correlated color temperature (CCT) per IES LM-79 and ANSI/NEMA/ANSLG C78.377, Specification for the Chromaticity of Solid-State Lighting (SSL) Products:

        - 3500 ºK for general lighting and down-lighting,

        - 2700 ºK for accent and display lighting, and special purpose lighting.

      - LED Design life (L70): Not less than 50,000 hours per IES LM-80, Approved Method: Measuring Lumen Maintenance of LED Light Sources.

      - Driver System Design Life: Not less than the LED design life; note that the driver system includes all associated components, not just the driver integrated circuit. Driver system design life is defined as when 2 percent of the systems would have failed.

      - Power factor: 0.90 or better.

      - Design ambient temperature: 35 °C (95 °F); note that this is the ambient temperature surrounding the luminaire, not the LED or driver heat-sink temperature.

      - EMI/RFI: Meet FCC 47 CFR Part 15.

      - Minimum dimming provisions or capability:

        - 50% step for general lighting,

        - Down to 20% for accent and display lighting, and special purpose lighting.

    - Manufacturers:

      - Recessed LED troffers: Cree LED Lighting, Inc. “CR Series” or approved equal.

      - LED downlights: Cree LED Lighting, Inc. “LR Series” with compatible IC-rated housings, or approved equal.

  - LAMPS

*************************************************************************************************************

Edit specification to suit project requirements

*************************************************************************************************************

    - Furnish lamps that comply with requirements specified below and the luminaire schedule on the Drawings.

    - Conform to the NEMA C78 standard applicable to each type of lamp.

    - For fluorescent general lighting in interior spaces use T8, T5, or T5HO lamps as indicated on the Drawings with the following characteristics:

| - Characteristic | - T8 Lamps | - T5 Lamps | - T5HO Lamps |
| --- | --- | --- | --- |
| - Nominal length: | - 48 inches | - 46 inches | - 46 inches |
| - Actual length (base face to base face): | - 47.2 inches | - 45.2 inches | - 45.2 inches |
| - Base type: | - Medium bi-pin | - Miniature bi-pin | - Miniature bi-pin |
| - Initial Light Output (after 100 hours of operation): | - 2700 - 2850 lumens | - 2900 - 3050 lumens | - 5000 lumens |
| - Mean Light Output (at 40 percent of rated life): | - 2440 - 2710 lumens | - 2660 - 2900 lumens | - 4600 - 4740 lumens |
| - Nominal Lamp Efficacy: | - 87 lumens per watt at 77 °F | - 103 lumens per watt at 95 °F | - 93 lumens per watt at 95 °F |
| - Color temperature: | - 3500 ºK | - 3500 ºK | - 4100 ºK |
| - Minimum Average Life (based on 3-hour switching cycle): | - 20,000 hours | - 20,000 hours | - 30,000 hours |
| - Color rendering index (CRI) | - 75 | - 85 | - 85 |
| - Minimum Starting Temperature: | - 50 °F | - -4 °F | - -4 °F |
| - EPA TCLP Compliant: | - Yes | - Yes | - Yes |
| - Ballast Type: | - Electronic programmed start | - Electronic programmed start with end-of-life shutdown. | - Electronic programmed start with end-of-life shutdown. |

    - For fluorescent accent lighting and downlighting in interior spaces use energy-efficient compact fluorescent lamps with the following features:

      - 3000 to 3500 ºK color temperature

      - Minimum 10,000 hours average life with 3 hours between starts.

      - Lumens at 40 percent of rated life not less than 80 percent of initial lumens.

      - Color rendering index (CRI) of at least 80.

    - For pulse-start metal-halide general lighting in interior spaces use lamps with 3700 to 4000 K color temperatures and color rendering index (CRI) of at least 65.

    - For high-pressure sodium general lighting use improved color quality lamps with 2200 K color temperature and color rendering index (CRI) of at least 65.

    - All linear fluorescent lamps, fluorescent compact lamps, and high pressure sodium lamps shall pass the EPA Toxic Characteristic Leachate Procedure (TCLP) test for mercury by using the lamp sample preparation procedure described in NEMA LL 1, Procedure for Linear Fluorescent LAML Sample Preparation and TCLP Extraction.

    - Manufacturers: GE Lighting, North American Phillips, Sylvania.

  - FLUORESCENT LAMP BALLASTS

*************************************************************************************************************

Edit specification to suit project requirements.

*************************************************************************************************************

    - For fluorescent luminaires provide NRTL-listed electronic fluorescent ballasts that have the following characteristics:

      - Conform to UL 935 - Fluorescent Lamp Ballasts and NEMA C82.11 – High Frequency Electronic Lamp Ballasts (ANSI)

      - Ballast protection: Class P

      - Starting method: programmed rapid-start

      - Power factor: at least 95 percent

      - Ballast factor: at least 0.87

      - Crest factor: 1.7 or less

      - Line current total harmonic distortion (THD): less than 15 percent

      - Minimum operating frequency: 40 kHz

      - Sound rating: Class A

      - Minimum starting temperature: 0 degrees F with T5 and T8 lamps

      - Transient voltage protection: ANSI C62.41 location A2

      - EMI/RFI compliance: FCC 47 CFR Part 18, Non-Consumer

      - Ballasts for T5 and T5HO lamps shall have circuitry to shut down the system when lamps reach end-of-life.

    - For dimmer controlled linear and compact  fluorescent luminaires in heated interior spaces (maintained above 60ºF) provide NRTL-listed controllable electronic fluorescent ballasts that have the following characteristics:

      - Conform to UL 935 - Fluorescent Lamp Ballasts and NEMA C82.11 – High Frequency Electronic Lamp Ballasts (ANSI)

      - Ballast protection: Class P

      - Dimming capability range: 100 to 5 percent of light output, flicker-free

      - Starting method: programmed rapid-start at any preset without first having to go to full output

      - Power factor: at least 0.95 at full light output and at least 0.90 over the entire dimming range

      - Ballast factor: at least 0.87 at full output, less than 10 percent at full dim

      - Crest factor: 1.7 or less

      - Line current total harmonic distortion (THD): less than 20 percent over the entire dimming range

      - Minimum operating frequency: Not less than 40 kHz

      - Sound rating: Class A

      - Minimum starting temperature: 60 degrees F.

      - Control voltage: 0 – 10 Vdc

      - Transient voltage protection: ANSI C62.41 location A2

      - EMI/RFI compliance: FCC 47 CFR Part 18, Non-Consumer

      - Ballasts for T5 and T5HO lamps shall have circuitry to shut down the system when lamps reach end-of-life.

    - Manufacturers: Advance, GE Lighting, Universal, Sylvania

    - Three and four lamp luminaires shall have two ballasts per luminaire for multilevel switching.

    - For emergency ballasts refer to Section 26 5200, Emergency Lighting.

    - Provide NRTL-listed luminaire disconnect assembly for each ballast. Manufacturer: IDEAL “PowerPlug”, Thomas & Betts “Sta-Con.”

  - HIGH INTENSITY DISCHARGE LAMP BALLASTS

*************************************************************************************************************

Edit specification to suit project requirements.

*************************************************************************************************************

    - Pulse-start metal-halide and high pressure sodium ballasts shall comply with requirements specified below for lamps specified in this Section and the luminaire schedule on the Drawings:

      - Conform to UL 1029 - High-Intensity-Discharge Lamp Ballasts and NEMA C82.4 - Ballasts for High-Intensity-Discharge and Low-Pressure Sodium Lamps.

      - Constant wattage auto-transformer (CWA) or regulator, high-power-factor type, minimum 90 percent.

      - Ballasts shall incorporate a solid-state igniter/starter with an average life in the pulsing mode of 4,000 hours at a case temperature of 90 C.

    - Manufacturers: Advance, GE Lighting, Universal

  - Luminaire ACCESSORIES

    - Provide stud supports, mounting brackets, frames, plaster rings and other accessories required for luminaire installation.

    - Furnish hangers as specified below and as required by conditions of installation:

      - Stem hangers shall be made of 1/2-inch steel tubing with 45 degrees swivel ball hanger fitting and ceiling canopy. Finish the same as the luminaire.

      - Rod hangers shall be made of 1/4 inch threaded zinc-plated steel rod.

      - For HID luminaires provide hook hangers that are integrated assemblies matched to the luminaire and line voltage; equip with threaded attachment, power cord and locking type plug. Provide a safety chain or cable for each luminaire that will attach to the building structure, the ballast housing, and to the reflector/diffuser assembly.

    - Use NRTL-listed T-bar safety clips for lay-in fluorescent luminaires.

    - Where indicated on the Drawings or where lamp breakage is detrimental, such as above food counters, provide open fluorescent luminaires with:

      - Self-locking sockets or lamp retainers, two per lamp, and

      - Clear polycarbonate protective lamp sleeves with end caps over each lamp. Sleeve shall have a light transmission of 95 percent and shall be rated for the thermal profile of the lamp and ballast.

- EXECUTION

*************************************************************************************************************

Seismic: If Project Spec includes 26 0548.16, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

  - EXISTING WORK

*************************************************************************************************************

Edit specification to suit project requirements.

*************************************************************************************************************

    - Disconnect and remove luminaires, lamps, and accessories as indicated on the Drawings.

    - Extend existing interior luminaire installations using luminaires, lamps, and installation methods compatible with existing installations, or as specified.

    - Clean and repair existing luminaires that are to remain, or are to be reinstalled, as indicated on the drawings.

    - To the extent indicated on the Drawings, refurbish existing luminaires that are to remain or are to be reinstalled as follows:

      - Replace magnetic ballasts with specified electronic ballasts.

      - Replace T12 lamps with T8, T5, or T5HO lamps as indicated on the Drawings.

      - Replace discolored lenses with new specified lenses.

  - INSTALLATION

    - Install interior lighting system in accordance with the NEC, manufacturer's installation instructions, approved shop drawings, and the following NECA National Electrical Installation Standards:

      - NECA/IESNA 500, Recommended Practice for Installing Indoor Commercial Lighting Systems (ANSI)

      - NECA/IESNA 502, Recommended Practice for Installing Industrial Lighting Systems (ANSI).

    - Have the manufacturer’s installation instructions available at the Project site.

    - Mounting heights specified or indicated on the Drawings are to the bottom of the luminaire for ceiling-mounted fixtures and to the center of the luminaire for wall-mounted fixtures.

    - Where the ceiling forms the protective membrane of a fire-resistive assembly, install protective coverings over luminaires in accordance with manufacturer’s requirements.

    - For luminaires in or on suspended ceilings.

      - Use NRTL-listed clips to secure the luminaire to the ceiling framing members.

      - Install slack safety wires as described below:

        - Wire shall be minimum 12 gauge, galvanized, soft-annealed steel wire conforming to ASTM A641.

        - Attach wire to the building structure directly above the attachment point on the box or luminaire; make trapezes of framing channel material as required to span obstacles.

        - Secure wire(s) at each end with not less than three tight turns in 1-1/2 inches.

        - For luminaires weighing less than or equal to 56 pounds, install two independent slack safety lines.

        - Luminaires weighing more than 56 pounds shall be supported directly from the structure above by approved hangers.

    - In suspended ceilings, connect luminaires using 6 ft. lengths of flexible wiring arranged to accommodate not less than 4 inches of differential seismic movement in any direction. Refer to “Raceway Installation” in Section 26 0533 Raceways and Boxes for Electrical Systems.

*************************************************************************************************************

Seismic: Refer to Guide for details on an exemption to the following sway-brace requirement.

*************************************************************************************************************

    - For luminaires that are subject to swaying (e.g., pendant-mounted or chain-/ cable-supported), brace directly from the structure above using a 9-gauge wire or an approved alternate support (other than a “non-structural support,” (e.g., a ceiling suspension system)).

      - Install seismic restraints for such luminaires to prevent luminaires from swaying.

*************************************************************************************************************

Seismic: Refer to Guide for editing guidance.

*************************************************************************************************************

  - FLEXIBLE CONNECTIONS for luminaires not in suspended ceilings

    - Install flexible connections for [_________] where shown on drawings.

  - Dual-Level Lighting Control

*************************************************************************************************************

Edit specification to suit project requirements. Delete if not applicable.

*************************************************************************************************************

    - In spaces 100 square feet and larger, connect luminaires to provide dual-level control.

    - Coordinate circuiting of luminaires having manual control and automatic control so the manual control can reduce the lighting load by at least 50 percent in a reasonably uniform lighting pattern.

    - Coordinate placement and circuiting of luminaires with daylighting apertures, such as windows.

  - Luminaire maintenance marking

    - Each luminaire shall be clearly and permanently marked with a field-applied pressure-sensitive label indicating specific replacement lamps and ballasts, if applicable. The following information shall be noted in the format “Use Only _______”

      - Lamp diameter code (T5, T5HO, T8), tube configuration (twin tube, quad, triple), base type, and nominal wattage for fluorescent and compact fluorescent luminaires.

      - Lamp type, wattage, bulb type (e.g., ED17, B56) and coating (clear or coated) for HID luminaires.

      - Start type (preheat, rapid start, programmed start) for fluorescent and compact fluorescent luminaires.

      - ANSI ballast type (e.g., M98, M57) for HID luminaires.

      - Correlated color temperature (CCT) and color rendering index (CRI) for all lamps].

    - Markings shall be located to be readily visible to service personnel, but unseen from normal viewing angles when lamps are in place.

    - Pressure-sensitive labels shall be in accordance with UL 969 – Marking and labeling Systems.

  - Field Quality Control

    - Make electrical connections, clean interiors and exteriors of luminaires, install lamps, energize and test luminaires, inspect interior lighting system, and deliver spare parts in accordance with manufacturer's instructions and the following NECA National Electrical Installation Standards:

      - NECA/IESNA 500, Recommended Practice for Installing Indoor Commercial Lighting Systems (ANSI)

      - NECA/IESNA 502, Recommended Practice for Installing Industrial Lighting Systems (ANSI)

    - Test electronic dimming ballasts for full range dimming capability.

      - Burn-in dimmer controlled fluorescent lamps at full output for not less than 100 hours before dimming.

      - Check for visually detectable flicker over the full dimming range.

*************************************************************************************************************

NOTE TO DESIGNER: The luminaire schedule on the Drawings should contain the following information:

1. 	Luminaire type designation (e.g. "A").

2. 	Description of luminaire (e.g. "2'x4' four lamp lay-in fluorescent troffer with hinge and latch flush steel door").

3. 	Description of finish (e.g. "Baked white enamel finish").

4. 	Description of lens or louver (e.g. "Prismatic K-12 pattern acrylic lens").

5. 	Description of ballast if applicable (e.g. "277V programmed-start electronic ballast").

6. 	Ballast factor for fluorescent luminaires (e.g. Ballast factor = 0.88)

7. 	Description and quantity of lamps (e.g. "4-F32T8/835 lamps").

8. 	Manufacturer and catalog number (e.g. "XYZ #123456-7890").

Minimize the number of lamp and ballast types on each project.

************************************************************************************************************

END OF SECTION

**********************************************************

Do not delete the following reference information:

**********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 26 5100, Rev. 6, dated September 2, 2020.