SECTION 27 3000

VOICE COMMUNICATIONS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

*************************************************************************************************************

NOTE: The paging system described in this Section is NOT suitable for use as an emergency evacuation annunciation system. Refer to LANL ESM Chapter 7 Section D5000 paragraph 12.0-H.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Zoned overhead voice communications paging system.

LANL-FURNISHED and installed equipment

*************************************************************************************************************

Edit the following article to match the mounting condition for paging system equipment on this project. In some cases the paging system equipment will be mounted in a GFE equipment rack in the telecommunications room. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

[None.]

[Equipment rack space for the paging system equipment.]

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for components and installation.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application and environment in which installed.

Submittals

Submit the following in accordance with Section 01 3300, Submittal Procedures.

Catalog data for zone paging controllers, paging amplifiers, cable, terminal blocks, speakers, back boxes, and baffles.

Wiring diagram of system showing zone paging controller, paging amplifiers, paging system terminal blocks, and all paging zones.

Calculations for speaker line wire selections, speaker line losses, and amplifier selection.

Proposed programming for zone paging controller.

As-built documents showing programming of zone paging controller, paging system speaker outlets, routing and size of raceways, junction boxes, and pull boxes.

As-built records of cable routing and speaker circuiting.

Test and inspection report for the completed installation.

*************************************************************************************************************

Edit the following article to match the Project requirements. In most cases the paging system equipment will be installed in a telecommunications room. In some cases the equipment will mounted in a GFE equipment rack in the telecommunications room. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

COORDINATION

Coordinate location of the paging system equipment in the telecommunications room(s) with the LANL Telecommunications Group through the LANL Subcontract Technical Representative (STR).

Coordinate schedule for the installation of the paging system equipment in the telecommunications room(s) with the LANL Telecommunications Group through the LANL STR.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - Zone Paging Controller

Provide a zone paging controller that will enable one way paging from the telephone system to one, multiple, or all of the paging zones in the building.

The zone paging controller shall allow direct connection to loop start or ground start trunk telephone systems and PBX or key paging ports via an RJ11 plug.

The zone paging controller shall be field programmable using DIP switches and using the DTMF keys of a telephone. Non-volatile, solid-state storage shall retain programming information during power interruptions.

Paging zone outputs shall be compatible with the paging amplifier(s) specified in this Section.

*************************************************************************************************************

Edit the following article to match the mounting condition for paging system equipment on this project. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

Housing shall have provisions for wall mounting with all connections and controls front accessible. [Provide accessory rack-mounting brackets.]

Provide a suitable NRTL-listed 12 V dc power supply.

Zone paging controller shall be registered under Part 69 of FCC rules.

Manufacturer: Bogen Model PCM2000 Zone Paging System with PCMPS2 power supply.

  - Paging Amplifier

Provide NRTL-listed telephone paging amplifier(s) with minimum power rating as determined by this article. Each amplifier shall provide its full rated output with less than 1 percent distortion.

Provide paging amplifier(s) with individual power rating not less than the sum of the following:

The sum of the tap watts of the matching transformers on the speakers served by the amplifier, plus

The sum of the power losses of the speaker distribution cabling, plus

20 percent power reserve for future system growth, plus

25 percent so an amplifier will never operate at more than 75 percent of its output power rating.

Paging amplifier inputs shall include:

600-ohm balanced telephone line

Low-impedance balanced microphone

Externally accessible controls on the paging amplifier shall include:

Page volume

Automatic level control

Bass control

Treble control

Output from each amplifier shall be a 25 volt balanced line with thermal and electronic overload protection.

*************************************************************************************************************

Edit the following article to match the mounting condition for paging system equipment on this project. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

Amplifier housings shall have provisions for wall mounting with all connections and controls front accessible. [Provide accessory rack-mounting brackets.]

Power source: 120 Vac, 60 Hz

Bogen Models TPU35B, TPU60B, TPU100B, and TPU250 depending on amplifier power required for the system.

  - Raceways and boxes

Provide conduit raceway system for voice communication system wiring.

Use minimum 4x4 metal outlet boxes for speaker wiring. Provide a solid metal cover for each box.

Use flexible metal conduit for connection from outlet boxes to speakers installed in accessible ceilings.

Select conduits to limit cable fill to 40 percent of conduit area.

Refer to Specification Section 26 0533, Raceways and Boxes for Electrical Systems for materials and installation requirements.

Speaker Cable

Provide speaker cable, 18-gage minimum, stranded conductors, single twisted pair, non-shielded , PVC insulation and jacket:

18 AWG: Belden #8461.

16 AWG: Belden #8471.

14 AWG: Belden #8473

12 AWG: Belden #8477

*************************************************************************************************************

Edit the following article to match Project requirements. Delete speaker types not required,

*************************************************************************************************************

Speaker Assemblies

For recessed speakers in lay-in ceiling systems provide pre-assembled drop-in units consisting of the following components:

1 ft x 2 ft steel panel with perforated face and off-white finish,

8-inch cone-type loudspeaker with 10 oz ceramic magnet,

70/25-volt transformer with tap selector switch for 4, 2, 1, 0.5, and 0.25 watts,

Coated steel speaker back-box, and

Support rail crossbar.

Manufacturer: Bogen #CSD1X2.

For recessed speakers in suspended dry-wall or plaster ceilings provide recessed ceiling speaker assemblies consisting of  the following components:

12.75” diameter steel baffle with white powder-coat finish and welded speaker mounting studs

8-inch cone-type loudspeaker with 10 oz ceramic magnet, and

70/25-volt transformer with taps for 5, 2, 1, 0.5, and 0.25 watts,

Manufacturer: Atlas Sound #SD72W.

Lined and coated steel speaker back-box with support rail: Atlas Sound #EZ96-8

For wall-mounted speakers provide speaker assemblies consisting of  the following components:

Sloped baffle with black fabric grille and walnut grain housing,

8-inch cone-type loudspeaker with 5 oz ceramic magnet, and

70/25-volt transformer with taps for 4, 2, 1, 0.5, and 0.25 watts,

Manufacturer: Atlas Sound #WD417-72.

For speakers in noisy or outdoor locations provide re-entrant horn speaker assemblies consisting of the following components:

15 watt horn and driver in a weather-proof housing,

70/25-volt transformer with weatherproof rotary tap switch for 15, 7.5, 1.8, 0.94, and 0.46 watts,

Mounting bracket with horizontal and vertical adjustment, and

Manufacturer’s standard painted finish on all parts.

Manufacturer: Bogen #SPT-15A.

Wiring Duct

Provide non-metallic wiring duct that is NRTL listed to UL 1565 “Positioning Devices.”

Duct and cover material shall be rated as low flammability per UL94V-0 and low smoke generating per ASTM E 662.

Select duct size so wire fill will not exceed 50 percent of duct cross-sectional area.

Manufacturers: Panduit Type TMC.

TERMINAl BLOCKS

Provide DIN rail mounted, double-deck, push-on style terminal blocks with associated mounting rails, markers, end/intermediate plates, and jumpers.

Terminal blocks shall be rated for 28 to 12 AWG solid or stranded wires.

Manufacturer: WAGO #281-619.

EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Remove exposed abandoned paging system components, including abandoned speaker cable and raceways above accessible ceiling finish.  Patch surfaces where removed cables pass through building finishes.

Provide access to existing paging system wiring connections remaining active and requiring access. Modify installation or install access panel.

Extend existing paging circuits using materials and methods as specified in this Section

  - EXAMINATION

Verify that interior of building is protected from weather.

Verify that work of other trades likely to damage paging system components is completed.

Examine building finishes that are to receive paging system components and cables for compliance with installation tolerances and other conditions.  Do not proceed with installation until unsatisfactory conditions have been corrected.

Paging device locations and conduit routings shown on Drawings are approximate unless dimensioned.

Locate paging system components as required to meet project conditions.

Route conduits and cables as required by project conditions.

Where conduit routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet project conditions.

  - Terminal Block INSTALLATION

Furnish and install terminal blocks on the telecommunications room plywood backboard above the location indicated on the Drawings for the voice communications (paging) equipment.

Provide an individual terminal for each speaker cable and arrange terminal blocks by paging system zone.

Mount terminal blocks approximately 6 ft above the floor.

  - CONDUIT and BOX INSTALLATION

Install an outlet box within 6 ft of each speaker assembly location in accessible suspended ceilings.  Install a 1/2” flexible metal conduit from outlet box to speaker back-box located in accessible suspended ceilings.

Install an outlet box at each wall-mounted speaker and each horn-type speaker.  Conduit may be connected directly to speaker back-boxes located in non-accessible suspended ceilings.

Install conduit system for paging system cables starting above the paging system terminal blocks in the telecommunications room and extending to all paging system outlet boxes.

Refer to Section 26 0553, Raceways and Boxes for Electrical Systems, for additional installation requirements.

  - SPeaker Assembly Installation

Install speaker assemblies at locations indicated on the Drawings and as required to provide uniform coverage for each occupied space at the lowest sound power level possible but at least 6 dB above the ambient noise.

In spaces with less than 70-dB ambient noise install ceiling-mounted speakers so the distance between speakers is approximately twice the ceiling height.

In corridors and in similar long, narrow spaces install ceiling-mounted speakers along the center of the space at approximately 8-ft intervals.

In spaces with greater than 70-dB ambient noise or outdoors install horn speakers.

Install speaker assemblies in accordance with the manufacturer’s instructions.  Have the manufacturer’s installation instructions available at the construction site.

Coordinate speaker assembly locations with building finishes, building structure, mechanical ductwork and grills, lighting fixtures, and automatic sprinkler system.

Where the ceiling forms the protective membrane of a fire resistive assembly, install protective coverings over speaker assemblies in accordance with the UL Fire Resistance Design Directory.

Do not support speaker assemblies by ceiling acoustical panels or by dry-wall ceiling or wall panels.

Mount recessed speaker assemblies with at least two 3/4-inch support rails or with tile bridges attached to suspended ceiling support system.

Where recessed speaker assemblies are supported from a suspended ceiling support system, install not less than two independent support rods or wires attached to the building structure.

Install surface mounted speakers directly to outlet boxes that are supported from structure, framing, or suspended ceiling support system.

Mount wall-mounted speakers with center not less than one foot below the ceiling grid but no higher than 9 feet above floor level.

Adjust speaker baffle to fit adjacent surface.

Connect speakers for 25V, 0.5 watt tap operation unless otherwise noted on the Drawings.

  - GROUNDING INSTALLATION

Use approved fittings and minimum 12 AWG bonding jumpers to make paging system raceways electrically continuous.

Bond the paging system conduits to the ground bar in the telecommunications room using 6 AWG ground cable.

Refer to Section 26 0526, Grounding and Bonding for Electrical Systems, for installation requirements.

Paging System Cable Installation

Install paging system cables according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction, the NEC, and requirements in this Section.

Completely and thoroughly swab raceways before installing cable.

Clean foreign matter from interior of boxes before installing cables.

Store cable for 24 hours in the installation area ambient temperature before installing.

Comply with Article 800 of the NEC.

Install speaker wiring as a 25-ohm balanced line.

Terminate speaker cables on the terminal blocks in the telecommunications room.

Use an individual terminal block position for each speaker cable and arrange terminations by paging system zone.

Dress the cables in a neat and orderly manner extending to the termination blocks from the bottom.

Use wiring duct to manage cables from the paging system conduits to the terminal blocks, from the terminal blocks to the paging amplifiers, and between the paging amplifiers and the zone paging controller.

Identification

Uniquely identify each speaker cable at both ends using a numbering scheme that indicates the paging zone.

Uniquely identify signal cables interconnecting the paging zone controller, paging amplifier(s) and terminal blocks with a “from-to” numbering scheme.

Uniquely identify terminal block positions using a numbering scheme that indicates the paging zone.

Identify paging system cable under provisions of Section 26 0553 Identification for Electrical Systems; use a tag produced using a label printing machine.

Paging amplifer Installation

Install paging amplifier(s) in accordance with the manufacturer’s instructions and the approved construction submittal documents. Have the manufacturer’s installation instructions and approved construction submittal documents available at the construction site.

*************************************************************************************************************

Edit the following articles to match the mounting location for paging system equipment on this project. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

[Mount paging amplifiers on plywood terminal board in telecommunications room below the paging terminal blocks.]

[Mount paging amplifiers on GFE equipment rack in telecommunications room.]

Connect paging amplifiers to speaker wiring and to zone paging controller in accordance with approved wiring diagrams.

Use multi-outlet assembly in telecommunications room as 120 Vac power source.

Zone Paging Controller Installation

Install zone paging controller in accordance with the manufacturer’s instructions and approved construction submittal documents. Have the manufacturer’s installation instructions and approved construction submittal documents available at the construction site.

*************************************************************************************************************

Edit the following articles to match the mounting location for paging system equipment on this project. Coordinate with the LANL Telecommunications Group.

*************************************************************************************************************

[Mount zone paging controller on plywood terminal board in telecommunications room below the paging amplifier(s).]

[Mount zone paging controller on GFE equipment rack in telecommunications room.]

Provide a telephone outlet with RJ11 jack next to the zone paging controller.

Connect the zone paging controller to paging amplifiers and in telephone system in accordance with approved construction submittal wiring diagrams.

Use multi-outlet assembly in telecommunications room as 120 Vac power source.

Program the zone paging controller in accordance with the manufacturer’s instructions and approved construction submittal programming documents

FIELD QUALITY CONTROl

Upon installation of wires and cables and before electrical circuitry is energized, show product capability and compliance with requirements and verify by testing that conductors are free from shorts and unintentional grounds.

Inspect each installed speaker assembly for damage.  Replace damaged components.

Test installed paging system for proper operation and output volume.

Provide instruments to make and record test results.

Replace or repair malfunctioning components then re-test.

Verify that system can be accessed and controlled from the telephone system.

Adjust transformer taps as required to obtain a paging signal in each that is within 3 dB of the levels listed below.

Enclosed offices: 61 dBA (6 dB above a 55 dBA ambient)

Open plan offices: 76 dBA (6 dB above a 70 dBA ambient)

Laboratories: 76 dBA (6 dB above a 70 dBA ambient)

Corridors: 71 dBA (6 dB above a 65 dBA ambient)

Mechanical rooms: 91 dBA (6 dB above an 85 dBA ambient)

Submit test and inspection report for the completed installation.

END OF SECTION

*******************************************************************************************************

Do not delete the following reference information:

*******************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 27 3000, Rev.3, dated July 1, 2008.