SECTION 28 3100

FIRE DETECTION AND ALARM

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Fire POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections. 
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Design, furnish, install, test, certify, and place into service a complete addressable fire alarm system.  The system shall be complete with all hardware and software specifically tailored for this installation.

Provide a fire alarm system consisting of, but not limited to the following components:

Fire alarm control panel (FCP)

Conduit and wiring necessary to connect the FCP to alarm initiating devices, notification appliances and auxiliary equipment

*************************************************************************************************************

Edit 3 through 13 to match project fire alarm system requirements.

*************************************************************************************************************

Addressable manual fire alarm stations

Addressable analog area smoke detectors

Addressable analog duct smoke detectors

Addressable analog heat detectors

Connections to sprinkler waterflow alarm switches

Connections to sprinkler supervisory switches and tamper switches

Audible and visual combination notification appliances

Air handling systems shutdown relays

Elevator recall/shunt relays (if the building has an elevator)

Battery standby

Conduit and GFE cable to building’s main telecommunications room

Provide a fire alarm system that conforms to the requirements of the latest editions of (1) NFPA 72 National Fire Alarm and Signaling Code, (2) NFPA 70 National Electrical Code, (3) ASME A17.1 Safety Code for Elevators and Escalators, and (4) NFPA 90A Standard for the Installation of Air-Conditioning and Ventilating Systems.

SYSTEM FUNCTIONAL DESCRIPTION

*************************************************************************************************************

Edit system functional description to match the project fire alarm system requirements.  Projects with high explosives areas or NEC Article 500 hazardous locations will require additional specialized equipment and system characteristics not included in this specification.

*************************************************************************************************************

The system shall identify any off normal condition and log each condition into the system database as an event.

The system shall automatically display on the control panel the first event of the highest priority by type.  The priorities and types shall include alarm, supervisory, and trouble.

The system shall have a queue operation, and shall not require event acknowledgment by the system operator.  The system shall have a labeled color-coded indicator for each type of event.

The user shall be able to review each event by selecting scrolling keys.

New alarm, supervisory, or trouble events shall sound a silence-able audible signal at the control panel.

Operation of any alarm-initiating device shall automatically:

Update the control/display as described above.

Audibly and visibly annunciate the alarm condition at the FCP.

Activate all NAC appliances in accordance with the respective evacuation plan and matching functional matrix.  The fire alarm evacuation tone shall be the three-pulse temporal pattern.

Operate the alarm relay and initiate the transmission of an alarm signal to the LANL central station over a digital alarm communicator system.

Operate control relay contacts to shut down all HVAC units serving the floor of alarm initiation.

*************************************************************************************************************

Delete 6 and 7 if there is no elevator.

*************************************************************************************************************

Operate control relay contacts to return all elevators that serve the floor of alarm initiation to the ground floor.  If the alarm originates from the ground floor, operate control circuits contacts to return all elevators to the floor above or to a level as directed by the LANL Fire Protection Group.

Shut down power to elevator equipment before sprinkler operation in the elevator equipment room.

Activation of a supervisory initiating device shall:

Update the control/display as described above.

Audibly and visibly annunciate the supervisory condition at the FCP.

Operate the supervisory relay and initiate the transmission of a supervisory signal to the LANL Central Station over a digital alarm communicator system.

The entire fire alarm system wiring shall be electrically supervised to automatically detect and report trouble conditions to the FCP.  Any opens, grounds, or disarrangement of system wiring and shorts across alarm horn/strobe wiring shall automatically:

Update the control/display as described above.

Operate the trouble relay contacts to initiate the transmission of a trouble signal to the LANL central station over a digital alarm communicator system.

Visually and audibly annunciate a general trouble condition, on the FCP. The visual indication shall remain on until the trouble condition is repaired.

The FCP shall have an optional LED Annunciator/Switch Card component installed and programmed for pre-defined disable groups particular to this installation.  Disable groups shall consist of the following to facilitate routine inspection, testing, and maintenance (ITM):

All control relays that initiate/control closure of the specified combination fire/smoke dampers listed in Sections 1.2.B.6 and 1.2.B.7.

All control relays that initiate/control HVAC shutdown listed in Section 1.2.B.5.

All notification appliances.

All elevator related control functions.

SYSTEM DESIGN

- System Design: Provide the services of a qualified factory trained fire alarm designer for the FCP to be installed on this project.  The designer shall assure the completeness and correctness of the fire alarm system design by performing the following:

Prepare drawings of FCP indicating location of components, interconnection of components and connections to alarm initiating, indicating, and auxiliary circuits.

Prepare a system input/output matrix to verify that the proper sequences occur for each initiating point or zone.

Prepare drawings of fire alarm layout, conduit and wiring plans.  Show location of all fire alarm appliances, conduit layout, quantity, and type of wires in each conduit, and interface with other systems for functions such as central station signaling, fan shutdown, damper operation, and elevator recall.

Prepare terminal-to-terminal field wiring diagrams for alarm initiating, indicating and auxiliary circuits; detail the interfaces with other systems; indicate labeling of each fire alarm system conductor.

Calculate conductor sizes for each alarm initiating, indicating, and auxiliary circuit; limit voltage drops so that they do not exceed the FCP manufacturer’s limitations, for the most remote device on each circuit.

Prepare battery load calculations for the FCP and any remote power supply panels and select proper battery size.  Battery shall be sized to include an additional 50% safety margin above calculated system demand.

Calculate alarm signal in all spaces to comply with ADAAG requirements: minimum 15 dBA above ambient at all locations, but not over 120 dBA at any location.

Select alarm initiating, alarm indicating, and auxiliary devices compatible with FCP.

ACTION SUBMITTALS

Provide the following per project submittal procedures.

Certifications

Within 30 days after Notice to Proceed (~60% submittal; see Appendix), certifications of the qualifications of the fire alarm installing firm as described in the quality assurance paragraph of this Section.

Within 30 days after Notice to Proceed (~60% submittal; see Appendix), certifications of the qualifications of the fire alarm system technician as described in the quality assurance paragraph of this Section.

Certification from the fire alarm control manufacturer that proposed alarm-initiating devices, alarm appliances, and auxiliary devices are compatible with the FCP and other auxiliary equipment.

Delegated Design Submittals

NOTE:  From a review standpoint, calcs and drawings may be treated as design outputs by LANL and reviewed using a Design Review Record form/process instead of the construction submittal form/process.

Calculations: Submit the following with Design Drawings (~60%, 90%, 100% submittals; see Appendix).

System battery capacity calculations to demonstrate that the battery is sized to support the system operating in a “normal” (non-alarm) condition for not less than 24 hours plus a general alarm condition (all alarm notification appliances used for evacuation being activated) for not less than 10 minutes following the completion of the 24-hour period. Battery shall be sized to include an additional 50% safety margin above calculated system demand.

Voltage drop calculations to demonstrate that the signal voltage at the most remote notification appliances on each circuit will not be less than the FCP or the notification appliance manufacturer’s recommendations.

Design/Installation Drawings (~60%, 90%, 100% submittals)

Prepare floor plan drawings using a minimum scale of 1/8" - 1'0" for plans and 1/4" = 1'-0" for details.

Hand-lettering shall be a minimum of 3/16" and other lettering a minimum of 1/8" to permit reproduction.

Show location of FCP, all fire alarm appliances, conduit layout, quantity and type of wires in each conduit, and interface with other systems for functions such as central station signaling, fan shutdown, damper operation, and elevator recall.

Show layout of the FCP indicating location of components, interconnection of components, and connections to alarm initiating, indicating, and auxiliary circuits.

Provide terminal-to-terminal wiring diagrams for alarm circuits, supervisory circuits, remote power supply panels, and interfaces with other systems such as HVAC and elevators.

Submit with calculations at least 30 days prior to scheduled start of fire alarm system installation (~60%, 90%, 100% submittals; see Appendix).  Installation shall not proceed without 100% Submittal design approval by the LANL Fire Protection Group.

Catalog Data:  For all equipment furnished under this Section.  See Appendix for submittal schedule.

Installation Instructions: See Appendix for submittal schedule.

Materials and Parts List: See Appendix for submittal schedule.

FCP Program

Provide FCP input/output matrix and a copy of the proposed FCP program at least two weeks prior to the anticipated pre-test date of the fire alarm system.

Provide final FCP input/output matrix and the final FCP program before requesting final tie-in/acceptance testing.

O&M Manual

Submit operating and instruction manuals with the 100% submittal of calculation and drawings (see Appendix).

Submit five complete sets of project-specific operating and maintenance instruction manuals upon successful completion of testing.  Provide complete, step-by-step testing instructions giving recommended and required testing frequency of all equipment, methods for testing each piece of equipment, and a complete trouble shooting manual explaining how to test the primary internal parts of each piece of equipment.  Maintenance instructions shall be complete, easy to read, understandable, and shall provide the following information:

Provide instructions for replacing any components of the system, including internal parts.

Provide a list of recommended spare parts.

Provide instructions for periodic cleaning and adjustment of equipment with a schedule of these functions.

Provide a complete list of all equipment and components with information as to the address and telephone number of both the manufacturer and local supplier of each item.

Provide operating instructions prominently displayed on a separate sheet located next to the FCP in accordance with UL Standard 864.

Test Reports

Submit report of the pre-final tests indicating system status and corrective actions required before requesting the final acceptance tests.

Submit test plan for the final acceptance tests of unique/special fire detection and alarm equipment such as UV/IR fire detectors, high-sensitivity smoke detection (HSSD) systems, air-aspirating/sampling detectors, linear fire detectors, and others having special manufacturer’s requirements and recommendations for acceptance testing, before requesting the final acceptance tests.

Upon successful completion of final acceptance tests, submit final “Record of Completion” and “Inspection and Testing Form” as required by NFPA 72.

Project Record Documents

Provide updated drawings reflecting as-built conditions showing the work completed under this Section.  Include notes on special systems or devices, new and existing, locations of equipment, actual conduit installation, wiring color-coding, wire tag notations, interconnections between all equipment, and internal wiring of the equipment. Include conduit size, conductor size, and number of conductors per conduit.

Provide the updated drawings on electronic media in “.pdf” and AutoCAD “*.dwg” formats.

Provide “Record of Completion" and associated documentation for the completed system according to NFPA 72.

Warranties: Warrant all equipment and wiring free from inherent mechanical and electrical defects for one year (365 days) from the date of final acceptance, in writing.

QUALITY ASSURANCE

Qualifications of the installing firm:

Be licensed by any state in the United States to engage in the design, fabrication, and installation of fire alarm systems.

Have satisfactorily installed at least twenty fire alarm systems of equivalent nature and scope to the system described in this Section.

Provide the services of a qualified fire alarm system technician to design the fire alarm system and to test the completed system.

Be a factory-certified representative of the manufacturer of the FCP that will be used on this project.

Qualifications of the fire alarm system technician:

Be factory trained in the theory, operation, installation, and troubleshooting of the FCP that will be used for this project.

Have satisfactorily designed at least twenty fire alarm systems of equivalent nature and scope to the system described in this Section.

Have satisfactorily field-tested at least twenty fire alarm systems of equivalent nature and scope to the system described in this Section.

Be NICET (National Institute for Certification in Engineering Technologies) Fire Alarm Certified, or certified by an equivalent organization acceptable to the LANL Fire Authority Having Jurisdiction.

PRODUCT HANDLING

Materials and Equipment: Protect from damage during shipping, storage, and installation.

*************************************************************************************************************

Add special product handling requirements for the facility in which this system is to be installed.

*************************************************************************************************************

PRODUCTS

  - GENERAL

Provide materials and equipment that are new and unused, free of defects, specifically designed for the use intended, conform to the requirements of the NEC and NFPA 72, and are NRTL listed for the intended use.

Provide products suitable for operation at an elevation of 7,500 ft.

FIRE ALARM CONTROL PANEL

The FCP shall incorporate all control electronics, relays, and necessary modules and components in a flush or semi-flush mounted cabinet (dependent on FCP mounting location).  The operating controls and zone/supervisory indicators shall be located behind locked door with viewing window.  All control modules shall be labeled, and all zone locations shall be identified.  The assembly shall contain a base panel, system power supply and battery charger with additional modules to meet the requirements of these specifications.

System circuits shall be configured as follows: Addressable analog loops Class B/Style 4; Initiating Device Circuits (if used) Class B/Style B; Notification Appliance Circuits Class B/Style Y.

The system shall store all basic system functionality and job specific data in non-volatile memory.  The system shall survive a complete power failure intact.

The system shall allow down loading of a job specific custom program created by system application software.  It shall support programming of any input point to any output point.

The system shall support distributed processor intelligent detectors with the following features: integral multiple differential sensors, environmental compensation, pre-alarm, dirty detector identification, automatic day/night sensitivity adjustment, dual normal/alarm LEDs, relay bases, and isolator bases.

The system shall use full digital communications to supervise all addressable loop devices for placement, correct location, and operation.  It shall allow swapping of “same type” devices without the need of addressing and impose the “location” parameters on replacement device.  It shall initiate and maintain a trouble if a device is added to a loop and clear the trouble when the new device is defined in the system.

The system shall have a nationally recognized testing laboratory (NRTL) listed detector sensitivity test feature, which will be a function of the smoke detectors and performed automatically.

All panel modules shall be supervised for placement and initiate a trouble signal if damaged or removed.

The system shall have a CPU monitoring circuit to initiate a trouble signal should the CPU fail.

The system evacuation signal rate shall be suitable to support audio-visual combination-type electronic three pulse temporal pattern sounder and strobe combination units.

The system program shall meet the requirements of this project, current codes and standards, and satisfy the LANL Fire Authority Having Jurisdiction.

Passwords shall protect any changes to system operations.

The power supply shall be a high efficiency switch mode type with line monitoring to automatically switch to batteries for power failure or brown out conditions.  The automatic battery charger shall have low battery discharge protection.  The power supply shall provide internal power and 24 Vdc for notification appliance circuits.  All outputs shall be power limited.  The battery shall be sized to support the system for 24 hours of supervisory and trouble signal current plus general alarm for 10 minutes.

The FCP shall have a high-contrast, alphanumeric display to show system status, alarm information, and supervisory information.  The FCP shall have LED indicators for the following common control functions: AC power, alarm, supervisory, monitor, trouble, disable, ground fault, CPU fail, and test.  There shall be control keys and visual indicators for; reset, alarm silence, trouble silence, and drill.

Battery boxes, if required, shall be UL Listed for the purpose.

The FCP shall have a digital alarm communicator transmitter (DACT) module to transmit detailed alarm, supervisory and trouble signals to a digital alarm communicator receiver (DACR) at a Central Monitoring Station.

The DACT shall support dual telephone lines, “contact ID” communications format, and configured for dual-tone, multi-frequency (DTMF).

The DACT shall be listed for “Central Station Fire Service” and for “Proprietary Station Fire Service” and shall be of the same manufacturer as the control panel.

The DACT shall transmit the following information to the LANL Central Station:

- Fire alarm per point addressable device (e.g., detector or water flow activation, manual pull stations, etc.)

- Supervisory signal per addressable device (e.g., valve tamper)

- General System Trouble (alarm panel trouble)

      - Loss of AC Power

      - Communication Line Failure (Primary and Backup)

      - Trouble per zone or point addressable device

      - Battery Failure

Restoration of each signal condition identified above shall be transmitted to the LANL Central Station.

The secondary telephone line shall only be utilized for signal transmission in the event that attempts to communicate utilizing the primary line are unsuccessful.

The secondary telephone line shall have the same account code and communication format as the primary line.

A general alarm or supervisory signal shall not be transmitted by the DACT when specific point/zone information is transmitted.

Loss of AC power shall be transmitted 3 hours after the detected failure.

A test signal shall be sent once every 24 hours.

For consistency, telephone wire color configuration shall be as follows:

1 -  Four-pair wire (preferred method)

| To DACT | To Premise Telephone |
| --- | --- |
| Cable 1 | Cable 2 | Cable 1 | Cable 2 |
| Tip 1 | Ring 1 | Tip 2 | Ring 2 | Tip House 1 | Ring House 1 | Tip House 2 | Ring House 2 |
| White/ Blue | Blue/ White | White/ Green | Green/ White | White/ Orange | Orange/ White | White/ Brown | Brown/ White |

2 -  Two-pair wire

| To DACT | To Premise Telephone |
| --- | --- |
| Cable 1 | Cable 2 | Cable 1 | Cable 2 |
| Tip 1 | Ring 1 | Tip 2 | Ring 2 | Tip House 1 | Ring House 1 | Tip House 2 | Ring House 2 |
| Green | Red | Green | Red | Black | Yellow | Black | Yellow |

Manufacturers: Edwards EST3X or NOTIFIER NFS 2-640, no substitutions

led annunciator/switch card

Provide compatible components programmed per the pre-defined disable groups in Paragraph 1.2.E particular to this installation.

Manufacturers: Edwards EST 4X-12SR or NOTIFIER Annunciator Control Module ACM-24AT.  no substitutions.

ADDRESSABLE THERMAL DETECTORS

Provide addressable, intelligent, fixed temperature or rate-of-rise thermal detectors that are compatible with and acceptable to the FCP manufacturer.  The heat detection design documentation shall state the required performance objective of the system.  The designer responsible for the strategy of the structure as a whole shall establish the “type” selection criteria.

The detector shall be rated at 135ºF and shall be spaced according to the detector manufacturer’s spacing guidance and the structure’s attributes.  For applications requiring other than 135 ºF, consult the LANL Fire Protection Group.

Manufacturers: Edwards EST SIGA2-HFS or SIGA2-HRS, or NOTIFIER FST-851 or FST-851R, no substitutions.

ADDRESSABLE PHOTOELECTRIC DETECTORS

Provide addressable, analog, intelligent, photoelectric type smoke detectors that are compatible with and acceptable to the FCP manufacturer.

The photoelectric detector shall be rated for ceiling installation at a minimum of 30 ft (9.1m) centers and be suitable for wall mount applications.

Manufacturers: Edwards EST SIGA2-PS or NOTIFIER FSP-851.  no substitutions.

DETECTOR MOUNTING BASES

Provide standard bases suitable for mounting on 3-1/2” or 4” octagon box and 4” square box.  The base shall contain no electronics and support all detector types.  Removal of the detector shall not affect communications with other detectors.

Manufacturers: Edwards EST SIGA-SB or NOTIFIER B210LP Low profile base.  no substitutions.

DUCT SMOKE DETECTOR AND HOUSING

Provide addressable photoelectric detectors compatible with and acceptable to the FCP manufacturer and listed for the maximum air flow velocity anticipated.

Provide duct housing assemblies to facilitate mounting an intelligent analog photoelectric detector along with a standard relay or isolator detector mounting base.  Provide for variations in duct air velocity between 300 and 4000 feet per minute. Protect the measuring chamber from damage and insects.  Provide an air exhaust tube and an air sampling inlet tube that extends into the duct air stream.  Provide drilling templates and gaskets to facilitate locating and mounting the housing.  Finish the housing in baked red enamel.

Where a duct detector is installed in a concealed location, more than 10 ft above the finished floor, or in an arrangement where the detector alarm indicator is not readily visible to responding personnel, the detector shall be provided with a remote alarm indicator.  Remote alarm indicator shall be installed in a readily accessible location and shall be clearly labeled to indicate its function.

Provide detector wiring so that detector can be reset at FCP.

Manufacturers: Edwards EST SIGA-SD or NOTIFIER DNR Series.  no substitutions.

AUTOMATIC SPRINKLER SYSTEM

Refer to Section 21 1313, Wet-Pipe Sprinkler Systems, for pressure switches, flow switches and valve supervisory switches associated with the automatic sprinkler system.

Provide intelligent single-input or dual-input modules as required to connect pressure switches, flow switches, and valve supervisory switches to the addressable analog loop.  Each input shall provide a supervised Class B input circuit.

Manufacturers: Edwards EST “SIGA-CT1” single-input or “SIGA-CT2” dual-input, or NOTIFIER “FlashScan Monitor Module FMM-1” or “FDM-1 FlashScan dual monitor module.”  no substitutions.

ADDRESSABLE MANUAL PULL STATIONS

Provide addressable double-action, non-coded manual pull stations that are acceptable to the FCP manufacturer and are compatible with the FCP.

The fire alarm station shall be of Lexan or metal construction with an internal toggle switch. Provide a key locked test feature.  Finish the station in red with white “PULL IN CASE OF FIRE” lettering.  The manual station shall be suitable for mounting on 2-1/2” deep 1-gang boxes and 1-1/2” deep 4” square boxes with 1-gang covers.

Provide the appropriate back boxes and mounting plates for flush-mounting or surface mounting (depending on the building construction).

Manufacturers: Edwards EST SIGA 278 or NOTIFIER NBG-12LX.  no substitutions.

ADDRESSABLE CONTROL RELAY MODULES

Provide modules acceptable to the FCP manufacturer and compatible with the FCP.

The control relay module shall provide one “Form C” dry relay contact rated at 2 amps at 24 Vdc to control external appliances or equipment shutdown.  The control relay shall be rated for pilot duty and releasing systems.  The position of the relay contact shall be confirmed by the system firmware.

Manufacturers: Edwards EST SIGA-CR or NOTIFIER FRM-1, no substitutions.

Provide additional relays with voltage and current ratings as required to perform functions such as air handling system shutdown and elevator recall.

Control relays should be installed in a “readily accessible location and height”.

AUDIBLE AND VISUAL COMBINATION NAC DEVICES

Provide NRTL-listed 24 VDC audio-visual combination-type electronic three-pulse temporal pattern sounder and strobe combination units that are acceptable to the FCP manufacturer and are compatible with the FCP.

Sounder shall include three-pulse temporal pattern generating electronics, audio transducer, and screw terminals housed in a red housing.  Acoustical output shall meet requirements of UL 464.  The audible signal shall be the “American National Standard Audible Emergency Evacuation Signal” (three-pulse temporal pattern) in accordance with ANSI S3.41, Audible Emergency Evacuation Signal.

Strobe signal output and flash rate shall meet UL 1971 and ADAAG requirements.  Unit shall have a xenon flash tube enclosed in a clear Lexan lens with “FIRE” in white lettering, and shall produce a synchronized strobe flash.  Provide strobes with flash output levels as required to meet NFPA 72 visual signal requirements for each space.

*************************************************************************************************************

Edit D. to match project fire alarm system requirements.

*************************************************************************************************************

Horn/strobe shall mount to a 4” x 2-1/8” deep electrical box with single device cover. Provide weatherproof wall boxes for outdoor mounting.

Manufacturers: EST “GENISIS” series, Wheelock “Exceder” series, or System Sensor “P” Series. no substitutions.

Voice Alarm Systems shall utilize System Sensor SpectrAlert series appliances.

NOTIFICATION BOOSTER POWER SUPPLIES

Provide notification circuit booster power supplies (as needed) that are acceptable to the FCP manufacturer and are compatible with the FCP.

Manufacturers: Edwards EST “BPS-10A” or NOTIFIER “ACPS-610.”  no substitutions.

CONDUIT

Install fire alarm wiring in conduit.  Minimum conduit size 3/4 inch.

Refer to Section 26 0533, Raceway and Boxes for Electrical Systems, for conduit systems.

JUNCTION BOXES

Refer to Section 26 0533, Raceway and Boxes for Electrical Systems, for junction boxes.

WIRING

Color Code: Use the following color code for the fire alarm system wiring:

Black - 120-Volt AC phase wire.

White - 120-Volt AC neutral wire.

Green - System ground wire.

Brown - Negative connection for strobe device.  (If wired separately from horns.)

Orange - Positive connection for strobe device.  (If wired separately from horns.)

Blue - Negative connection for horn circuit or horn/strobe combination circuit.

Yellow - Positive connection for horn circuit or horn/strobe combination circuit.

Gray - Negative conventional alarm initiating device connection.

Violet - Positive conventional alarm initiating device connection.

Black - Negative circuit connection for duct smoke detector reset, HVAC interlock, and other auxiliary connections.

Red - Positive circuit connection for duct smoke detector reset, HVAC interlock, and other auxiliary connections.

Black/Red Twisted Pair - Addressable device data loop, evacuation speaker circuit.

Conductors: Provide alarm and supervisory signaling system conductors that meet the requirements of Article 760 in the NEC and are NRTL-listed for the type of service to which they will be subjected.  Minimum conductor requirements:

Interior/Dry Locations: Red-jacketed NEC type FPL cable with No. 16 AWG (minimum) twisted-pair conductors for addressable devices (shielded if required by the FCP manufacturer), and listed per UL1424.

Low voltage binary signal conductors shall be type THHN, thermoplastic insulation, No. 16 AWG minimum, and solid copper conductor.

Other low voltage conductors shall be type TFN, No. 16 AWG (minimum), thermoplastic insulation, and single solid copper conductor.

Exterior/Wet Locations: Red-jacketed NEC type FPL cable with No. 16 AWG (minimum) twisted-pair conductors for addressable devices (shielded if required by the FCP manufacturer), and listed for WET locations per UL1424.

Low voltage binary signal conductors shall be type THWN-2, thermoplastic insulation, No. 16 AWG minimum, and solid copper conductor.

Power conductors shall be type THHN/THWN-2, No. 12 AWG, thermoplastic insulation, and single solid copper conductor.

Size conductors of the fire alarm systems as recommended by the manufacturer, based on the operating ampacity of the circuit and the permissible resistance and voltage drop characteristics that will allow proper operation of the equipment. Provide conductors selected to provide voltages within the manufacturer specification limits for the most remote fire alarm notification appliance or field device.

Design each addressable analog loop so device loading will not exceed 80% of loop capacity in order to leave for space for future devices.

TEST EQUIPMENT

Provide any special test equipment manufactured by the fire alarm equipment manufacturer for maintenance, testing, or troubleshooting.

SURGE PROTECTION

NOTE:  All surge protectors shall be installed to be readily accessible for servicing.

Provide a UL 1449 listed 120V surge protective device for the main FCP, each sub-FCP, and each booster power supply that has a 120V supply circuit.

Device shall be capable of absorbing a maximum single pulse of at least 6,500 amperes.

Clamping voltage shall not exceed 330 volts line-to-neutral when tested in accordance with ANSI/IEEE C62.31 category C1/B3.

Manufacturer: EDCO Model “FAS-120AC” or as recommended by the FCP manufacturer.

Provide a UL 497B listed surge protective device for each analog initiating device signaling circuit entering/leaving each building that is monitored by the FCP.

Device shall be capable of absorbing a peak 8x20 microsecond current of 10,000 amperes at least 10 times.

Clamping voltage shall not exceed 30 volts.

Capacitance shall not exceed 50pf.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: EDCO model “PC642C-030LC” (protects 2 pairs) and “PCB1B” socket, or as recommended by the FCP manufacturer.

Provide a UL 497B listed surge protective device for each 24-volt initiating device circuit or control circuit entering/leaving each building that is monitored by the FCP.

Device shall be capable of absorbing a peak 8x20 microsecond current of not less than 10,000 amperes at least 10 times.

Clamping voltage shall not exceed 30 volts.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: EDCO model “PC642C-030” (protects 2 circuits) and “PCB1B” socket, or as recommended by the FCP manufacturer.

Provide a UL 497B listed surge four-wire protective device for each FCP RS-232 circuit entering/leaving each building monitored by the FCP.

Device shall be capable of absorbing a peak 8x20 microsecond current of 10,000 amperes at least 10 times.

Clamping voltage shall not exceed 20 volts for RS-232 applications.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: EDCO model “PC642C-020” with “PCB1B” socket, or as recommended by the FCP manufacturer.

Provide a UL 497B listed surge four-wire protective device for each FCP RS-485 circuit entering/leaving each building monitored by the FCP.

Device shall be capable of absorbing a peak 8x20 microsecond current of 10,000 amperes at least 10 times.

Clamping voltage shall not exceed 8 volts for RS-485 applications.

Line to line and line to ground capacitance shall not exceed 50pf.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: EDCO model “PC642C-008LC” with “PCB1B” socket, or as recommended by the FCP manufacturer.

Provide a UL 497B listed surge protective device for each 24-volt notification appliance circuit entering/leaving each building that is monitored by the FCP.

Protective device shall have a series resistance not exceeding 0.2 ohms per pair and shall be capable of carrying a continuous current of 5 amperes.

Device shall be capable of absorbing a peak 8/20 microsecond current of 5000 amperes and a 2000-ampere occurrence at least 50 times.

Clamping voltage shall not exceed 43 volts.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: EDCO model “PHC-043” (protects 2 circuits) and “PCB1B” socket, or recommended by the FCP manufacturer.

Provide a single-point ground bus for each enclosure containing one or more surge protective devices.  Manufacturer: EDCO model “TER-BUS” or as recommended by the FCP manufacturer.

EXECUTION

  - FIELD CONDITIONS

Prior to installation carefully inspect the installed work of other trades, whether pre-existing or part of this project and verify that such work is complete to the point where the installation of the fire alarm system may properly commence.

Notify the LANL Subcontract Technical Representative (STR) if conditions exist, not resulting from work of this project, that prohibit the installation from conforming to applicable codes, regulations, standards, and the original, approved design.

INSTALLATION

General:

Install the fire alarm system in accordance with the NEC, NFPA 72, and this specification.

Follow Section 26 0529, Hangers and Supports for Electrical Systems, for anchorage requirements.

Verify dimensions in the field.  Lay out work in the most direct and expeditious manner to avoid interference.

Coordinate necessary shutdowns of existing systems by notifying the LANL STR a minimum of seven working days before rendering such systems inoperative.  Do not render inoperative any system without the prior approval of the LANL STR.  The LANL STR will initiate and submit the LANL Utility Outage Request for Fire Protection.

Coordinate fire alarm detectors and associated equipment with existing ceiling or roof materials, lighting, ductwork, conduit, piping, suspended equipment, structural and other building components.

Coordinate installation of fire alarm system with work of other trades.  Protect fire alarm equipment with suitable coverings until completion of Project.

Device Mounting Heights:

Install manual pull stations with center 44 inches above finished floor.

Install combination audible/visual notification appliances with the bottom 84 inches above finished floor or 6 inches below ceiling, whichever is lower. In high bay type areas the devices may be installed at a maximum of 96 inches above the floor.  Any deviations from these heights require approval from the LANL AHJ.

Comply with ADA Accessibility Guidelines (ADAAG) for device mounting heights and locations.

FCP Installation

Install FCP following manufacturer’s written instructions, NFPA 72, and the NEC.

Locate the FCP in the main building lobby or entry vestibule so fire department personnel entering the building can readily access it.  Coordinate location of FCP with the LANL Fire Protection Group.

Install FCP with top of cabinet trim 66 inches above finished floor. Refer to manufacturer’s recommended installation height.

Mount FCP plumb and rigid without distortion of the box. Mount flush cabinets   uniformly flush with wall surfaces.

Install filler plates in unused spaces in FCP.

Train conductors in cabinet gutters neatly in groups; bundle and wrap with cable ties after completion of testing.

Tighten electrical connectors and terminals, including grounding connections, according to the manufacturer’s published torque-tightening values.  Where manufacturer's torque values are not indicated, use those specified in UL 486A.

Control relays: Install in a readily accessible location and height acceptable to the AHJ.

Wiring Installation:

Install fire alarm system wiring in conduit raceway.

Do not pull wire or cable until the conduit system is complete between pull points.

Bundle conductors in panels and boxes into groups by service and destination.

Run electronic cable continuous between termination points.  No splicing is permitted without prior approval from the LANL AHJ.  Where splicing is approved, use terminal strips that are acceptable to the LANL Fire Protection Group.  Do not use “wire nuts.”

Do not install AC current-carrying conductors in the same raceway with the DC or digital fire alarm detection and signaling conductors.

Circuit each addressable analog loop so device loading shall not exceed 80% of loop capacity in order to leave for space for future devices--the loop shall have Class B operation.  Where it is necessary to interface conventional devices provide intelligent modules to supervise Class B wiring.

Minimize the number of T-taps in fire alarm addressable data circuits and adhere to the manufacturer requirements/limitations.  Make no T-taps in notification appliance circuits.  T-taps shall only be made on device terminals or on terminal strips that are acceptable to the LANL Fire Protection Group, do not use “wire nuts.”

Make allowances in conductor length at panels and other enclosures to permit forming the conductors neatly within the enclosures.  Where wiring troughs are not provided with the enclosures, neatly cable and adequately support the wiring.

Ring out and identify power and control conductors before terminal connections are made.  Check polarity and phasing and make changes as required before making terminal connections.

Test conductors for continuity and for freedom from shorts or unintentional grounds.

Junction Box and Conduit Installation: Refer to Section 26 0533, Raceway and Boxes for Electrical Systems, requirements.   Provide minimum 3/4” fire alarm system conduit.

Install audible and visual notification appliances in the following locations to obtain an audible signal level that is at least 15 dB above ambient but does not exceed 120 dB at any location:

Corridors

Conference rooms

Mechanical equipment rooms

Computer rooms

Enclosed offices where dB levels are questionable

Common areas such as restrooms (strobes only)

Use a strobe-only device in the vicinity of the FCP

Surge Protective Device (SPD) Installation

Install a 120V SPD for the main FCP, each sub-FCP, and each booster power supply.

Install an SPD for each initiating device circuit, notification appliance circuit, data, and signaling line circuit entering/leaving each building that is monitored by the FCP.

SPDs shall be installed so that they are readily accessible for servicing.

If permitted by the FCP manufacturer, install SPDs in the FCP cabinet.

If the FCP manufacturer does not allow SPDs to be installed within the FCP cabinet, install one or more metal enclosures near the protected fire alarm equipment.  Provide separate enclosures for 120V and signal voltage devices, or provide one enclosure with a metal partition to separate the 120V from the signal voltage devices.

Install a single-point ground bar in the enclosure for the SPD.  Bond the ground bar to the enclosure and to the power circuit equipment-grounding conductor.  Connect each SPD to the ground bar with a separate 12 AWG solid, green-insulated ground wire.  Keep ground wires as short and straight as possible.

Install SPDs in accordance with manufacturer’s instructions, keeping leads and ground conductors as short and straight as possible.

Identification

Follow Section 26 0553, Identification for Electrical Systems, for all system components.

Label each conductor at each terminal and junction point.  Use wire markers specified in Section 26 0553, Identification for Electrical Systems.  On wire markers indicate the type of fire alarm circuit (e.g. Pull Stations, Fan Shutdown, Alarm Strobes, etc.).

Mark floor in front of cabinet(s) to show the NEC required working clearances according to Section 26 0553, Identification for Electrical Systems.

Label fire alarm junction boxes with 2-1/4” x 1/2” (minimum size) pressure sensitive vinyl markers having “FIRE ALARM” in red letters on a white background.

Label all devices with address/zone information.  Use self-adhesive vinyl labels with 3/4 inch (minimum) lettering easily visible without a ladder.

PAINTING

Exposed Surfaces: Paint exposed fire alarm conduit, panels, cabinets, pullboxes, supports, and other electrical equipment as follows:

Galvanized Surfaces: Paint for repairing galvanized materials shall be zinc-rich type.

Refinishing: Thoroughly clean and touch up shop-primed or finish-painted surfaces damaged in handling or installation with paint supplied with the equipment or an approved matching paint.

Interior Conduit: Paint new exposed interior conduit in rooms finished and/or occupied to match the existing background paint color.  Paint conduit to be painted with one coat of primer.  Paint conduit to match the existing background colors with two coats of paint to provide a minimum thickness of 6 mils.

EQUIPMENT INSTALLATION

Install devices or equipment not specifically covered by these specifications in accordance with manufacturer's instructions.

CONNECTION TO LANL CENTRAL STATION

Install 6 x 6 x 4 enclosure adjacent to the FCP with a conduit to the appropriate factory knockout.

Install a 3/4 inch conduit with measuring pull tape from the 6 x 6 x 4 enclosure to the main telecommunications room.

Install two GFE Category 5e telecommunications cables in the conduit and label each end of the cable as “emergency.”

LANL will terminate the telecommunications cable on two 8-pin RJ-31X telephone outlet jacks in a 2-port outlet that is mounted inside the 6 x 6 x 4 enclosure.  LANL will label one jack as “primary,” and the other as “backup.”

LANL will terminate the telecommunications cable pairs to two separate lines (numbers) at the telecommunications room, selecting dedicated numbers or low-usage (lobby, conference room, etc), voice-grade, loop-start DTMF numbers that provide timed-release disconnect.

LANL will connect the “primary” and “secondary” number ports on the DACT to the corresponding telephone outlet jacks.

CLEANING

Blow out junction boxes and fire alarm equipment not hermetically sealed with clear, dry, oil-free (15 psig maximum) air to remove dust and dirt prior to energizing.

FIELD QUALITY CONTROL

Provide the services of a qualified factory trained and certified technician for the FCP installed on this project.  The factory technician shall assure the completeness and correctness of the installation by performing the following:

Prepare as-built documentation of FCP indicating location of components, interconnection of components, and connections to alarm initiating, indicating and auxiliary circuits.

Field-verify and mark as-built drawings of fire alarm layout, conduit and wiring plans, and point-to-point field-wiring diagrams.

Verify correct labeling of fire alarm system conductors.

Verify that conductor sizes are adequate for each alarm initiating, indicating and auxiliary circuit.

Prepare as-built battery load calculations. Battery shall be sized to include the additional 50% safety margin above calculated system demand.

Measure and adjust audible alarm signal in all spaces to comply with ADAAG requirements: minimum 15 dBA above ambient, but not over 120 dBA at any location.

Test all devices for proper supervision and alarm operation.

Test all interlocks with HVAC and elevator system for proper operation in normal and by-pass modes.

Perform pre-final acceptance inspections and tests of the fire alarm system modifications.

Prepare final acceptance test plan when required (see Section 1.4-D).

After the pre-final test, provide a report to the LANL Project Leader indicating the status of the fire alarm system and any corrective actions required before the acceptance tests.

Submit a detailed test plan for the final acceptance test.

Submit the test plan (when required, see Section 1.4-D) not less than 10 working days before the planned final acceptance date.

Follow test methods outlined in NFPA 72.

Submit FCP program at least two weeks prior to final acceptance test.

Submit final drawings, calculations, and manufacturer’s data at least one week prior to final acceptance test.

Coordinate date of final acceptance test with installer, LANL Project Leader, LANL Fire Protection Group representative, and subtier subcontractors for HVAC, sprinklers, and elevator controls.  Make corrective actions before final acceptance test date.

FINAL ACCEPTANCE TEST

Notify lANL STR at a minimum of 2 weeks in advance of final acceptance tests.  The more advance notice will help minimize scheduling conflicts and delays. Perform final acceptance tests in the presence of authorized representatives of LANL’s STR, Fire Protection Division, and Facility Operations Director (FOD).

Before the final acceptance test begins, present a preliminary copy of the Record of Completion to the authorized representative of the LANL Fire Protection Group.

Preliminary Record of Completion shall be of the form required by NFPA 72.

Indicate on the preliminary Record of Completion that the pre-final inspections and tests have been performed and all corrective actions have been completed.

The final acceptance test shall not proceed before the Record of Completion is presented to the authorized representative of the LANL Fire Protection Group.

Perform final acceptance tests on the completed fire alarm system:

Follow the approved test plan and comply with NFPA 72 requirements.

Test FCP and the connected initiating, alarm, and auxiliary devices.

Perform 24-hour discharge test on the FCP batteries.

LANL Fire Protection will perform tests on connections made by other LANL groups.

LANL Telecommunications Group will perform the acceptance test of the telephone lines from the modular plug connectors, to verify telephone line continuity and switch features before turning lines over to the LANL Fire Protection Group.

At the final acceptance test, have marked-up shop drawings and point-to-point wiring diagrams available for review and verification.  Final acceptance test will not proceed without these as-built documents.  If LANL verification of the as-built documents reveals errors, re-verify the complete fire alarm raceway and wiring system in the presence of a LANL Fire Protection Group representative.

Correct deficiencies discovered in the final acceptance test and re-test fire alarm system until satisfactory test results are obtained.

Upon successful completion of acceptance tests, submit final “Record of Completion” and “Inspection and Testing Form” and “recommended spare parts” list per Para 1.4.A.

SYSTEM IDENTIFICATION PLACARD

Furnish and install a permanently mounted placard in or adjacent to the fire alarm control cabinet.

Provide the following information typewritten or engraved on the placard:

Name, address and telephone number of installing subcontractor.

Reference to the standards, including date of issue to which the system conforms (e.g. NFPA 72 and NFPA 70, latest edition).

Circuit number of power supply to FCP and location of the electrical panelboard.

Location of fire alarm system Operating and Maintenance Instructions if they are not stored in the FCP cabinet.

Location of fire alarm system as-built documents.

END OF SECTION

****************************************************************

Do not delete the following reference information:

****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 28 3100 Rev. 8, dated May 23, 2014.

Five (5) copies/sets of each deliverable below are required:

| Deliverable | Spec Ref. | 60% | 90% | 100% | Two weeks before pre-test | Before requesting final test | Upon Completion of Testing |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certifications | 1.4.B | X |  |  |  |  |  |
| Design Submittal Drawings including: Calculations Floor Plans Wiring Diagrams System Input/Output Matrix | 1.4.C | X X X X | X X X X | X X X X | X |  | X X X X |
| Catalog Data | 1.4.C.3 | X |  |  |  |  | X |
| Installation Instructions | 1.4.C.4 |  |  | X |  |  | X |
| Materials and Parts List | 1.4.C.5 | X | X | X |  |  | X |
| FCP Program | 1.4.C.6 |  |  | X | X |  | X |
| Operations & Maintenance Manual | 1.4.C.7 |  |  | X |  |  | X |
| Test Reports: Pre-final Test Report Test plan for Final Test (if unusual/requested) Record of Completion Inspection & Testing Form | 1.4.D |  |  |  |  | X X | X X |
| Project Record Documents (as-builts of all submitted items) | 1.4.E |  |  |  |  |  | X |
| Warranties | 1.4.F |  |  |  |  |  | X |