# SECTION 33 5100

# NATURAL GAS DISTRIBUTION

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

# PART 1 	GENERAL

SECTION INCLUDES

Site distribution gas piping system including above grade piping and appurtenances upstream of and including the low pressure regulator station.

LANL PERFORMED WORK

*************************************************************************************************************

Installed gas regulator stations are limited to stations identified in Civil Standard Drawings ST-G3060-2.  A-E shall provide the design and parameters for the regulators in accordance with Civil Standard Drawings ST-G3060-2 and for parameters outside Civil Drawings ST-G3060-2 contact the ES-UI System Engineer for regulator station design.

*************************************************************************************************************

LANL Utilities and Institutional Group (U&I) will tie into existing gas piping system.

LANL U&I will install regulator station and adjust outlet pressure of gas regulators.

ACTION SUBMITTALS

*************************************************************************************************************

# Submittals shall be approved by the LANL U&I Group gas system representative.

******************************************************************************************************************

Submit the following:

- Catalog data on regulators pipe materials, pipe fittings, valves, pipe coating, pipe pig, and accessories, and directional drilling pull (weak link) device and casing seals.

- Certified material inspection report for steel pipe.

- Certification of welders and qualified welding procedure.

- Certified Welding Inspector (CWI) inspection report

- [Submittals for the Horizontal Directional Drilling.]

- [Pipe pigging inspection report for 4 inch diameter and larger pipe and for all piping sizes with lengths greater than 500 feet.]

- [Tracing wire continuity test report, install with non-metallic pipe.]

- Catalog data on identification tape [and tracing wire].

- Total connected natural gas load in BTU’s per hour, heat input requirement for each connected device in BTU’s per hour, and pressure (psig) requirement at building wall.

QUALITY ASSURANCE

Welders Certification, Qualified Procedure Standard, and Weld Inspection/Testing.

      - Exterior Steel Pipe: API Standard 1104

On-site and joining welding shall comply with LANL ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4455, Onsite Welding & Joining Requirements.

          - Use LANL Welding Procedures

          - Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

Weld Inspection: Weld inspection acceptance shall be in accordance with API Standard 1104, Section 9, for steel pipe and LANL ESM Chapter 13 – Welding, Joining & NDE.  Certified Weld Inspector (CWI) shall visually inspect 100% of the completed welds. Inspector should make an effort to visually inspect weld fit up, root and second pass when on-site.

      - Plastic Pipe: Comply with ESM, Chapter 13 – Welding, Joining & NDE and 49 CFR 192.283 and 192.285.

On-site and joining welding shall comply with LANL ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4455, Onsite Welding & Joining Requirements.

          - Use LANL Welding Procedures

          - Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

Weld Inspection: Comply with ESM, Chapter 13 – Welding, Joining & NDE and 49 CFR 192.287 for PE pipe.

Clean and pig piping 4 inch diameter and larger, and all piping sizes with lengths greater than 500 feet.

LANL STR shall submit the material and accessory catalog data, certified material inspection report for steel pipe, and certification of welders and qualified welding procedure to the LANL U&I gas system engineer and the LANL construction inspector for verification of construction items and certifications during field quality assurance.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

POLYETHYLENE PIPING, BELOW GRADE

***************************************************************************************************************

Do not use polyethylene piping when design pressure exceeds gauge pressure of 100 psig 
(49 CFR 192.123). Provide 1 inch, 1-1/4 inch, 2 inch, or 3 inch PE service line and 2 inch minimum PE main line.

***************************************************************************************************************

Manufacturer: Performance Pipe (Driscopipe 8100 or Yellowstripe 8300), no substitution.

Pipe: Polyethylene, high density, ASTM D2513, PPI-PE4710, SDR11 iron pipe size, ASTM D3350 cell classification number 445574C.  Provide and install SDR-9 polyethylene pipe when performing horizontal directional drilling or other pipe pulling operation.

Fittings: Polyethylene, high density, butt heat fusion type, ASTM D2513, PE4710, SDR 11, ASTM D3350 cell classification number 445574C.

STEEL PIPING, BELOW GRADE

*************************************************************************************************************

Contact a LANL U&I Group gas system representative for approval to use steel piping below grade. Provide minimum 2 inch steel service line.

*************************************************************************************************************

Pipe: Standard wall, black steel, ASTM A53, Type E, Grade B or API 5L EW, Grade B or ASTM A106, Grade B.

Fittings: Standard wall, black steel, butt-welding type, ASTM A 234, Grade WPB.

Coating: Factory applied fused system consisting of; an adhesive primer layer, with minimum 10 mil thermoplastic elastomer layer and minimum 40 mil polyolefin top layer containing UV protection; or alternate of an epoxy primer layer with minimum 50 mil high density polyethylene top layer; or an approved equal by the LANL U&I Group gas system representative.

Manufacturers:

- Tyco Adhesives, Synergy Plant Coating System

- Tyco Adhesives, VANGUARD Plant Coating System

Product marking shall be in accordance with ASTM A53, Section 21. Product marking shall be transferred to and stenciled to the outside of the pipe coating. Minimum transferred information shall include; pipe specification, grade, size, type, and heat number in accordance with the certified material test report and the product marking.

STEEL PIPING, ABOVE GRADE

Pipe: Standard wall, black steel, ASTM A53, Type E, Grade B or API 5L EW, Grade B or ASTM A106, Grade B.  Welded for pipe sizes above 2 inches, threaded for pipe sizes 2 inches or less.

Fittings: Malleable iron, threaded type, ANSI B16.3, Class 150 or standard wall, black steel, butt welding type, ASTM A234, Grade WPB.

Flanges: Forged steel, ASTM A105, ANSI Class 150, weld neck, raised face, dimensions per ANSI B16.5.

Gasket Material: Neoprene, durometer hardness 50-65.

PRESSURE REGULATOR STATION

*************************************************************************************************************

Regulator stations are limited to the stations and regulators identified in the Civil Standard Drawings ST-G3060-2.

*************************************************************************************************************

LANL's U&I group will install, and adjust outlet pressure of gas regulator station in conjunction with the subcontractor.

SHUT-OFF VALVE, ABOVE GRADE, THREADED ENDS

Manufacturer: Balon Series S, No Substitution.

Valve: Ductile iron body, threaded ends, non-lubricated full port opening ball valve, lever-operated, 1000 psig working pressure, size [ 1 ], [ 2 ] inch.

SHUT-OFF VALVE, ABOVE GRADE, FLANGED ENDS

Manufacturer: Balon Series F, No Substitution.

Valve: Steel body, flanged ends, non-lubricated full port opening ball valve, lever-operated, Class 150, size [ 2 ], [ 3 ], [ 4 ] inch, or gear operated, Class 150, size [ 6 ], [8], [10] inch.

SHUT-OFF VALVE, ABOVE AND BELOW GRADE, WELDED ENDS

Manufacturer: Balon US Series Weld X Weld, No Substitution.

Valve: Steel body, butt welded ends, non-lubricated full port opening ball valve, wrench operated, Class 150, size [ 2 ], [ 3 ], [ 4 ], [ 6 ] inch.

SHUT-OFF VALVE, BELOW GRADE, POLYETHYLENE

Manufacturer: Nordstrom Poly-Gas.

Ball Valve for natural gas service ASME B16.40, ASTM D 2513, material PPI- PE 4710 (PE 3408), for use with Performance Pipe (Driscopipe 8100 or Yellowstripe 8300 designation), SDR11, iron pipe size 100 psig service pressure, butt fusion end connections.  Full bore when available.

- Valve Size: [ 1 ], [ 1 1/4 ], [ 2 ], [ 3 ] , [ 4 ] inch.

ANODELESS RISER

Manufacturer: R.W. Lyall and Company, Inc.

Prebent, for use with Performance Pipe (Driscopipe 8100 or Yellowstripe 8300) polyethylene piping, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size NPT steel end by PE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, API 5L EW, Grade A or ASTM A53, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch and larger.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per ASTM D2513, Category 1.

TRANSITION FITTING

Manufacturer: R.W. Lyall and Company, Inc.

Preformed steel pipe to PE pipe, for use with Performance Pipe (Drisopipe 8100 or Yellowstripe 8300) polyethylene piping, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size beveled steel end for welding by PE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, API 5L EW, Grade A or ASTM A53, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch and larger.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per ASTM D2513, Category 1.

VALVE BOX

Manufacturer: Tyler, Series 6860

Valve Box: Cast iron, 5 1/4 inch shaft screw type, with lid marked gas, length to suit burial depth.

TEST PLUG (PETE’s PLUG)

1/4 inch NPT, brass body, neoprene core, rated for 1,000 psig, complete with sealing cap and gasket, to receive 1/8 inch O.D. probe.

EXECUTION

  - preparation

Ream pipe ends and remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

  - GENERAL INSTALLATION

Furnish and install gas piping in accordance with Uniform Plumbing Code, Uniform Mechanical Code, ASME B31.1 Power Piping, ASME B31.8 Gas Transmission and Distribution Piping Systems, and 49 CFR 192 Code of Federal Regulations.

Do not run gas piping below buildings, structures, or in crawl spaces.

Do not run gas piping under walks and equipment pads adjacent to building.  If unavoidable, sleeve line with non-metallic piping.

Pressure test piping in accordance with Section 22 0813, Testing Piping Systems.

Paint outside gas regulator piping, valves, and appurtenances above ground to match building exterior.  Refer to Section 09 9100, Painting.

Support piping in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

Test steel pipe coating in accordance with Section 22 0813, Testing Piping Systems.

Minimum cover over pipe shall be measured from finish grade to top of pipe.

cleaning of natural gas piping interior

Use a pipeline pig to clean the interior of natural gas piping.  The pipeline pig used shall be of a type and configuration to provide optimum cleaning of scale, debris, and moisture from the pipeline interior.

      - Soft pigs shall be used with polyethylene pipe to avoid damage to the pipe.

A pressuring system shall be used to provide sufficient energy to drive the pig but to not overpressure the pipeline, the pressure to drive the pig shall not exceed the final test pressure.

A pig catcher of a design to provide a safe and effective means to receive the pig as it discharges from the line shall be used.

POLYETHYLENE PIPING INSTALLATION

# *************************************************************************************************************

# Refer to Civil Standard Drawing ST-G30GEN-4 for trench width and piping burial depth.

# *************************************************************************************************************

Lay piping on trench bottom in such a manner as to snake piping from one side of trench to the other with one cycle approximately every 40 feet.  This will insure that sufficient piping material is available for expansion and contraction.

Provide minimum of 5 feet of cover over piping installed under any roadways and vehicle parking areas.  Minimum cover over pipe shall be from finish grade to top of pipe.

*************************************************************************************************************

Use steel pipe if gas line is installed less than 20 feet from steam and condensate lines.

*************************************************************************************************************

Perform butt heat-fusion joining in accordance with ASTM D2657 and manufacturer’s written instructions.  See PART 1, Quality Assurance.

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G30GEN-3 and ST-G30GEN-4 for trenching, piping burial depth, warning tape, and tracer wire details.

Refer to the Engineering Standards Manual, Civil Chapter, Section G30, for required minimum utility line clearances

*************************************************************************************************************

Refer to Drawings and Section 31 2000, Grading, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Make plastic-to-steel connection with transition fitting that is butt fused on plastic end and welded on steel end.

horizontal directional drilling or cased boring

Crossing of paved streets or roadways or other areas, if approved by LANL U&I group representative, may be accomplished by horizontal directional drilling (HDD) or cased boring, whenever practical. Casings for steel carrier pipe are not allowed. The bore shall be kept to a maximum of 2 inches larger than the pipe or the casing. Care shall be exercised to ensure the paved surface is not damaged during the boring operation.

Top of HDD or casing shall have a minimum below grade bury depth of 36 inches and a minimum bury depth of 60 inches below any paved surface. Any casing shall be designed to withstand superimposed loads. Depth shall not exceed excavation by standard, conventional means and shall be approved by LANL U&I group representative.

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturer’s recommendation. Both pipe ends shall be monitored for continuous, smooth movement. Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below. Manufacturer’s procedures and design parameters shall be followed, in addition to ASTM F1962.

The pipe shall be inserted into the casing in such a manner that the pipe and the casing insulators will not be damaged. Polyethylene pipe shall extend 3-5% of the pulled-in length past the termination points to allow for contraction. Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished. A minimum of five (5) feet of pipe shall extend beyond the borehole or casing to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

The annulus between the casing and the pipe shall be sealed with a waterproof mechanical seal, e.g., a Link-Seal. Polyethylene pipe shall be allowed to snake in the casing and centering spacers are not required.

STEEL PIPING INSTALLATION

Butt weld underground steel piping.  See PART 1, Quality Assurance.

Use threaded joints for above grade piping 2 inches and smaller and butt-welded joints for piping above 2 inches.

Apply Polyken primer 1019 or 1027 to underground joints, fittings, and valves, and spiral wrap with a double layer, half lapped, 35 mil tape, Polyken 934 system.  Follow manufacturer’s instructions.

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G30GEN-3 and ST-G30GEN-4 for trenching, warning tape, and tracer wire details.

Refer to the Engineering Standards Manual, Civil Chapter, Section G30, for required minimum utility line clearances

*************************************************************************************************************

Refer to Drawings and Section 31 2000, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

piping TIE-IN

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G3060-1 for gas piping tie-in details

*************************************************************************************************************

Tie-in to existing system will be performed by LANL U&I.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  Tie-in will be inspected by LANL STR and the LANL U&I Group gas system representative.

LANL STR will notify LANL U&I group at least 15 working days in advance to schedule tie-in.

Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL U&I Group and bell hole excavation meets access and OSHA requirements.

CORROSION CONTROL (STEEL PIPING BELOW GRADE)

*************************************************************************************************************

Contact LANL U&I Corrosion Specialist or the LANL U&I Group Gas System Representative for cathodic protection requirements.  Also refer to the ESM Electrical Chapter, Section G4040.

*************************************************************************************************************

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 5100 Rev. 7, dated August 28, 2012.