SECTION 33 6300

STEAM ENergy DISTRIBUTION

************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

************************************************************************************************************

GENERAL

SECTION INCLUDES

Site steam and condensate distribution piping, fittings, valves, steam trap, etc.  See definitions below.

LANL PERFORMED WORK

LANL’s MSS Utilities Work Group will tie into existing site steam piping systems and condensate piping systems.

DEFINITIONS

*******************************************************************************

Design all piping upstream of the building steam PRV for 150 psig and 500 degrees F.  Design condensate piping for 150 psig and 250 degrees F.

Piping shall enter the structure in a designated mechanical equipment room.

*******************************************************************************

Site Steam Distribution Piping: Steam piping upstream of first steam shutoff valve inside building.

Site Condensate Distribution Piping: Condensate piping downstream of condensate shutoff valve inside building, including steam trap piping upstream of first steam shutoff valve.

SUBMITTALS

****************************************************************************

Submittals shall be approved by the LANL Steam System Engineer.

****************************************************************************

Submit the following in accordance with Section 01 3300, Submittal Procedures:

Catalog data on pipe and pipe fittings, valves, steam traps, welding rod.

Certified material test report for the pipe.

Certification of welders and qualified welding procedures.

Welding Process Visual Examination Report.

Installation instructions for pre-insulated steam/condensate piping.

Plan and profile for steam/condensate piping system.

Thermal expansion calculation for steam/condensate piping system.

QUALITY ASSURANCE

Welding

Welders: Certified in accordance with Section IX of ASME Boiler and Pressure Vessel Code.

Welding Materials and Procedures: Comply with Section IX of ASME Boiler and Pressure Vessel Code.

Visual Examination: Comply with ASME B31.1, Power Piping.

Dimensions

Dimensions (valves, fittings and flanges): Comply with ASME B16 series standards.

Installation

Distribution Piping: Comply with ASME B31.1, Power Piping.

PRODUCTS

******************************************************************************************************

Distribution piping, fittings, and materials described herein are generally restricted to a maximum 150 psig working steam pressure (WSP) with 500 degrees F temperature.  For other pressure and temperature ratings, additional specification and restrictions may be required. Different products or materials are listed for each application.  Select one or any combination for the application.  Refer to Part 3 for valves and strainers installation instruction.

*******************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

STEAM PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Pipe: Black steel, A106, Grade B, Schedule 40.

Fittings (socket weld): Forged steel, ASTM A105, Class 3000.

Fittings (butt weld): Wrought carbon steel, ASTM A234, Grade WPB, Schedule 40.

Joints: Welded.

CONDENSATE PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Pipe: Black steel, Schedule 80, ASTM A53, Type E or S, Grade B or A106, Grade B.

Fittings (socket weld): Forged steel, ASTM A105, Class 2000 or 3000.

Fittings (butt weld): Wrought carbon steel, ASTM A234, Grade WPB, Schedule 80.

Joints: Butt welded for pipe size 2 1/2 inches and larger and socket welded for 2 inches and below.

pre-insulated STEAM PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Manufacturer: Perma-Pipe, Multi-Therm 500, or Thermacor, Duo-Therm 505, factory prefabricated, pre-insulated piping system, suitable for 500 degrees F.

Distribution Pipe: Black steel, A106, Grade B, Schedule 40.

Outer Conduit: Black steel, minimum 10 gage thickness.

Distribution Pipe Insulation: Mineral wool contained within a drainable, dryable, pressure tested steel conduit.

Outer Conduit Insulation: One-inch minimum polyurethane foam, ASTM C591, encased in fiberglass (FRP) jacket or high-density polyethylene (HDPE) jacket.

Pipe Fittings (socket weld): Forged steel, ASTM A105, Class 3000.

Pipe Fittings (butt weld): Wrought carbon steel, ASTM A234, Grade WPB, Schedule 40.

Joints: Butt welded for pipe size 2 1/2 inches and larger, and socket welded for 2 inches and below.

pre-insulated CONDENSATE PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Manufacturer: Perma-Pipe, Poly-Therm, or Thermacor, Ferro-Therm, factory prefabricated, pre-insulated piping system.

Distribution Pipe: Black steel, Schedule 80, ASTM A53, Type E or S, Grade B or A106, 
Grade B.

Conduit Insulation: One-inch minimum Polyurethane foam, ASTM C591, encased in fiberglass (FRP) jacket or high-density polyethylene (HDPE) jacket.

Pipe Fittings (socket weld): Forged steel, ASTM A105, Class 3000.

Pipe Fittings (butt weld): Wrought carbon steel, ASTM A234, Grade WPB, Schedule 80.

Joints: Butt welded for pipe size 2 1/2 inches and larger, and socket welded for 2 inches and below.

STEAM PIPING, ABOVE GRADE AND IN STEAM PITS (150 PSIG MAXIMUM)

Pipe: Black steel, A106, Grade B, Schedule 40 (welded pipe).

Pipe: Black steel, A106, Grade B, Schedule 80 (threaded pipe).

Fittings (threaded): Forged steel, ASTM A105, Class 3000.

Fittings (socket weld): Forged steel, ASTM A105, Class 3000.

Fittings (butt weld): Steel, ASTM A234, Grade WPB, Schedule 40.

Joints: Threaded or socket welded for pipe sizes through 2 inch, butt welded or flanged for pipe sizes above 2 inch.

CONDENSATE PIPING, ABOVE GRADE AND IN STEAM PITS (150 PSIG MAXIMUM)

Pipe: Black steel, Schedule 80, ASTM A53, Type E or S, Grade B or A106, Grade B.

Fittings (threaded): Forged steel, ASTM A105, Class 2000 or 3000.

Fittings (socket weld): Forged steel, ASTM A105, Class 3000.

Fittings (butt weld): Steel, ASTM A234, Grade WPB, and Schedule 80.

Joints: Threaded or socket welded for pipe sizes through 2 inch, butt welded or flanged for pipe sizes above 2 inch.

FLANGES, FOR PIPE SIZES OVER 2 Inches

Forged steel, ASTM A105, ANSI Class 150, weld neck, raised face, dimensions per ANSI B16.5

GASKET MATERIAL

Manufacturer:  Flexitallic style CG; or Garlock style RW or Edge; or Lamons style WR.

Steam and Condensate Flanges Piping: Spiral wound metal with solid metal outer ring – winding metal of 304SS, filler of graphite, outer ring of carbon steel to ANSI B16.20 dimensions.  Gasket thickness 0.175 inch and outer ring 1/8 inch thick.

BOLTS, STUDS AND NUTS

Bolts/Studs: Alloy steel, ASTM A193, Grade B7.

Nuts: Alloy steel, ASTM A194, Grade 2H.

SMALL STEEL GATE VALVES (THREADED or SOCKET WELD ENDS)

Manufacturer: Vogt, Series 12111; or Velan, 2054B-02TY series.

Forged steel, ASTM A105, Class 800, steam service, 500 degrees F at 
1595 psig, conventional port, bolted bonnet, rising stem, threaded or socket weld ends, hard faced seat and disc or 13% chrome disc and stem, stellite 6 faced seat.

LARGE STEEL GATE VALVES (FLANGED ENDS)

Manufacturer: Velan, 0064C-02TY series.

Cast carbon steel, ASTM A216, Grade WCB, full port, bolted bonnet, Class 150, steam service, 500 degrees F at 170 psig, rising stem, flanged to B16.5 dimensions,  13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat.

SMALL STEEL GLOBE VALVES (THREADED ENDS)

Manufacturer: Vogt, Series 12141; or Velan, 2014B-02TY

Forged steel, ASTM A105, Class 800, steam service, 500 degrees F at 1595 psig, conventional port, bolted bonnet, rising stem, threaded or socket weld ends, hard-faced seat and disc, or 13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat.

LARGE STEEL GLOBE VALVES (FLANGED ENDS)

Manufacturer: Velan, 0014B-02TY

Cast carbon steel, ASTM A216, Grade WCB, bolted bonnet, Class 150, steam service, 500 degrees F at 170 psig, rising stem, flanged to B16.5 dimensions, 13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat and disc.

SMALL STEEL CHECK VALVES (THREADED ENDS)

Manufacturer: Check-All CN[size]SSMT.125IX or Durabla SCV with seal welded body

Spring-assisted, in-line, threaded, 316SS body, Inconel X-750 spring, cracking pressure of less than 0.25 psi, metal-to-metal seat, cold working pressure of at least 750 psig.

STRAINERS (THREADED ENDS)

“Y” Type, rated for 600 psig steam, 20 or higher gage mesh stainless steel screens, steel body, ASTM A216, grade WCB, with blowoff gate valve and plug.  Manufacturer:  Keckley, SB-7

STRAINERS (FLANGED ENDS)

“Y” Type, Class 150 psig, steam service, 20 or higher gage mesh stainless steel screens, steel body, ASTM A216, grade WCB, with blowoff gate valve and plug.  Manufacturer:  Keckley, SA-7

thermostatic trap  (THREADED ENDS)

Manufacturer:

Yarway, 761-5 Bellows type.

Bestobell, GM16

Trap: Carbon steel or stainless steel body, stainless steel trim, integral strainer, rated pressure of 300 psig at 650 degrees F.

Size, 3/4 inch or larger as determined by the LANL Steam System Engineer.

expansion Joints

*********************************************************************

Contact LANL Steam System Engineer for review and approval for use of appropriate expansion joint in piping system.  Consult with manufacturer for part number.

*********************************************************************

Manufacturer: ADSCO Corruflex Equalizing series S11E10O.

Metal expansion joint, single controlled flexing bellows with ANSI flanged ends. 304 Stainless steel bellows.  Rated pressure and temperature 150 psig / 500 degree F.

EXECUTION

  - PREPARATION

Ream pipe and tube ends. Remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

BURIED PIPING

*******************************************************************************

Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping. Comply with Civil Standard Drawing ST-G30GEN-3 for tracer wire/test station details and Civil Standard Drawing ST-G30GEN-4 for trenching detail.

Refer to the LANL Engineering Standards Manual, Civil Chapter, Section G30, for required utility line clearances.

********************************************************************************

Refer to Drawings and Section 31 2000, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

INSTALLATION

Install in accordance with manufacturers’ instructions.

Route piping in orderly manner and maintain gradient.

Provide sleeve and packing gland or compressible modular seal between sleeve and pipes penetrating exterior walls or manholes below grade to provide a waterproof installation.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide clearance for installation of insulation and access to valves and fittings.

Slope steam and condensate piping 1 inch in 40 feet (0.25 percent) in direction of next low point.

Install valves with stems upright or horizontal, not inverted.

Use steel valves and strainers in piping above grade and in steam pits.

Provide eccentric reducers, flat on bottom, in horizontal runs of steam and condensate piping where line size changes.

Provide globe valves for throttling, bypass, or manual flow control services.

Provide gate valves for first steam valve inside building.

Connect steam and condensate branch lines into top of main or at a 45-degree angle from top of main.

Pressure test piping in accordance with Section 22 0813.

Support piping in accordance with section 22 0529.

Insulate piping in accordance with Section 22 0713.

Install factory prefabricated, pre-insulated underground distribution piping in accordance with manufacturer’s instructions. Piping manufacturer shall provide factory trained field technical assistance for critical installation periods, e.g., field joint instructions, pressure testing.

Locate first steam shutoff valve inside building within 5 feet of building wall penetration.

PIPING TIE-IN

*****************************************************************************

Contact LANL Steam System Engineer for point of tie-in and required details. Designer shall submit required details for specific installation to LANL Utilities Group for final approval.  Refer to the ESM Civil Standard Drawings ST-G3040-1 for tie-in detail.

*****************************************************************************

Tie-in to existing steam and condensate piping systems will be performed by LANL’s Utilities Work Group.  Excavation, backfill and materials required for tie-in shall be provided by Contractor.  The tie-in will be inspected by the LANL Subcontract Technical Representative (STR) and the LANL Steam System Engineer.

Notify LANL STR at least 15 working days in advance to schedule tie-in.  The LANL STR will notify LANL’s Utilities Work Group.

Prior to notifying Utilities Work Group, the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, and material submittals and all test reports have been approved by LANL Utilities Group.

CORROSION CONTROL (only for Maintenance by LANL UTILITIES)

****************************************************************************

Contact Utilities Corrosion Specialist (665-5270), or the LANL Gas System Engineer for cathodic protection requirements.

NOTE: Factory pre-insulated piping systems (e.g., Perma-Pipe, Poly Therm).

NOTE: Pipe coating or cathodic protection is not required for steam piping.

****************************************************************************

Buried Condensate Pipe and Joint Coating: Field coating shall be a minimum of 30 mils thick and suitable for a continuous operating temperature of 250 degrees F.

Joints and Fittings: Apply a hand brush application of Polyken 1627 primer and a double layer of half-lapped tape, Polyken 1636, 30 mil.

Apply field coatings in accordance with the manufacturer’s instructions.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 6300 Rev. 3, dated March 25, 2009.