SECTION 33 8126

COMMUNICATION UNDERGROUND DUCTS, MANHOLES, AND HANDHOLES

****************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file at https://engstandards.lanl.gov

Rev. 1 Summary of Changes Revised PART 2 spacing, pulling irons, manhole accessories.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This template must also be edited to delete requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Communications POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

****************************************************************************************************************

GENERAL

SECTION INCLUDES

****************************************************************************************************************

Edit the following articles to match Project requirements. Delete systems not applicable to Project.

****************************************************************************************************************

Underground ductbanks for open telecommunications utility systems.

Underground ductbanks for secure communications cables.

Manholes for open telecommunications utility systems.

Manholes for secure communications cables.

LANL-Performed Work

****************************************************************************************************************

Edit the following articles to match Project requirements. Delete systems not applicable to Project.

****************************************************************************************************************

LANL Telecommunications Group will order through project, install, and test open telecommunications cables.

LANL Secure Communications will order through project, install, and test secure communications cables.

SUBMITTALS

Action Submittals

*************************************************************************************************************

Delete the following article if manholes are not needed.

*************************************************************************************************************

Catalog Data: Describing pre-cast manhole(s), manhole frame(s) and lid(s), ladders, and cable racks. Include data substantiating that materials comply with specified requirements.

Closeout Submittals

Project Record Documents: Accurately record GPS-based survey locations of ductbanks, new and existing manholes, and places where ductbanks cross other underground systems.

QUALITY ASSURANCE

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1 – Standard Practices for Good Workmanship in Electrical Construction and NECA/NEMA 605 – Recommended Practice for Installing Underground Nonmetallic Utility Duct.

SEQUENCING AND SCHEDULING

Notify LANL Subcontract Technical Representative (STR) to schedule inspection of each ductbank or ductbank segment before concrete is placed.

Notify LANL STR 10 days before duct tests.

****************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

****************************************************************************************************************

For secure communication ductbank systems, notify the LANL STR at least 30 days prior to the scheduled start of construction of the ductbank to have design drawings and appropriate application forms submitted to the LANL CNI Site Coordinator.  Once approval has been obtained from same, the LANL STR will inform Subcontractor that construction may begin.

****************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

****************************************************************************************************************

For secure communication ductbank systems notify the LANL STR at least 3 working days prior to the scheduled concrete encasement of the ductbank. The LANL CNI Site Coordinator must inspect the secure ductbank prior to encasing with concrete.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500 – Substitution Procedures.

  - INTERMEDIATE METAL CONDUIT AND FITTINGS

IMC: UL1242 – Intermediate Metal Conduit and ANSI C80.6 – Intermediate Metal Conduit.

Fittings and conduit bodies: Zinc-plated, threaded, malleable iron, meeting UL514B – Fittings for Conduit and Outlet Boxes, and ANSI/NEMA FB1 – Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit and Cable Assemblies.

  - RIGID Metal CONDUIT AND FITTINGS

Conduit per UL6 – Rigid Metal Electrical Conduit and ANSI C80.1 – Rigid Steel Conduit, Zinc Coated.

Fittings and conduit bodies: Zinc-plated, threaded, malleable iron, meeting UL514B and ANSI/NEMA FB1.

  - PLASTIC-COATED STEEL CONDUIT AND FITTINGS

Conduit or IMC:  PVC exterior coated, urethane interior coated, galvanized rigid steel per NEMA RN 1 – PVC Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit.

Conduit bends must be long, sweeping bends with a radius not less than:

1.  	Six times the internal diameter of conduits 2 inches or smaller, or

2. 	Ten times the internal diameter of conduits larger than 2 inches.

Fittings and conduit bodies: 40 mil PVC exterior coated, urethane interior coated, zinc-plated, threaded, malleable iron meeting UL514B – Fittings for Conduit and Outlet Boxes and NEMA RN 1 – PVC Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit.

  - RIGID NON-METALLIC CONDUIT AND FITTINGS

Conduit:  PVC per UL651 – Schedule 40 and 80 Rigid PVC Conduit and NEMA TC 2 – Electrical Plastic Tubing and Conduit, ANSI C80.3.

Fittings: Solvent-welded socket fittings meeting UL514C – Non-Metallic Fittings for Conduit and Outlet Boxes, and NEMA TC 3 – PVC Fittings for Use with Rigid PVC Conduit and Tubing.

  - UTILITIES DUCT AND FITTINGS

PVC type EB, 90 degree C rated, utilities duct for concrete encasement per NEMA TC 6 – Plastic Utilities Duct for Underground Installation, ANSI C130.2, ASTM F 512 – Standard Specification for Smooth-Wall PVC Conduit and Fittings for Underground Installation, and UL-651A – Type EB and A Rigid PVC Conduit and HDPE Conduit.

PVC fittings per NEMA TC 9 – Fittings for Plastic Utilities Duct for Underground Installation and ASTM F 512 – Standard Specification for Smooth-Wall PVC Conduit and Fittings for Underground Installation.

  - DUCT SPACERS

Duct spacers must provide 3-inch separation between ducts and 3-inch concrete coverage on bottom, sides, and top (for secure communications, 6 inches for all dimensions).

  - GROUND CABLE

Use 4/0 AWG bare-stranded, soft-temper, copper cable per ASTM B 8, Standard Specification for Concentric-Lay Stranded Copper Conductors.

  - CORROSION PROTECTION TAPE

Pressure-sensitive, 10-mil thick, PVC-based tape for corrosion protection of metal conduit and fittings.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

  - UNDERGROUND WARNING TAPE

Furnish non-detectable underground warning tape for underground duct banks.

Use 6 inch wide, minimum 4.0 mils thick, high visibility, continuously printed, inert fiber reinforced polyethylene for direct burial service underground warning tape with an orange background color.

Black lettering stating:

"CAUTION BURIED COMMUNICATION LINE BELOW."

  - Raceway MEASURING/Pulling TAPE

Raceway measuring/pulling tape with permanently printed measurements in one-foot increments and minimum 1,200 lb. average breaking strength.

*************************************************************************************************************

Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - INSULATING BUSHINGS

NRTL-listed insulating bushings with 105 ºC rated insulation.

*************************************************************************************************************

Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - GROUNDING BUSHINGS

NRTL-listed, galvanized malleable iron, 150ºC rated insulated throat grounding bushings with lay-in type ground cable lugs.

*************************************************************************************************************

Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - DUCT PLUGS

Soft, expansible gasket material compressed with non-metallic plates and bolts to produce a positive seal against water and gas in unused ducts.

*************************************************************************************************************
Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - DUCT SEALANT

Expandable foam duct sealant kits to prevent water and gas from entering manholes, vaults, or structures.

*************************************************************************************************************

Edit manhole size(s) to match Project requirements. Delete article if manholes are not needed. Refer to LANL Standard Details ST-G4010-35, ST-G4010-36, and ST-G4010-37.  Provide manhole plans and details in the Drawings.

*************************************************************************************************************

  - PRE-CAST MANHOLES

Per ASTM C 858 – Standard Specification for Underground Precast Concrete Utility Structures.

Telecommunications manholes with the following minimum inside dimensions: 12'-0" long, 6'-0" wide, 7'-0" high or 8’-0” long, 6’-0” wide, 7’-0” high.  Coordinate requirements with LANL Telecommunications Group through the LANL STR.

Minimum thickness of floor, walls, and roof: 6 inches.

Minimum design loading meeting ASTM C 857 – Standard Practice for Minimum Structural Design Loading for Underground Precast Concrete Utility Structures

Manholes not subject to vehicle traffic: design live load to be 300 lb/sq ft minimum.

Manholes installed in a street or parking area: Design live loading shall be AASHTO HS-20 per AASHTO HB-17.

Manhole floor shall be cast integral with walls to form the bottom ring.

Furnish a keyed joint between the bottom ring and top ring.

*************************************************************************************************************

Edit knockout sizes and locations to match Project requirements.

*************************************************************************************************************

Coordinate locations of knockout panels in telecommunications manholes with LANL Telecommunications Group through the LANL STR.

Position a 12-inch diameter sump hole with cast iron cover in the floor centered under the access opening.

Locate a 36-inch diameter access opening centered in the roof of the manhole.

Furnish pre-cast concrete grade rings:  As required to place top of manhole flush with paving or 2 to 4 inches above finished grade and with minimum inside diameter of 36 inches.

Furnish cast iron manhole steps at 12 inches on-centers and the first step not to exceed 12” from the top of the frame.

Furnish lifting inserts in each manhole section for unloading and positioning.

Pulling irons: Hot-dip-galvanized steel with a capacity of 8,000 lb. and a safety factor of two.  Position one iron under each knockout panel and two along each side wall (total of six).

Embed 1-5/8 inches x 1-5/8 inches hot dip galvanized steel continuous pre-set inserts in each side wall of manhole.

Orient inserts horizontally and space 20 inches apart with bottom insert 12 inches above the floor.

Extend inserts to within 6 inches of end walls.

Manufacturer: Unistrut, P3200 series.

Manufacturers:   Jensen Pre-Cast; Old Castle Infrastructure; Vaughn Concrete Products, Inc.

*************************************************************************************************************

Delete the following article if manholes are not needed.

*************************************************************************************************************

  - PREMOLDED JOINT FILLER

Closed cell expanded neoprene joint filler conforming to ASTM D1056 – Standard Specification for Flexible Cellular Materials - Sponge or Expanded Rubber.

Manufacturer: Williams Products, Inc., Type NN-1; ConSeal Concrete

*************************************************************************************************************

Delete the following article if manholes are not needed.

*************************************************************************************************************

  - MANHOLE ACCESSORIES

Heavy duty, cast-iron manhole frame with solid lid.

Material: ASTM A48 – Standard Specification for Gray Iron Castings, Class 35B.

Frame and lid suitable for AASHTO HS-20 wheel loads.

Minimum clear opening through the frame: 36 inches.

Lid lettering “Communications.”

Manufacturer: Neenah Foundry Company, R-1640 Series.

Furnish hooked manhole ladder meeting OSHA 29 CFR 1910.27 and ANSI A14.3 – Safety Code for Fixed Ladders.

Material: ASTM A36 – Standard Specification for Structural Steel.

Manufacturer: Condux International; INWESCO.

Furnish hot dip galvanized steel telescoping ladder safety post in manholes with two or more grade ring steps. Manufacturer: Bilco LU-2.

Furnish hot-dip-galvanized cable racks and cable-rack supports for manholes.

Furnish 7-inch-long and 3-inch-long cable rack hooks.  Coordinate quantity and types with the LANL STR.

Manufacturer: INWESCO; Condux International.

EXECUTION

  - PREPARATION

Install underground ductbank systems per the NEC, the NESC, NECA/NEMA 605 – Recommended Practice for installing Underground Nonmetallic Utility Duct, and the requirements in this Section.

Duct bank system routing shown on Drawings is in approximate locations unless dimensioned. Route as required to complete the system.

Coordinate underground ductbank system work to avoid interference with other trades and existing utilities.

Verify routing and termination locations of duct banks before excavation for rough-in.

Verify that field measurements are as shown on Drawings.

Position trench so concrete envelope of ductbanks will have the following minimum horizontal and vertical separations from parallel or perpendicular runs of other utility pipes or conduits.

*************************************************************************************************************

Ensure dimensions in table below meet ESM Chapter 3 Civil, Section G20, Rev.4 or later (when issued).

*************************************************************************************************************

| UTILITY TYPE | PARALLEL LINES | PERPENDICULAR CROSSINGS |
| --- | --- | --- |
| Water | 36 inches horizontal separation | 24 inches |
| Gravity Sewer | 36 inches horizontal separation | 24 inches |
| Force Main Sewer | 36 inches horizontal separation | 24 inches |
| Storm Drain | 36 inches horizontal separation | 24 inches |
| Natural Gas | 60 inches horizontal separation | 24 inches |
| Steam or Hot Water | 60 inches horizontal separation | 24 inches |
| Open Communications | 24 inches horizontal separation of tamped soil or 3 inches of concrete | 12 inches vertical separation of tamped soil or 3 inches of concrete |
| Secure Communications | 36 inches horizontal separation of tamped soil or 6 inches of concrete; verify case-by-case with LANL CNI Team | 24 inches vertical separation of tamped soil or 6 inches of concrete; verify case-by-case with LANL CNI Team |
| Electrical | 12 inches horizontal separation of tamped soil or 3 inches of concrete | 12 inches vertical separation of tamped soil or 3 inches of concrete |

*************************************************************************************************************

The Drawings should contain detail(s) reflecting the requirements in LANL Standard Details ST-G30GEN-4 and ST-G30GEN-5.

*************************************************************************************************************

  - EXCAVATION AND BACKFILL

Make excavation for manholes and underground ductbanks to depth required and to provide solid bearing.

Set excavation so top of telecommunication ductbank concrete encasement will be not less than 24 inches below finished grade or paving.

*************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

*************************************************************************************************************

Set excavation so top of secure communications ductbank concrete encasement will not be less than 36 inches below finished grade or paving (the secure duct is to be not less than 1 meter deep).

Grade trenches for underground ductbanks to a minimum of 4 inches per 100 ft. toward manholes.

Keep excavation dry during installation of work.

Make trenches of sufficient width to receive work to be installed and provide specified concrete coverage on sides.

Backfill excavations for ductbanks and manholes in 6-inch layers; use soil excavated; remove roots, rocks, and sharp objects.  Furnish coarse sand as required for additional backfill material.

Moisture condition backfill soil and compact in accordance with ASTM D 1557 to 95% of maximum density under paved areas and 90% of maximum density under unpaved areas.

Overfill excavations to allow for settlement.

Refer to Section 31 2000 – Earth Moving for additional requirements.

*************************************************************************************************************

Edit the following article to match Project requirements. Refer to LANL Standard Detail ST-G4010-32.  Provide ductbank plans and details in the Drawings.

*************************************************************************************************************

  - UNDERGROUND DUCTBANK INSTALLATION

Install the number and size of ducts as indicated on the Drawings.

Use the following duct materials:

*************************************************************************************************************

Edit 1–3 to match Project requirements.

*************************************************************************************************************

Use Schedule 40 rigid non-metallic conduit, Type EB utility duct, galvanized intermediate metal conduit, or rigid galvanized steel conduit for communications ducts.

Use plastic-coated galvanized rigid steel conduit, tape-wrapped galvanized intermediate metal conduit, or tape-wrapped rigid galvanized steel conduit for elbow and riser where ducts turn up to the surface.

Grade ducts to a minimum of 4 inches per 100 ft to drain to manholes. do not trap ducts.  Align ducts to prevent trapping moisture at any point.

Use the smooth earth walls of trenches as forms for concrete encasement of ducts.

If a manhole is not indicated, make horizontal changes in direction of duct runs using long sweep bends with a minimum radius of 35 feet unless otherwise noted on the Drawings.

Where ducts turn up into the surface, use RGS, IMC, or PVC coated rigid steel elbows with minimum 36 inches radius; terminate in a coupling 4 inches above the surface or equipment pad.  Install zinc-plated malleable iron pipe plug in each unused duct stub-up.

Support ducts with duct spacers placed at intervals not exceeding 5 ft.  Stagger duct supports to prevent any discontinuity in the concrete encasement.

Anchor ducts to bottom of trench using at intervals not exceeding 10 ft.

Terminate telecommunications ducts in manholes, vaults and building walls using bell end fittings.

For ducts installed through holes cut by Subcontractor in an existing building, vault, or manhole wall, pack opening with non-shrink grout. Feather the edge of the grout around each bell and conform to the curvature of the bell end.  Remove sharp edges and projections and fill voids within 6 inches of bell ends.

For concrete-encased ducts installed in new manholes through a knockout panel, after removing forms from the end of the ductbank, rub the exposed concrete surface smooth.  Feather the edge of the concrete around each bell and conform to the curvature of the bell end.  Remove sharp edges and projections and fill voids within 6 inches of bell ends.

*************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

*************************************************************************************************************

All underground secure communications ducts must meet Section 2700.15 requirements.

For secure ducts installed through holes cut in existing building, vault or manhole walls, pack opening with non-shrink grout.

Ground metallic conduit exposed to contact to NFPA 70 requirements.  Use hydraulically irreversible crimps for concealed grounding connections.

Install a 4/0 AWG bare copper ground cable centered within each telecom ductbank.

Connect to ground cable in manholes using hydraulically irreversible crimps.

Connect to ground bar in telecommunications room using IEEE 837 certified compression connectors.

Make-up joints in underground ducts to be tight, driven home on both sides and thoroughly waterproof.  On non-metallic ducts use manufacturer's recommended solvent-cement.  On metallic conduits, coat male threads with red colored, alkyd base, tank and structural primer that is suitable for galvanized steel; make up fittings wrench-tight.

*************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

*************************************************************************************************************

Mark secure communication ducts with red painted stripes on 5-foot centers. Mark secure communications conduits in manholes with 3/4-inch-wide red plastic tape on 1-foot centers.

Where metallic conduits exit concrete encasement, use plastic coated rigid steel conduit or tape wrap with corrosion protection tape, half-lapped.  Wrap IMC or RGS conduit 12 inches on each side of exit point and wrap all metal conduits in contact with earth.

Schedule inspection of each ductbank or ductbank segment with CNI Site Coordinator before concrete is placed.

Test each duct for blockage or deformation after concrete has cured for 24 hours.

Use a flexible mandrel/scraper not less than 12 inches long with a diameter approximately 1/4 inch less than the inside diameter of the duct.

Pull a mandrel behind a brush with stiff bristles.

Replace any duct section found blocked.

Notify LANL STR not less than two working days before duct tests; submit written reports of tests to STR.

After ducts have been successfully inspected and tested:

Backfill the trench as described in “Excavation and Backfill” article above, and

Place underground warning tape in backfill 12 inches below the surface.

Install measuring and pulling tape in each duct. Leave not less than 12 inches of slack at each end of the tape.  Secure each end of tape.

Stub-Up Connections:

Use rigid steel conduit or IMC for outdoor stub-up connections. Non-metallic conduit may be used for indoor stub-up connections that are not subject to physical damage.

Extend conduits through concrete pad or floor for connection to freestanding equipment with an adjustable top or coupling threaded inside for plugs; set flush with the finished floor or equipment pad.

Where equipment connections are not made under this Subcontract, install threaded insert plugs set flush with the floor.

Install corrosion protection tape on metal conduits and fittings in contact with soil using half-lapped wrappings.

  - CONCRETE ENCASEMENT

Concrete-encase underground ductbanks to provide not less than 3 inches of coverage on all sides.

Refer to Section 03 3053 – Miscellaneous Cast-in-Place Concrete or Section 03 3001 – Reinforced Concrete for basic material and installation requirements. Neither concrete reinforcing nor concrete testing is required for this application.

Use a pre-approved concrete mix design that is suitable for exterior use exposed to freezing and thawing.

Place concrete using deflecting trough directing concrete through the duct assembly.

Place concrete envelope as one monolithic pour where possible; taper any joints with a 10:1 slope.

Allow for expansion/contraction of ducts; place concrete starting at one end of ductbank allowing the free end to move.

*************************************************************************************************************

Delete the following article if ductbank systems are not for secure communications.

*************************************************************************************************************

The LANL CNI Site Coordinator must perform an inspection of the secure communications ductbank system prior to encasing with concrete.

***************************************************************************************************************

Delete the following article if manholes are not needed. Refer to LANL Standard Details ST-G4010-35, ST-G4010-36, and ST-G4010-37. Provide manhole plans and details in the Drawings.

****************************************************************************************************************

  - MANHOLE INSTALLATION

Install manholes at locations indicated on the Drawings.

Install manholes in accordance with ASTM C891 – Standard Practice for Installation of Underground Precast Concrete Utility Structures.

Make excavation of suitable dimensions so ducts enter manhole at proper elevation. Refer to Section 31 2000 – Earth Moving for additional requirements.

Install at least 6 inches sand bedding under manholes; level and compact to 95% maximum density accordance with ASTM D 1557.

Install a sump of 3/4-inch gravel below the drain sump opening in the bottom ring of the manhole.

Place pre-molded joint filler in joints between bottom ring, top ring, grade rings and manhole frame.  Install following manufacturer's instructions.

Install a continuous loop of 4/0 AWG bare copper ground cable around inside walls of manholes at floor level.

Attach to walls using copper or cast bronze cable holders and masonry anchors.

Connect to duct bank ground cable using hydraulically irreversible compression fittings.

Ground metallic conduits or duct bell ends to ground cable loop using irreversible compression fittings.

Ground metal cable racks and permanent ladders using hydraulically irreversible compression fittings.

Install cable racks as required to support cables at intervals not exceeding 3 ft.  Coordinate quantity and types of racks and arms with the LANL Telecommunications Group.

For manholes in unpaved areas, install an 8 ft by 8 ft by 6-inch concrete apron around manhole frame and cover.  Taper the concrete one inch away from the frame to the edge of the apron for drainage.

Stamp manhole structure number on north edge of manhole ring. Use steel dies with 3/8 inch or larger characters.

  - DUCT PLUGGING AND SEALING

Install duct plugs in both ends of all unused ducts that cross any natural gas line.

Install duct sealant in both ends of all ducts containing cables that cross any natural gas line.

FIELD QUALITY CONTROL

    - Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

*************************************************************************************************************

Edit the following article to match Project requirements: delete inspection points that are not applicable to the Project.

*************************************************************************************************************

    - Inspection Points – Provide not less than 2 working days advance notice to the LANL STR for the following LANL inspection points. In the notice, identify the specific areas of the Project for which LANL inspection is requested. Correct deficiencies identified during inspections. If the requested LANL inspection does not occur within 3 working days of the LANL inspection point, work may proceed.

Underground ducts: After ducts have been installed but before concrete-encasement or trench backfilling commences. Inspections may be scheduled for one or more segments. LANL inspection may include but is not limited to:

        - Correct duct material, quantity, and size,

        - Proper duct spacing and supports,

        - Proper anchoring of support spacers,

        - Proper depth and grading of ducts,

        - Correct duct stub-up locations,

        - Duct connection and coupling integrity,

        - Ground cable material and size,

        - Ground cable connection integrity.

Mandrel testing of underground ducts: After concrete-encasement has cured for 24 hours but before trench backfilling commences.  LANL witnessing of Subcontractor-performed tests may be scheduled for one or more segments.

Manholes: After manholes have been installed but before concrete- backfilling commences. Inspections may be scheduled for one or more manholes. LANL inspection may include but is not limited to:

        - Correct manhole material and size,

        - Proper manhole location, orientation, leveling, and depth, and

        - Proper installation of pre-molded joint filler between sections.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project spec section is based on LANL Master Specification Section 33 8126, Rev. 1, dated June 7, 2022.